## 220kV
Voltage | Inservice time | Test time | Year-of-test | H2(μL/L) | CO(μL/L) | CO2(μL/L) | CH4(μL/L) | C2H4(μL/L) | C2H6(μL/L) | C2H2(μL/L) | total consub(μL/L) | Acid (mgKOH/g) | PF(90℃)(%) | Breakdown voltage(kV) | CO/CO2
220 | 2013-11-08 | 2013-11-08 | 0 | 0.26 | 5.89 | 120.69 | 0.36 | 0.24 | 0 | 0.08 | 0.68 | 0.014 | 0.05 | 52 | 20.4907
交流220kV | 2012-03-22 | 2012-03-22 | 0 | 0.67 | 8.2 | 59.15 | 0.3 | 0 | 0 | 0 | 0.3 | 0 | 0 | 0 | 7.2134
交流220kV | 2013-10-30 | 2013-10-30 | 0 | 6 | 27 | 179 | 5.96 | 0.16 | 0.21 | 0 | 6.33 | 0.006 | 0.11 | 56.7 | 6.6296
交流220kV | 2013-10-30 | 2013-10-30 | 0 | 7 | 29 | 232 | 5.88 | 0.21 | 0.42 | 0 | 6.51 | 0.006 | 0.21 | 52.3 | 8
交流220kV | 2013-10-30 | 2013-10-30 | 0 | 9 | 35 | 217 | 6.02 | 0.16 | 0.31 | 0 | 6.49 | 0.006 | 0.11 | 56.7 | 6.2
交流220kV | 2013-04-27 | 2013-04-27 | 0 | 1.1 | 2.7 | 94.7 | 0.2 | 0.3 | 0.4 | 0.1 | 1 | 0.01 | 0.17 | 48.8 | 35.0741
交流220kV | 2012-10-24 | 2012-10-24 | 0 | 1.98 | 38.71 | 1488.85 | 2.21 | 0.52 | 1.06 | 0 | 3.79 | 0.005 | 0.002 | 51 | 38.4616
交流220kV | 2011-03-17 | 2011-03-18 | 0.0027397 | 2.4 | 12.5 | 156.5 | 0.4 | 0 | 0 | 0 | 0.4 | 0 | 0 | 0 | 12.52
交流220kV | 2010-12-23 | 2010-12-24 | 0.0027397 | 7.14 | 68.78 | 287.12 | 6.31 | 7.38 | 1.17 | 0 | 14.86 | 0.01 | 0 | 60 | 4.1745
交流220kV | 2012-06-10 | 2012-06-11 | 0.0027397 | 2.3 | 10.6 | 250.2 | 0.2 | 0 | 0 | 0 | 0.2 | 0 | 0 | 0 | 23.6038
交流220kV | 2012-06-10 | 2012-06-11 | 0.0027397 | 2.3 | 11.4 | 211.6 | 0.2 | 0 | 0 | 0 | 0.2 | 0 | 0 | 0 | 18.5614
交流220kV | 2012-07-06 | 2012-07-07 | 0.0027397 | 3.48 | 16.28 | 167.66 | 0.61 | 0 | 0 | 0 | 0.61 | 0 | 0 | 0 | 10.2985
交流220kV | 2010-11-28 | 2010-11-29 | 0.0027397 | 1.5 | 8.1 | 110.9 | 0.6 | 0 | 0 | 0 | 0.6 | 0 | 0 | 0 | 13.6914
交流220kV | 2011-03-17 | 2011-03-18 | 0.0027397 | 3.3 | 13.5 | 146.9 | 0.4 | 0 | 0 | 0 | 0.4 | 0 | 0 | 0 | 10.8815
交流220kV | 2013-01-14 | 2013-01-15 | 0.0027397 | 0.68 | 4.13 | 162.42 | 0.28 | 0 | 0 | 0 | 0.28 | 0.008 | 0.192 | 56.8 | 39.3269
交流220kV | 2013-01-14 | 2013-01-15 | 0.0027397 | 0.81 | 4.03 | 243.16 | 0.55 | 0 | 0 | 0 | 0.55 | 0.008 | 0.296 | 59.6 | 60.3375
交流220kV | 2012-10-27 | 2012-10-28 | 0.0027397 | 9 | 147 | 198 | 0.3 | 0.2 | 0.1 | 0 | 0.6 | 0.014 | 0.25 | 56 | 1.3469
交流220kV | 2012-10-27 | 2012-10-28 | 0.0027397 | 6 | 142 | 201 | 0.3 | 0.3 | 0.1 | 0 | 0.7 | 0.036 | 0.25 | 56 | 1.4155
交流220kV | 2012-07-01 | 2012-07-03 | 0.0054795 | 8.19 | 16.18 | 128.75 | 0.74 | 0 | 0 | 0 | 0.74 | 0 | 0 | 0 | 7.9574
交流220kV | 2011-07-13 | 2011-07-15 | 0.0054795 | 5.2 | 21.3 | 303.2 | 0.5 | 0 | 0 | 0 | 0.5 | 0 | 0 | 0 | 14.2347
交流220kV | 2011-06-28 | 2011-06-30 | 0.0054795 | 4.6 | 13.2 | 131.3 | 0.2 | 0 | 0 | 0 | 0.2 | 0 | 0 | 0 | 9.947
交流220kV | 2011-06-28 | 2011-06-30 | 0.0054795 | 3.6 | 11.3 | 111.1 | 0.2 | 0 | 0 | 0 | 0.2 | 0 | 0 | 0 | 9.8319
交流220kV | 2014-03-24 | 2014-03-26 | 0.0054795 | 3.34 | 4.48 | 217.02 | 10.1 | 0.7 | 0 | 0.32 | 11.12 | 0.06 | 0.001 | 49 | 48.442
交流220kV | 2013-10-30 | 2013-11-01 | 0.0054795 | 12 | 35 | 202 | 6.89 | 0.16 | 0.21 | 0 | 7.26 | 0.006 | 0.21 | 52.3 | 5.7714
交流220kV | 2008-01-08 | 2008-01-10 | 0.0054795 | 11.85 | 60.04 | 237.3 | 0.22 | 0.76 | 0.35 | 0.8 | 2.13 | 0.01 | 0.11 | 55 | 3.9524
交流220kV | 2012-08-06 | 2012-08-08 | 0.0054795 | 8.23 | 87.41 | 315.2 | 1.13 | 0.08 | 0.39 | 0 | 1.6 | 0.001 | 0.001 | 55 | 3.606
交流220kV | 2013-06-20 | 2013-06-22 | 0.0054795 | 1 | 9 | 247 | 2 | 0.2 | 0.14 | 0 | 2.34 | 0.005 | 1.092 | 65 | 27.4444
交流220kV | 2013-07-09 | 2013-07-11 | 0.0054795 | 5 | 28 | 329 | 2.27 | 0.37 | 0.14 | 0.15 | 2.93 | 0.03 | 0.011 | 74 | 11.75
交流220kV | 2012-06-10 | 2012-06-13 | 0.0082192 | 2.1 | 9.9 | 201.7 | 0.2 | 0 | 0 | 0 | 0.2 | 0 | 0 | 0 | 20.3737
交流220kV | 2012-03-22 | 2012-03-25 | 0.0082192 | 0.92 | 8.27 | 63.29 | 0.3 | 0 | 0 | 0 | 0.3 | 0 | 0 | 0 | 7.653
交流220kV | 2012-06-10 | 2012-06-13 | 0.0082192 | 2.6 | 11.8 | 247.4 | 0.2 | 0 | 0 | 0 | 0.2 | 0 | 0 | 0 | 20.9661
交流220kV | 2010-07-23 | 2010-07-26 | 0.0082192 | 11 | 28 | 209 | 2.16 | 2.42 | 0.44 | 0.22 | 5.24 | 0.001 | 0.001 | 50 | 7.4643
交流220kV | 2011-09-19 | 2011-09-22 | 0.0082192 | 39.81 | 43.89 | 685.58 | 4.63 | 0.39 | 0.32 | 0 | 5.34 | 0 | 0.003 | 52 | 15.6204
交流220kV | 2012-08-06 | 2012-08-09 | 0.0082192 | 5.79 | 85.41 | 328.54 | 1.1 | 0.08 | 0.28 | 0 | 1.46 | 0.002 | 0.001 | 54 | 3.8466
交流220kV | 2012-08-06 | 2012-08-09 | 0.0082192 | 3.36 | 24.24 | 449.13 | 1.79 | 0.22 | 2.88 | 0.13 | 5.02 | 0.001 | 0.001 | 54 | 18.5285
交流220kV | 2011-03-17 | 2011-03-21 | 0.010959 | 3.5 | 14.5 | 150.3 | 0.4 | 0 | 0 | 0 | 0.4 | 0 | 0 | 0 | 10.3655
交流220kV | 2013-09-05 | 2013-09-09 | 0.010959 | 1.8 | 11.2 | 185.2 | 1.2 | 0.2 | 3.3 | 0 | 4.7 | 0 | 0 | 0 | 16.5357
交流220kV | 2011-03-17 | 2011-03-21 | 0.010959 | 2.6 | 13.9 | 160.7 | 0.4 | 0 | 0 | 0 | 0.4 | 0 | 0 | 0 | 11.5612
交流220kV | 2011-10-27 | 2011-10-31 | 0.010959 | 24 | 40 | 156 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.9
交流220kV | 2012-07-06 | 2012-07-10 | 0.010959 | 5.84 | 21.24 | 201.56 | 0.69 | 0 | 0 | 0 | 0.69 | 0 | 0 | 0 | 9.4896
交流220kV | 2011-05-31 | 2011-06-04 | 0.010959 | 5.7 | 12.3 | 103.1 | 1 | 0 | 0 | 0 | 1 | 0.01 | 0.135 | 58.4 | 8.3821
交流220kV | 2011-10-27 | 2011-10-31 | 0.010959 | 24 | 38 | 140 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 3.6842
交流220kV | 2014-03-24 | 2014-03-28 | 0.010959 | 6.75 | 22.81 | 449.04 | 1.22 | 0.83 | 0 | 0.33 | 2.38 | 0.04 | 0.001 | 48 | 19.6861
交流220kV | 2012-11-17 | 2012-11-21 | 0.010959 | 13.1 | 45 | 376 | 4.9 | 0.2 | 1 | 0 | 6.1 | 0.005 | 0 | 48 | 8.3556
交流220kV | 2011-06-30 | 2011-07-04 | 0.010959 | 2 | 10.8 | 109.1 | 0.3 | 0 | 0 | 0 | 0.3 | 0.012 | 0.04 | 62 | 10.1019
交流220kV | 2011-06-30 | 2011-07-04 | 0.010959 | 3 | 13 | 141.5 | 0.3 | 0 | 0 | 0 | 0.3 | 0.009 | 0.04 | 61 | 10.8846
交流220kV | 2010-11-28 | 2010-12-03 | 0.013699 | 2.5 | 9.3 | 136.9 | 0.7 | 0 | 0 | 0 | 0.7 | 0 | 0 | 0 | 14.7204
交流220kV | 2011-12-30 | 2012-01-04 | 0.013699 | 3.4 | 16 | 115 | 0.1 | 0 | 0 | 0 | 0.1 | 0 | 0 | 0 | 7.1875
交流220kV | 2011-09-29 | 2011-10-04 | 0.013699 | 8 | 65 | 171 | 0.7 | 0 | 0 | 0 | 0.7 | 0 | 0 | 0 | 2.6308
交流220kV | 2011-09-29 | 2011-10-04 | 0.013699 | 10 | 66 | 192 | 0.6 | 0 | 0 | 0 | 0.6 | 0 | 0 | 0 | 2.9091
交流220kV | 2013-04-26 | 2013-05-01 | 0.013699 | 6.2 | 72 | 203.01 | 0.52 | 0.3 | 0.15 | 0.11 | 1.08 | 0.003 | 0.514 | 65 | 2.8196
交流220kV | 2012-10-27 | 2012-11-01 | 0.013699 | 9 | 145 | 254 | 0.3 | 0.2 | 0.1 | 0 | 0.6 | 0.063 | 0.25 | 55 | 1.7517
交流220kV | 2012-10-27 | 2012-11-01 | 0.013699 | 8 | 145 | 201 | 0.3 | 0.2 | 0.1 | 0 | 0.6 | 0.051 | 0.32 | 52 | 1.3862
交流220kV | 2013-04-26 | 2013-05-01 | 0.013699 | 6 | 18 | 203 | 0.5 | 0.3 | 0.2 | 0.1 | 1.1 | 0.028 | 0.514 | 65 | 11.2778
交流220kV | 2011-06-28 | 2011-07-04 | 0.016438 | 6.8 | 18.9 | 141.2 | 0.5 | 0 | 0 | 0 | 0.5 | 0 | 0 | 0 | 7.4709
交流220kV | 2011-06-28 | 2011-07-04 | 0.016438 | 10.1 | 22.9 | 141.7 | 0.4 | 0 | 0 | 0 | 0.4 | 0 | 0 | 0 | 6.1878
交流220kV | 2011-04-20 | 2011-04-26 | 0.016438 | 2.94 | 6.51 | 279.73 | 0.53 | 0.07 | 0.11 | 0 | 0.71 | 0.006 | 0.002 | 54.6 | 42.9693
交流220kV | 2011-04-20 | 2011-04-26 | 0.016438 | 2.43 | 10.8 | 206.6 | 0.5 | 0.07 | 0.11 | 0 | 0.68 | 0.005 | 0.001 | 54.8 | 19.1296
交流220kV | 2012-03-22 | 2012-03-29 | 0.019178 | 3.51 | 8.18 | 137.38 | 0.59 | 0.29 | 0.1 | 0 | 0.98 | 0.011 | 0.068 | 60 | 16.7946
交流220kV | 2013-01-29 | 2013-02-05 | 0.019178 | 10 | 53.7 | 277 | 0.8 | 0 | 0 | 0 | 0.8 | 0.006 | 0.001 | 45 | 5.1583
交流220kV | 2013-03-18 | 2013-03-25 | 0.019178 | 0.63 | 8.99 | 242.53 | 0.52 | 0 | 0 | 0 | 0.52 | 0.004 | 0.003 | 52 | 26.9778
交流220kV | 2013-04-26 | 2013-05-03 | 0.019178 | 5 | 19 | 260 | 0.6 | 0.3 | 0.1 | 0.1 | 1.1 | 0.03 | 0.524 | 150 | 13.6842
交流220kV | 2011-07-13 | 2011-07-21 | 0.021918 | 6.3 | 25.9 | 188.1 | 0.5 | 0 | 0 | 0 | 0.5 | 0 | 0 | 0 | 7.2625
交流220kV | 2011-05-31 | 2011-06-08 | 0.021918 | 7.5 | 16.9 | 100.8 | 0.6 | 0 | 0 | 0 | 0.6 | 0.01 | 0.135 | 58.8 | 5.9645
交流220kV | 2013-07-22 | 2013-07-30 | 0.021918 | 3.8 | 48.2 | 307.1 | 0.53 | 0 | 0 | 0 | 0.53 | 0 | 0 | 0 | 6.3714
交流220kV | 2012-06-10 | 2012-06-19 | 0.024658 | 3.3 | 11.1 | 182 | 0.3 | 0 | 0 | 0 | 0.3 | 0 | 0 | 0 | 16.3964
交流220kV | 2012-06-10 | 2012-06-19 | 0.024658 | 2 | 10.9 | 183.1 | 0.3 | 0 | 0 | 0 | 0.3 | 0 | 0 | 0 | 16.7982
交流220kV | 2012-03-22 | 2012-03-31 | 0.024658 | 2 | 15 | 98 | 0.57 | 0 | 0 | 0 | 0.57 | 0 | 0 | 0 | 6.5333
交流220kV | 2011-06-28 | 2011-07-08 | 0.027397 | 12 | 27 | 133 | 0.5 | 0 | 0 | 0 | 0.5 | 0 | 0 | 0 | 4.9259
交流220kV | 2011-06-28 | 2011-07-08 | 0.027397 | 10 | 25.1 | 159.6 | 0.3 | 0 | 0 | 0 | 0.3 | 0 | 0 | 0 | 6.3586
交流220kV | 2011-03-17 | 2011-03-27 | 0.027397 | 3 | 15.4 | 171.4 | 0.4 | 0 | 0 | 0 | 0.4 | 0 | 0 | 0 | 11.1299
交流220kV | 2012-07-06 | 2012-07-16 | 0.027397 | 6.66 | 36.36 | 232.9 | 0.79 | 0 | 0 | 0 | 0.79 | 0 | 0 | 0 | 6.4054
交流220kV | 2011-03-17 | 2011-03-27 | 0.027397 | 3.9 | 15.6 | 160.3 | 0.4 | 0 | 0 | 0 | 0.4 | 0 | 0 | 0 | 10.2756
交流220kV | 2011-06-20 | 2011-06-30 | 0.027397 | 4.9 | 33.5 | 217.5 | 0.5 | 0.1 | 0 | 0 | 0.6 | 0.006 | 0.05 | 50 | 6.4925
交流220kV | 2012-10-24 | 2012-11-03 | 0.027397 | 16.09 | 60.75 | 1488.71 | 1.67 | 0.37 | 0.73 | 0 | 2.77 | 0.004 | 0.002 | 52.3 | 24.5055
交流220kV | 2012-12-31 | 2013-01-11 | 0.030137 | 1.28 | 3.79 | 119.22 | 0.25 | 0.14 | 0.31 | 0 | 0.7 | 0 | 0 | 0 | 31.4565
交流220kV | 2012-07-01 | 2012-07-12 | 0.030137 | 7.92 | 67.85 | 174.85 | 0.64 | 0 | 0 | 0 | 0.64 | 0 | 0 | 0 | 2.577
交流220kV | 2011-06-26 | 2011-07-07 | 0.030137 | 0.5 | 7.5 | 324.8 | 0.7 | 0 | 0 | 0 | 0.7 | 0 | 0 | 0 | 43.3067
交流220kV | 2012-10-27 | 2012-11-07 | 0.030137 | 9 | 145 | 254 | 0.3 | 0.2 | 0.1 | 0 | 0.6 | 0.056 | 0.32 | 56 | 1.7517
交流220kV | 2012-10-27 | 2012-11-07 | 0.030137 | 6 | 145 | 254 | 0.3 | 0.2 | 0.1 | 0 | 0.6 | 0.025 | 0.23 | 59 | 1.7517
交流220kV | 2013-01-25 | 2013-02-06 | 0.032877 | 1.02 | 9.12 | 90.56 | 0.27 | 0.2 | 0.59 | 0 | 1.06 | 0 | 0 | 0 | 9.9298
交流220kV | 2013-01-25 | 2013-02-06 | 0.032877 | 1.42 | 13.12 | 110.89 | 0.43 | 0.2 | 0.62 | 0 | 1.25 | 0 | 0 | 0 | 8.452
交流220kV | 2013-05-22 | 2013-06-03 | 0.032877 | 37.1 | 23.2 | 463.1 | 6.41 | 2.67 | 5.49 | 0 | 14.57 | 0.004 | 0.046 | 55 | 19.9612
交流220kV | 2012-12-31 | 2013-01-13 | 0.035616 | 6 | 3 | 93 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 31
交流220kV | 2013-12-24 | 2014-01-06 | 0.035616 | 3.59 | 3.61 | 206.3 | 0.57 | 0.06 | 0.07 | 0 | 0.7 | 0.007 | 0.001 | 54 | 57.1468
交流220kV | 2011-09-29 | 2011-10-13 | 0.038356 | 12 | 90 | 203 | 0.7 | 0 | 0 | 0 | 0.7 | 0 | 0 | 0 | 2.2556
交流220kV | 2011-09-29 | 2011-10-13 | 0.038356 | 9 | 80 | 190 | 0.8 | 0 | 0 | 0 | 0.8 | 0 | 0 | 0 | 2.375
交流220kV | 2013-07-22 | 2013-08-05 | 0.038356 | 4.9 | 51.2 | 315.1 | 0.61 | 0 | 0 | 0 | 0.61 | 0 | 0 | 0 | 6.1543
交流220kV | 2011-12-22 | 2012-01-05 | 0.038356 | 1.13 | 6 | 102 | 0.36 | 0.09 | 0.38 | 0 | 0.83 | 0.021 | 0.058 | 53.5 | 17
交流220kV | 2012-07-17 | 2012-07-31 | 0.038356 | 13.9 | 12.3 | 141.8 | 0.7 | 0.2 | 0.4 | 0 | 1.3 | 0.006 | 0.08 | 53.4 | 11.5285
交流220kV | 2014-01-14 | 2014-01-28 | 0.038356 | 4 | 34 | 223 | 0.48 | 0.15 | 0.19 | 0 | 0.82 | 0.036 | 0.111 | 72 | 6.5588
交流220kV | 2011-10-27 | 2011-11-11 | 0.041096 | 19 | 31 | 164 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 5.2903
交流220kV | 2011-10-27 | 2011-11-11 | 0.041096 | 24 | 41 | 172 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 4.1951
交流220kV | 2012-03-28 | 2012-04-13 | 0.043836 | 0.8 | 10.1 | 155.5 | 0.3 | 0.1 | 0.1 | 0 | 0.5 | 0.001 | 0.13 | 54.8 | 15.396
交流220kV | 2012-03-28 | 2012-04-13 | 0.043836 | 0.9 | 9.1 | 169.1 | 0.3 | 0.1 | 0.1 | 0 | 0.5 | 0.001 | 0.08 | 59.6 | 18.5824
交流220kV | 2011-06-08 | 2011-06-30 | 0.060274 | 10.7 | 44 | 280.1 | 0.7 | 0.2 | 0 | 0.1 | 1 | 0.006 | 0.06 | 52 | 6.3659
交流220kV | 2010-09-17 | 2010-10-11 | 0.065753 | 12.5 | 64.6 | 420.8 | 0.9 | 0.2 | 0.1 | 0 | 1.2 | 0.003 | 0.23 | 53 | 6.5139
交流220kV | 2012-12-31 | 2013-01-25 | 0.068493 | 7 | 8 | 137 | 1 | 3 | 7 | 0.89 | 11.89 | 0 | 0 | 0 | 17.125
交流220kV | 2012-07-01 | 2012-07-27 | 0.071233 | 6.91 | 63.04 | 180.95 | 0.71 | 0 | 0 | 0 | 0.71 | 0 | 0 | 0 | 2.8704
交流220kV | 2011-06-03 | 2011-06-30 | 0.073973 | 12.9 | 94.5 | 774.4 | 1.9 | 0.2 | 0.3 | 0 | 2.4 | 0.003 | 0.44 | 51.8 | 8.1947
交流220kV | 2012-07-17 | 2012-08-14 | 0.076712 | 13.6 | 29.7 | 190.1 | 1.9 | 0.2 | 0.3 | 0 | 2.4 | 0.006 | 0.13 | 52 | 6.4007
交流220kV | 2011-05-31 | 2011-06-29 | 0.079452 | 16.9 | 21.4 | 116.8 | 0.7 | 0 | 0 | 0 | 0.7 | 0.01 | 0 | 56.4 | 5.4579
交流220kV | 2012-03-22 | 2012-04-20 | 0.079452 | 4 | 31 | 109 | 0.6 | 0 | 0 | 0 | 0.6 | 0 | 0 | 0 | 3.5161
交流220kV | 2010-11-28 | 2010-12-27 | 0.079452 | 3.9 | 17.3 | 249.6 | 0.9 | 1 | 1.2 | 0 | 3.1 | 0 | 0 | 0 | 14.4277
交流220kV | 2011-04-25 08:44 | 2011-05-25 | 0.081194 | 1.5 | 22.9 | 377.1 | 0.8 | 0.1 | 0.8 | 0 | 1.7 | 0 | 0 | 0 | 16.4672
交流220kV | 2013-01-27 | 2013-02-26 | 0.082192 | 6.01 | 45.02 | 195.38 | 0.51 | 0 | 0 | 0 | 0.51 | 0 | 0 | 0 | 4.3398
交流220kV | 2012-07-06 | 2012-08-05 | 0.082192 | 10.05 | 44.88 | 131.83 | 1.79 | 0.72 | 0 | 0 | 2.51 | 0 | 0 | 0 | 2.9374
交流220kV | 2014-01-19 | 2014-02-18 | 0.082192 | 8.5 | 13.7 | 135.8 | 0.7 | 0.1 | 0.1 | 0 | 0.9 | 0.001 | 0.12 | 64 | 9.9124
交流220kV | 2014-01-19 | 2014-02-18 | 0.082192 | 11.4 | 13.7 | 137 | 1.5 | 1.9 | 0.3 | 0.1 | 3.8 | 0.002 | 0.26 | 56.8 | 10
交流220kV | 2011-05-19 09:04 | 2011-06-19 | 0.083896 | 6.8 | 15.4 | 451.5 | 1.2 | 0 | 0.8 | 0 | 2 | 0 | 0 | 0 | 29.3182
交流220kV | 2012-06-10 | 2012-07-11 | 0.084932 | 3.66 | 20.65 | 182.38 | 0.33 | 0 | 0 | 0 | 0.33 | 0 | 0 | 0 | 8.832
交流220kV | 2011-03-17 | 2011-04-17 | 0.084932 | 4.8 | 19.8 | 203.6 | 0.4 | 0 | 0 | 0 | 0.4 | 0 | 0 | 0 | 10.2828
交流220kV | 2011-06-26 | 2011-07-27 | 0.084932 | 0.8 | 8.5 | 350 | 0.7 | 0 | 0 | 0 | 0.7 | 0 | 0 | 0 | 41.1765
交流220kV | 2012-06-10 | 2012-07-11 | 0.084932 | 5.79 | 28.2 | 274.09 | 0.45 | 0 | 0 | 0 | 0.45 | 0 | 0 | 0 | 9.7195
交流220kV | 2012-10-27 | 2012-11-27 | 0.084932 | 9 | 154 | 254 | 0.3 | 0.2 | 0.1 | 0 | 0.6 | 0.021 | 0.21 | 56 | 1.6494
交流220kV | 2012-10-27 | 2012-11-27 | 0.084932 | 6 | 125 | 254 | 0.3 | 0.2 | 0.1 | 0 | 0.6 | 0.014 | 0.26 | 56 | 2.032
交流220kV | 2011-06-28 | 2011-07-30 | 0.087671 | 22.1 | 52.9 | 221.5 | 0.9 | 0.1 | 0.3 | 0 | 1.3 | 0 | 0 | 0 | 4.1871
交流220kV | 2011-06-28 | 2011-07-30 | 0.087671 | 21.1 | 51.2 | 206 | 0.5 | 0.2 | 0 | 0 | 0.7 | 0 | 0 | 0 | 4.0234
交流220kV | 2014-01-25 | 2014-02-26 | 0.087671 | 7.17 | 39.36 | 239.35 | 0.58 | 0 | 0 | 0 | 0.58 | 0.003 | 0.055 | 53.5 | 6.081
交流220kV | 2011-09-29 | 2011-11-01 | 0.090411 | 13.07 | 78.23 | 219.8 | 5.19 | 2.62 | 0 | 0 | 7.81 | 0 | 0 | 0 | 2.8097
交流220kV | 2011-09-29 | 2011-11-01 | 0.090411 | 11.53 | 81.28 | 246.02 | 1.1 | 0.98 | 0 | 0 | 2.08 | 0 | 0 | 0 | 3.0268
交流220kV | 2013-09-27 | 2013-10-30 | 0.090411 | 14.91 | 43.76 | 244.73 | 0.81 | 0 | 0 | 0 | 0.81 | 0 | 0 | 0 | 5.5926
交流220kV | 2013-09-27 | 2013-10-30 | 0.090411 | 17 | 42.82 | 0 | 0.87 | 0 | 0 | 0 | 0.87 | 0 | 0 | 0 | 0
交流220kV | 2013-09-05 | 2013-10-08 | 0.090411 | 8.4 | 534.8 | 357.1 | 0.8 | 0.2 | 0.2 | 0 | 1.2 | 0 | 0 | 0 | 0.66773
交流220kV | 2011-01-28 | 2011-03-02 | 0.090411 | 22.87 | 88 | 112 | 1.99 | 0.22 | 0.54 | 0 | 2.75 | 0.024 | 0.045 | 58.8 | 1.2727
交流220kV | 2013-06-06 | 2013-07-10 | 0.093151 | 1.9 | 16 | 167.8 | 0.3 | 0 | 0 | 0 | 0.3 | 0 | 0 | 0 | 10.4875
交流220kV | 2012-07-04 | 2012-08-07 | 0.093151 | 4 | 21 | 165 | 2 | 0 | 0 | 0 | 2 | 0 | 0 | 0 | 7.8571
交流220kV | 2012-11-22 | 2012-12-26 | 0.093151 | 3.07 | 11.98 | 155.14 | 0.82 | 0.08 | 0.06 | 0 | 0.96 | 0.01 | 0.138 | 58 | 12.9499
交流220kV | 2012-11-22 | 2012-12-26 | 0.093151 | 2.55 | 10.73 | 184.4 | 0.79 | 0.07 | 0.11 | 0 | 0.97 | 0.009 | 0.238 | 57 | 17.1855
交流220kV | 2013-11-14 | 2013-12-18 | 0.093151 | 11.66 | 72.92 | 313.02 | 1.12 | 1.35 | 0.43 | 0 | 2.9 | 0.026 | 0.034 | 68.1 | 4.2926
交流220kV | 2013-11-14 | 2013-12-18 | 0.093151 | 10.32 | 67.16 | 297.88 | 1.1 | 1.39 | 0.77 | 0 | 3.26 | 0.022 | 0.028 | 57.4 | 4.4354
交流220kV | 2012-12-31 | 2013-02-04 | 0.09589 | 3.94 | 9.44 | 123.74 | 0.3 | 0.06 | 0 | 0 | 0.36 | 0 | 0 | 0 | 13.1081
交流220kV | 2011-10-27 | 2011-12-02 | 0.09863 | 4 | 43 | 211 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 4.907
交流220kV | 2010-12-23 | 2011-01-28 | 0.09863 | 8.03 | 70.57 | 282.76 | 6.57 | 7.62 | 1.27 | 0 | 15.46 | 0.014 | 0 | 58.4 | 4.0068
交流220kV | 2011-10-27 | 2011-12-02 | 0.09863 | 3 | 40 | 176 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 4.4
交流220kV | 2011-05-31 | 2011-07-07 | 0.10137 | 14.9 | 50.5 | 419.5 | 1.3 | 0 | 0 | 0 | 1.3 | 0 | 0 | 0 | 8.3069
交流220kV | 2013-06-09 | 2013-07-17 | 0.10411 | 192.1 | 20.2 | 159.8 | 0.3 | 0 | 0 | 0 | 0.3 | 0.009 | 0.061 | 61.8 | 7.9109
交流220kV | 2013-07-22 | 2013-08-30 | 0.10685 | 7 | 113 | 276.3 | 0.6 | 0 | 0 | 0 | 0.6 | 0 | 0 | 0 | 2.4451
交流220kV | 2013-06-06 | 2013-07-16 | 0.10959 | 3.5 | 26.9 | 278.5 | 0.3 | 0 | 0 | 0 | 0.3 | 0 | 0 | 0 | 10.3532
交流220kV | 2013-01-25 | 2013-03-07 | 0.11233 | 1.42 | 13.12 | 110.89 | 0.43 | 0.2 | 0.62 | 0 | 1.25 | 0 | 0 | 0 | 8.452
交流220kV | 2011-01-20 | 2011-03-03 | 0.11507 | 2.03 | 8 | 138 | 0.35 | 0.06 | 0 | 0 | 0.41 | 0.024 | 0.042 | 56.2 | 17.25
交流220kV | 2013-01-14 | 2013-02-26 | 0.11781 | 0.95 | 10.75 | 241.56 | 0.5 | 0 | 0 | 0 | 0.5 | 0.021 | 0.04 | 57.6 | 22.4707
交流220kV | 2011-12-19 | 2012-02-01 | 0.12055 | 11.6 | 12 | 121 | 0.44 | 0 | 0 | 0 | 0.44 | 0.008 | 0.001 | 41 | 10.0833
交流220kV | 2011-11-26 | 2012-01-09 | 0.12055 | 2.14 | 3.06 | 195.89 | 1.31 | 0.59 | 0.36 | 0 | 2.26 | 0.007 | 0.009 | 50.2 | 64.0163
交流220kV | 2014-01-14 | 2014-02-27 | 0.12055 | 7 | 35 | 301 | 0.5 | 0.1 | 0.1 | 0 | 0.7 | 0.1 | 0.1 | 72 | 8.6
交流220kV | 2013-01-25 | 2013-03-11 | 0.12329 | 2.37 | 37.43 | 172.82 | 0.46 | 0.32 | 0.89 | 0 | 1.67 | 0 | 0 | 0 | 4.6172
交流220kV | 2012-10-15 | 2012-12-05 | 0.13973 | 7.4 | 71.9 | 251.7 | 1.3 | 0.2 | 0.2 | 0 | 1.7 | 0 | 0 | 0 | 3.5007
交流220kV | 2013-01-25 | 2013-03-17 | 0.13973 | 5.42 | 98.12 | 256.89 | 0.78 | 0.67 | 0.96 | 0 | 2.41 | 0 | 0 | 0 | 2.6181
220 | 2013-11-11 | 2014-01-03 | 0.14521 | 8.09 | 179.71 | 741.19 | 2.92 | 0.56 | 0.26 | 0 | 3.74 | 0.008 | 0 | 55 | 4.1244
220 | 2013-11-11 | 2014-01-03 | 0.14521 | 5.24 | 132.22 | 704.28 | 2.36 | 0.32 | 0.26 | 0 | 2.94 | 0.01 | 0.001 | 55 | 5.3266
交流220kV | 2013-01-14 | 2013-03-14 | 0.16164 | 2.48 | 9.96 | 179.54 | 0.74 | 0.08 | 0 | 0 | 0.82 | 0.03 | 0.15 | 62.8 | 18.0261
交流220kV | 2013-01-14 | 2013-03-14 | 0.16164 | 1.69 | 8.71 | 207.03 | 0.3 | 0.09 | 0 | 0 | 0.39 | 0.015 | 0.172 | 61.2 | 23.7692
交流220kV | 2012-10-12 | 2012-12-11 | 0.16438 | 6.7 | 21 | 193.8 | 0.8 | 0.1 | 0.3 | 0 | 1.2 | 0 | 0 | 0 | 9.2286
交流220kV | 2013-06-06 | 2013-08-05 | 0.16438 | 4.9 | 44 | 292.8 | 0.5 | 0 | 0 | 0 | 0.5 | 0 | 0 | 0 | 6.6545
交流220kV | 2011-12-23 | 2012-02-21 | 0.16438 | 2 | 17 | 362 | 0.94 | 0.07 | 0.13 | 0 | 1.14 | 0.004 | 0.001 | 57.5 | 21.2941
交流220kV | 2011-12-23 | 2012-02-22 | 0.16712 | 2 | 17 | 362 | 0.94 | 0.07 | 0.13 | 0 | 1.14 | 0.004 | 0.001 | 57.5 | 21.2941
交流220kV | 2011-06-30 | 2011-08-31 | 0.16986 | 26.81 | 35.01 | 299.96 | 5.25 | 0.39 | 4.8 | 0 | 10.44 | 0 | 0 | 0 | 8.5678
交流220kV | 2011-11-11 | 2012-01-13 | 0.1726 | 1.61 | 7 | 163.21 | 0.38 | 0 | 0 | 0 | 0.38 | 0.009 | 0.001 | 66.4 | 23.3157
交流220kV | 2012-10-10 | 2012-12-13 | 0.17534 | 7 | 43.5 | 177.1 | 0.6 | 0 | 0 | 0 | 0.6 | 0 | 0 | 0 | 4.0713
交流220kV | 2013-04-01 | 2013-06-05 | 0.17808 | 7.07 | 68.97 | 337.91 | 0.68 | 0.37 | 0 | 0 | 1.05 | 0.001 | 0.087 | 72.4 | 4.8994
交流220kV | 2011-11-11 | 2012-01-16 | 0.18082 | 0.47 | 8.1 | 171.19 | 0.81 | 0.11 | 0 | 0 | 0.92 | 0.001 | 0.009 | 61 | 21.1346
交流220kV | 2010-12-23 | 2011-02-28 | 0.18356 | 8.12 | 70.34 | 302.42 | 6.72 | 8.04 | 1.23 | 0 | 15.99 | 0.012 | 0 | 60 | 4.2994
交流220kV | 2013-03-31 | 2013-06-09 | 0.19178 | 6.13 | 23.92 | 147.57 | 0.48 | 0.12 | 0.11 | 0 | 0.71 | 0 | 0 | 0 | 6.1693
交流220kV | 2013-01-25 | 2013-04-06 | 0.19452 | 5.23 | 78.65 | 242.34 | 0.75 | 0.44 | 0.89 | 0 | 2.08 | 0 | 0 | 0 | 3.0812
交流220kV | 2013-01-27 | 2013-04-08 | 0.19452 | 5.55 | 17.58 | 115.64 | 0.51 | 0 | 0 | 0 | 0.51 | 0.013 | 0.001 | 71.9 | 6.5779
交流220kV | 2013-12-30 | 2014-03-12 | 0.19726 | 1.73 | 25.15 | 123.56 | 0.34 | 0 | 0 | 0 | 0.34 | 0.008 | 0.21 | 69 | 4.9129
交流220kV | 2010-11-30 | 2011-02-11 | 0.2 | 4.7 | 125 | 450 | 3.85 | 0.56 | 0.86 | 0.44 | 5.71 | 0.021 | 0.064 | 60 | 3.6
交流220kV | 2012-12-30 | 2013-03-14 | 0.20274 | 5.27 | 45.8 | 349.97 | 0.85 | 0.1 | 0.28 | 0 | 1.23 | 0.008 | 0.035 | 62.8 | 7.6413
交流220kV | 2010-12-13 | 2011-02-25 | 0.20274 | 10 | 90 | 178 | 1 | 0.19 | 0.4 | 0 | 1.59 | 0.001 | 0.001 | 49 | 1.9778
交流220kV | 2012-03-22 | 2012-06-05 | 0.20548 | 5 | 61 | 138 | 1 | 0 | 0 | 0 | 1 | 0.032 | 0.1 | 51 | 2.2623
交流220kV | 2011-11-11 | 2012-01-25 | 0.20548 | 1.69 | 7.9 | 166.9 | 0.56 | 0 | 0 | 0 | 0.56 | 0.001 | 0.005 | 61 | 21.1266
交流220kV | 2010-12-29 | 2011-03-19 | 0.21918 | 45.14 | 268.29 | 565.44 | 8.43 | 0.31 | 1.49 | 0 | 10.23 | 0.002 | 0.001 | 59.8 | 2.1076
交流220kV | 2003-12-19 | 2004-03-10 | 0.22466 | 6.7 | 49.5 | 165.9 | 0.9 | 1 | 4.5 | 0 | 6.4 | 0.004 | 0.001 | 50 | 3.3515
交流220kV | 2011-12-29 | 2012-03-22 | 0.23014 | 11.05 | 11.04 | 86.78 | 1.21 | 0.79 | 0.59 | 0 | 2.59 | 0.008 | 0.003 | 58.6 | 7.8605
交流220kV | 2011-09-29 | 2011-12-27 | 0.24384 | 15 | 114 | 261 | 1 | 0.4 | 0 | 0 | 1.4 | 0 | 0 | 0 | 2.2895
交流220kV | 2011-09-29 | 2011-12-27 | 0.24384 | 11 | 113 | 266 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 2.354
交流220kV | 2013-12-24 | 2014-03-24 | 0.24658 | 2.92 | 23.02 | 334.54 | 0.57 | 0.06 | 0.05 | 0 | 0.68 | 0.009 | 0.001 | 59.5 | 14.5326
交流220kV | 2011-06-28 | 2011-09-29 | 0.25479 | 23.9 | 75.7 | 236.3 | 0.9 | 0.2 | 0 | 0 | 1.1 | 0 | 0 | 0 | 3.1215
交流220kV | 2012-07-06 | 2012-10-08 | 0.25753 | 15.51 | 54.4 | 181.9 | 2.32 | 1.05 | 0 | 0 | 3.37 | 0 | 0 | 0 | 3.3438
交流220kV | 2011-12-27 | 2012-03-30 | 0.25753 | 3.26 | 10.32 | 573.43 | 1.65 | 0 | 0 | 0 | 1.65 | 0.003 | 0.08 | 56 | 55.5649
交流220kV | 2011-12-07 | 2012-03-13 | 0.26575 | 6.44 | 56.76 | 300.73 | 3.56 | 0.14 | 0 | 0 | 3.7 | 0.005 | 0.001 | 55.5 | 5.2983
交流220kV | 2011-12-07 | 2012-03-13 | 0.26575 | 6.81 | 30.78 | 238.26 | 3.03 | 0.15 | 0.14 | 0 | 3.32 | 0.005 | 0.001 | 55 | 7.7407
交流220kV | 2013-04-15 | 2013-07-22 | 0.26849 | 31.02 | 45.67 | 286.56 | 1.1 | 0.37 | 0.74 | 0 | 2.21 | 0.004 | 0.003 | 56.2 | 6.2746
交流220kV | 2011-07-27 | 2011-11-02 | 0.26849 | 25 | 57 | 382 | 1 | 0.4 | 0 | 0 | 1.4 | 0.057 | 0.006 | 61 | 6.7018
交流220kV | 2012-12-31 | 2013-04-11 | 0.27671 | 9.07 | 21.89 | 205.61 | 0.7 | 0.08 | 0.13 | 0 | 0.91 | 0 | 0 | 0 | 9.3929
交流220kV | 2013-05-18 | 2013-08-27 | 0.27671 | 16.5 | 217.8 | 759.5 | 2.1 | 0.2 | 0.2 | 0 | 2.5 | 0.003 | 0.05 | 50.3 | 3.4871
交流220kV | 2013-05-18 | 2013-08-29 | 0.28219 | 15.8 | 229 | 747.5 | 2.3 | 0.3 | 0.2 | 0 | 2.8 | 0.006 | 0.07 | 50 | 3.2642
交流220kV | 2012-12-15 | 2013-03-28 | 0.28219 | 5.6 | 14.64 | 316.06 | 3.14 | 0 | 0 | 0 | 3.14 | 0.012 | 0.001 | 61 | 21.5888
交流220kV | 2012-12-15 | 2013-03-28 | 0.28219 | 10.53 | 10.71 | 356.03 | 2.74 | 0.19 | 0 | 0 | 2.93 | 0.011 | 0.001 | 74.9 | 33.2428
交流220kV | 2011-09-26 | 2012-01-12 | 0.29589 | 4.06 | 17.37 | 191.85 | 1.03 | 0.64 | 0.03 | 0 | 1.7 | 0.007 | 0.125 | 52.6 | 11.0449
交流220kV | 2011-03-21 | 2011-07-07 | 0.29589 | 8.6 | 56.9 | 413.8 | 1 | 0.2 | 0.1 | 0.2 | 1.5 | 0.01 | 0.12 | 55 | 7.2724
交流220kV | 2011-06-10 | 2011-09-29 | 0.30411 | 10 | 41 | 165 | 1 | 0.1 | 0.4 | 0 | 1.5 | 0.014 | 0.001 | 59.6 | 4.0244
交流220kV | 2010-11-25 | 2011-03-18 | 0.30959 | 6.35 | 38.66 | 187.89 | 0.53 | 0.11 | 0.21 | 0 | 0.85 | 0.005 | 0.021 | 56 | 4.8601
交流220kV | 2010-11-25 | 2011-03-18 | 0.30959 | 6.14 | 42.38 | 220.62 | 0.66 | 0.06 | 0 | 0 | 0.72 | 0.008 | 0.03 | 59 | 5.2058
交流220kV | 2011-11-24 | 2012-03-16 | 0.30959 | 3.86 | 32.75 | 215.37 | 0.71 | 0.17 | 0.15 | 0 | 1.03 | 0.005 | 0.001 | 52 | 6.5762
交流220kV | 2011-01-22 | 2011-05-16 | 0.31233 | 4.63 | 75.45 | 419.22 | 5.34 | 0.79 | 0.72 | 0 | 6.85 | 0.01 | 0.002 | 60 | 5.5563
交流220kV | 2011-09-19 | 2012-01-11 | 0.31233 | 42.32 | 81.91 | 357.25 | 1.65 | 0.17 | 0.33 | 0 | 2.15 | 0.005 | 0.003 | 52 | 4.3615
220 | 2011-12-15 | 2012-04-09 | 0.31781 | 1 | 8 | 32 | 0 | 0.1 | 0 | 0 | 0.1 | 0.007 | 0.071 | 55 | 4
220 | 2011-12-15 | 2012-04-09 | 0.31781 | 2 | 14 | 18 | 0 | 0 | 0 | 0 | 0 | 0.007 | 0.063 | 52 | 1.2857
交流220kV | 2011-06-30 | 2011-10-24 | 0.31781 | 12.16 | 35.76 | 269.15 | 2.32 | 0.33 | 0.94 | 0 | 3.59 | 0 | 0 | 0 | 7.5266
交流220kV | 2011-12-18 | 2012-04-13 | 0.32055 | 3 | 14 | 236 | 0.22 | 0 | 0 | 0 | 0.22 | 0.004 | 0.06 | 60 | 16.8571
交流220kV | 2013-07-26 | 2013-11-21 | 0.32329 | 29.6 | 68.7 | 314.5 | 1.2 | 0 | 0 | 0 | 1.2 | 0.015 | 1.2 | 55 | 4.5779
交流220kV | 2011-11-28 | 2012-03-27 | 0.32877 | 12.38 | 28.83 | 296.86 | 1.17 | 0 | 0 | 0 | 1.17 | 0.005 | 0.001 | 59 | 10.2969
交流220kV | 2010-12-20 13:08 | 2011-04-20 | 0.33001 | 11.8 | 66.2 | 291.08 | 1.03 | 0.22 | 0.16 | 0 | 1.41 | 0.008 | 0.003 | 52.8 | 4.397
交流220kV | 2011-04-25 08:44 | 2011-08-25 | 0.33325 | 1.8 | 25.4 | 401.1 | 0.8 | 0.2 | 0.8 | 0 | 1.8 | 0 | 0 | 0 | 15.7913
交流220kV | 2011-03-17 | 2011-07-17 | 0.33425 | 4.4 | 23.4 | 251.7 | 0.6 | 0 | 0 | 0 | 0.6 | 0 | 0 | 0 | 10.7564
交流220kV | 2011-03-17 | 2011-07-17 | 0.33425 | 5.3 | 24.1 | 241.3 | 0.5 | 0 | 0 | 0 | 0.5 | 0 | 0 | 0 | 10.0124
交流220kV | 2011-05-19 09:04 | 2011-09-19 | 0.33595 | 8.3 | 16.3 | 520.4 | 1.2 | 0 | 0.8 | 0 | 2 | 0 | 0 | 0 | 31.9264
交流220kV | 2011-06-26 | 2011-10-27 | 0.33699 | 1.2 | 15.4 | 484 | 0.9 | 0 | 0.2 | 0 | 1.1 | 0 | 0 | 0 | 31.4286
交流220kV | 2012-11-17 | 2013-03-20 | 0.33699 | 9.26 | 25 | 341 | 1.27 | 0 | 0 | 0 | 1.27 | 0.005 | 0 | 49 | 13.64
交流220kV | 2011-06-10 | 2011-10-12 | 0.33973 | 8 | 87 | 126 | 1.4 | 0.4 | 0.5 | 0 | 2.3 | 0.002 | 0.002 | 50 | 1.4483
交流220kV | 2011-07-13 | 2011-11-15 | 0.34247 | 10 | 158 | 379 | 3.4 | 1.6 | 1.9 | 0.2 | 7.1 | 0.003 | 0.001 | 49 | 2.3987
交流220kV | 2011-07-13 | 2011-11-15 | 0.34247 | 11 | 118 | 407 | 3.1 | 0.4 | 0.7 | 0 | 4.2 | 0.003 | 0.002 | 54 | 3.4492
交流220kV | 2012-03-13 | 2012-07-19 | 0.35068 | 12.59 | 67.83 | 161.56 | 0.98 | 0.18 | 0 | 0 | 1.16 | 0.023 | 0.01 | 60 | 2.3818
交流220kV | 2012-03-13 | 2012-07-19 | 0.35068 | 12.59 | 67.83 | 161.56 | 0.98 | 0.18 | 0 | 0 | 1.16 | 0.005 | 0.01 | 60 | 2.3818
交流220kV | 2011-05-17 | 2011-09-22 | 0.35068 | 10 | 87 | 301 | 1.2 | 0.2 | 1.06 | 1.6 | 4.06 | 0.063 | 0.001 | 73 | 3.4598
交流220kV | 2011-05-17 | 2011-09-22 | 0.35068 | 7 | 78 | 435 | 1.2 | 0.4 | 0.5 | 0 | 2.1 | 0.057 | 0.001 | 75 | 5.5769
交流220kV | 2012-12-14 | 2013-04-22 | 0.35342 | 25.41 | 32.21 | 11.35 | 1.58 | 0.14 | 0.32 | 0 | 2.04 | 0.004 | 0.088 | 64 | 0.35238
交流220kV | 2013-01-27 | 2013-06-06 | 0.35616 | 10.95 | 101.58 | 341.88 | 0.81 | 0 | 0 | 0 | 0.81 | 0.001 | 0.037 | 66.1 | 3.3656
交流220kV | 2013-07-26 | 2013-12-04 | 0.3589 | 17.15 | 66.6 | 328.99 | 1.01 | 0 | 0 | 0 | 1.01 | 0 | 0 | 0 | 4.9398
交流220kV | 2013-07-26 | 2013-12-04 | 0.3589 | 17.94 | 69.12 | 305.44 | 1.01 | 0 | 0 | 0 | 1.01 | 0 | 0 | 0 | 4.419
交流220kV | 2013-01-25 | 2013-06-06 | 0.36164 | 92.95 | 71.25 | 302.32 | 1.83 | 0.65 | 0.25 | 0 | 2.73 | 0 | 0 | 0 | 4.2431
交流220kV | 2011-06-24 | 2011-11-03 | 0.36164 | 33 | 203 | 1126 | 3.6 | 0.4 | 0.4 | 0 | 4.4 | 0.003 | 0.001 | 58 | 5.5468
交流220kV | 2011-06-24 | 2011-11-03 | 0.36164 | 32 | 207 | 1115 | 4.8 | 0.4 | 0.5 | 0 | 5.7 | 0.003 | 0.008 | 46 | 5.3865
交流220kV | 2011-12-29 | 2012-05-11 | 0.36712 | 2.29 | 27.31 | 231.35 | 0.56 | 0 | 0 | 0 | 0.56 | 0 | 0 | 0 | 8.4713
交流220kV | 2012-12-06 | 2013-04-19 | 0.36712 | 3 | 16 | 218 | 0.18 | 0 | 0 | 0 | 0.18 | 0.004 | 0.189 | 60 | 13.625
交流220kV | 2012-12-06 | 2013-04-19 | 0.36712 | 2 | 12 | 298 | 0.18 | 0 | 0.1 | 0 | 0.28 | 0.003 | 0.088 | 60 | 24.8333
交流220kV | 2011-11-07 | 2012-03-21 | 0.36986 | 2 | 26 | 156 | 1.56 | 0.09 | 0.14 | 0 | 1.79 | 0.001 | 0.052 | 50 | 6
交流220kV | 2011-11-07 | 2012-03-21 | 0.36986 | 3 | 31 | 300 | 1.1 | 0.14 | 0.08 | 0 | 1.32 | 0.001 | 0.05 | 50 | 9.6774
交流220kV | 2012-05-04 | 2012-09-18 | 0.37534 | 11 | 40 | 611 | 1.5 | 0 | 0.3 | 0 | 1.8 | 0.007 | 0.001 | 50 | 15.275
交流220kV | 2013-07-22 | 2013-12-10 | 0.3863 | 2.25 | 92.2 | 400.14 | 1.3 | 0 | 0 | 0 | 1.3 | 0 | 0 | 0 | 4.3399
交流220kV | 2011-08-30 | 2012-01-18 | 0.3863 | 6 | 30 | 295 | 3.9 | 0 | 0 | 0 | 3.9 | 0.031 | 0.54 | 44 | 9.8333
交流220kV | 2011-05-31 | 2011-10-20 | 0.38904 | 6 | 59 | 168 | 7.19 | 0.08 | 0.25 | 0 | 7.52 | 0.011 | 0.002 | 50 | 2.8475
交流220kV | 2011-05-31 | 2011-10-20 | 0.38904 | 10 | 85 | 382 | 8.95 | 0.15 | 0.21 | 0.05 | 9.36 | 0.01 | 0.407 | 50 | 4.4941
交流220kV | 2013-07-26 | 2013-12-17 | 0.39452 | 16.8 | 52.5 | 424.9 | 1 | 0 | 0 | 0 | 1 | 0.02 | 0.8 | 46 | 8.0933
交流220kV | 2011-11-02 | 2012-03-27 | 0.4 | 12.22 | 31.28 | 721.34 | 1.35 | 0 | 0 | 0 | 1.35 | 0.005 | 0.001 | 56 | 23.0607
交流220kV | 2013-06-27 | 2013-11-21 | 0.40274 | 23.7 | 54.3 | 315.5 | 2.8 | 0 | 0 | 0 | 2.8 | 0.018 | 2.1 | 52 | 5.8103
交流220kV | 2011-04-01 | 2011-08-26 | 0.40274 | 22.68 | 96.89 | 413.56 | 1.09 | 0.19 | 0.27 | 0 | 1.55 | 0.01 | 0.001 | 59 | 4.2683
交流220kV | 2013-06-30 | 2013-11-26 | 0.40822 | 5.32 | 132.25 | 557.09 | 1.96 | 0.68 | 0.39 | 0 | 3.03 | 0.002 | 0.1 | 42 | 4.2124
交流220kV | 2010-12-22 | 2011-05-20 | 0.40822 | 9.79 | 60.03 | 401.31 | 1 | 0 | 0.11 | 0 | 1.11 | 0.02 | 0.003 | 56 | 6.6852
220 | 2013-06-30 | 2013-11-27 | 0.41096 | 2.53 | 34.2 | 207.62 | 0.92 | 0.23 | 0 | 0 | 1.15 | 0.005 | 0.105 | 61.2 | 6.0708
交流220kV | 2011-09-13 | 2012-02-10 | 0.41096 | 4.72 | 31 | 73 | 0.74 | 0.19 | 0.39 | 0.12 | 1.44 | 0.024 | 0.038 | 54 | 2.3548
220 | 2013-06-30 | 2013-11-28 | 0.4137 | 3.42 | 73.88 | 263.79 | 1.41 | 0.19 | 0 | 0 | 1.6 | 0.004 | 0.098 | 62.4 | 3.5705
交流220kV | 2011-08-12 | 2012-01-12 | 0.41918 | 4.81 | 65.04 | 243.26 | 2.1 | 0.52 | 0.32 | 0 | 2.94 | 0.007 | 0.074 | 53.5 | 3.7402
交流220kV | 2011-08-12 | 2012-01-12 | 0.41918 | 4.81 | 72.04 | 243.26 | 2.1 | 0.52 | 0.32 | 0 | 2.94 | 0.007 | 0.176 | 52.2 | 3.3767
交流220kV | 2012-07-04 | 2012-12-06 | 0.42466 | 16 | 82 | 167 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 2.0366
交流220kV | 2013-06-09 | 2013-11-12 | 0.4274 | 13.15 | 50.04 | 251.21 | 0.76 | 0 | 0 | 0 | 0.76 | 0.011 | 0.024 | 67 | 5.0202
交流220kV | 2011-11-03 | 2012-04-10 | 0.43562 | 6 | 176 | 1303 | 3.8 | 2.6 | 2 | 0 | 8.4 | 0.046 | 0.201 | 50 | 7.4034
交流220kV | 2011-11-03 | 2012-04-10 | 0.43562 | 6 | 176 | 1303 | 3.8 | 2.6 | 2 | 0 | 8.4 | 0.046 | 0.201 | 51 | 7.4034
交流220kV | 2013-06-29 | 2013-12-06 | 0.43836 | 5.2 | 68.6 | 502.5 | 1.9 | 0.2 | 0.9 | 0 | 3 | 0 | 0 | 0 | 7.3251
交流220kV | 2013-06-29 | 2013-12-06 | 0.43836 | 10.2 | 60.7 | 317.3 | 1.7 | 0.2 | 0.5 | 0 | 2.4 | 0 | 0 | 0 | 5.2273
交流220kV | 2011-07-13 | 2011-12-22 | 0.44384 | 14.25 | 71.15 | 329.62 | 1.26 | 1.62 | 0.19 | 0 | 3.07 | 0 | 0 | 57.2 | 4.6327
交流220kV | 2011-09-21 | 2012-03-01 | 0.44384 | 4.46 | 44.88 | 186.18 | 0.54 | 0 | 0 | 0 | 0.54 | 0.008 | 0.09 | 52 | 4.1484
交流220kV | 2011-12-31 | 2012-06-11 | 0.44658 | 6.07 | 44.39 | 149.63 | 0.51 | 0 | 0 | 0 | 0.51 | 0.012 | 0.069 | 0 | 3.3708
交流220kV | 2011-12-30 | 2012-06-11 | 0.44932 | 16.09 | 75.85 | 254.21 | 1.23 | 0 | 0 | 0 | 1.23 | 0.01 | 0.072 | 0 | 3.3515
交流220kV | 2010-11-29 | 2011-05-13 | 0.45205 | 13.93 | 71.96 | 301.19 | 1.22 | 0.23 | 0.22 | 0 | 1.67 | 0.01 | 0.001 | 59 | 4.1855
交流220kV | 2009-12-30 | 2010-06-14 | 0.45479 | 5.2 | 82.6 | 456.3 | 1.2 | 0.2 | 0.2 | 0 | 1.6 | 0.005 | 0.001 | 64.4 | 5.5242
交流220kV | 2013-07-27 | 2014-01-09 | 0.45479 | 21.83 | 45.66 | 205.38 | 1.99 | 0.33 | 0.31 | 0 | 2.63 | 0.005 | 0.028 | 70 | 4.498
交流220kV | 2013-09-30 | 2014-03-15 | 0.45479 | 11.93 | 23.09 | 175.46 | 1.01 | 0 | 0.11 | 0 | 1.12 | 0.007 | 0.04 | 68 | 7.599
交流220kV | 2013-07-27 | 2014-01-09 | 0.45479 | 24.2 | 51.6 | 203.07 | 1.94 | 0.6 | 0 | 0 | 2.54 | 0.006 | 0.053 | 71.6 | 3.9355
交流220kV | 2012-07-06 | 2012-12-20 | 0.45753 | 8.67 | 27.78 | 138.41 | 1.64 | 0.34 | 0.3 | 0 | 2.28 | 0 | 0 | 0 | 4.9824
交流220kV | 2012-12-31 | 2013-06-17 | 0.46027 | 57.7 | 95.5 | 374 | 3.2 | 0.2 | 0.4 | 0 | 3.8 | 0 | 0 | 0 | 3.9162
交流220kV | 2011-06-28 | 2011-12-13 | 0.46027 | 29.9 | 83 | 216 | 1.3 | 0 | 0 | 0 | 1.3 | 0 | 0 | 0 | 2.6024
交流220kV | 2011-10-14 | 2012-03-30 | 0.46027 | 8.79 | 44.05 | 572.11 | 3.86 | 0 | 0 | 0 | 3.86 | 0.003 | 0.07 | 54 | 12.9877
交流220kV | 2012-06-23 | 2012-12-11 | 0.46849 | 0.8 | 39.6 | 503.5 | 1.4 | 0.1 | 0.1 | 0 | 1.6 | 0 | 0 | 0 | 12.7146
交流220kV | 2011-06-26 | 2011-12-16 | 0.47397 | 17.5 | 48 | 443.9 | 1.8 | 0.2 | 0.4 | 0 | 2.4 | 0 | 0 | 0 | 9.2479
交流220kV | 2013-06-27 | 2013-12-17 | 0.47397 | 20.2 | 52.1 | 320.8 | 1 | 0 | 0 | 0 | 1 | 0.03 | 0.7 | 48 | 6.1574
交流220kV | 2012-06-20 | 2012-12-11 | 0.47671 | 6.2 | 87.2 | 448.1 | 1.7 | 0.3 | 0.2 | 0 | 2.2 | 0 | 0 | 0 | 5.1388
交流220kV | 2012-10-10 | 2013-04-02 | 0.47671 | 9.1 | 63.7 | 245.9 | 1 | 0.1 | 0 | 0.1 | 1.2 | 0 | 0 | 0 | 3.8603
交流220kV | 2012-10-10 | 2013-04-02 | 0.47671 | 9 | 64.2 | 218.7 | 0.7 | 0.1 | 0 | 0.1 | 0.9 | 0.006 | 0.06 | 56.2 | 3.4065
交流220kV | 2011-10-25 | 2012-04-16 | 0.47671 | 4 | 38 | 264 | 1.11 | 0.39 | 3.48 | 0 | 4.98 | 0.003 | 0.05 | 59 | 6.9474
交流220kV | 2011-06-30 | 2011-12-22 | 0.47945 | 16.7 | 36.62 | 210.46 | 2.33 | 0.28 | 0 | 0 | 2.61 | 0 | 0 | 0 | 5.7471
交流220kV | 2009-07-31 | 2010-01-22 | 0.47945 | 38 | 139 | 343 | 5.1 | 0.5 | 1.2 | 0 | 6.8 | 0.005 | 0.004 | 53 | 2.4676
交流220kV | 2009-12-14 | 2010-06-11 | 0.49041 | 5.69 | 57.13 | 173.12 | 0.76 | 0.63 | 1.46 | 0.15 | 3 | 0.006 | 0.29 | 71.3 | 3.0303
交流220kV | 2010-12-23 | 2011-06-22 | 0.49589 | 9.02 | 71.08 | 328.36 | 7.29 | 8.49 | 1.38 | 0 | 17.16 | 0.01 | 0 | 60 | 4.6196
交流220kV | 2012-05-26 | 2012-11-23 | 0.49589 | 11.78 | 70.32 | 264.6 | 1.52 | 0.19 | 0.3 | 0.07 | 2.08 | 0.002 | 0.02 | 45 | 3.7628
交流220kV | 2011-09-21 | 2012-03-20 | 0.49589 | 6.2 | 23.77 | 307.8 | 1.1 | 0.1 | 0.19 | 0.05 | 1.44 | 0.006 | 0.099 | 65.2 | 12.9491
交流220kV | 2011-10-28 | 2012-04-27 | 0.49863 | 3 | 38.5 | 171.6 | 0.4 | 0 | 0 | 0 | 0.4 | 0.004 | 0.034 | 53.2 | 4.4571
交流220kV | 2011-10-28 | 2012-04-27 | 0.49863 | 3.9 | 33.8 | 113.5 | 0.4 | 0 | 0 | 0 | 0.4 | 0.006 | 0.033 | 57.2 | 3.358
交流220kV | 2011-08-26 | 2012-02-24 | 0.49863 | 35.86 | 61.7 | 257.25 | 1.26 | 0.38 | 0.39 | 0 | 2.03 | 0.021 | 0 | 57.2 | 4.1694
交流220kV | 2011-08-25 | 2012-02-24 | 0.50137 | 28.68 | 43.53 | 277.84 | 0.95 | 0.75 | 1.18 | 0 | 2.88 | 0.021 | 0.001 | 57.6 | 6.3827
交流220kV | 2012-06-04 | 2012-12-05 | 0.50411 | 15.4 | 101.3 | 217.8 | 1.5 | 0.2 | 0.2 | 0 | 1.9 | 0 | 0 | 0 | 2.15
交流220kV | 2013-06-08 11:57 | 2013-12-10 | 0.50549 | 40.2 | 166.3 | 831.1 | 2.8 | 0.5 | 0.7 | 0 | 4 | 0 | 0 | 0 | 4.9976
220 | 2011-09-26 | 2012-03-31 | 0.51233 | 5.94 | 46.62 | 203.01 | 0.57 | 0.32 | 0.14 | 0 | 1.03 | 0.011 | 0.002 | 58 | 4.3546
交流220kV | 2010-12-24 | 2011-06-30 | 0.51507 | 4 | 47 | 531 | 1.16 | 0.96 | 0.28 | 0 | 2.4 | 0.006 | 0.15 | 55 | 11.2979
交流220kV | 2011-04-28 | 2011-11-02 | 0.51507 | 16 | 195 | 733 | 2 | 0.2 | 0.2 | 0 | 2.4 | 0.007 | 0.002 | 54 | 3.759
交流220kV | 2013-06-06 | 2013-12-12 | 0.51781 | 7.1 | 70.5 | 334.1 | 1.1 | 0 | 0 | 0 | 1.1 | 0 | 0 | 0 | 4.739
交流220kV | 2011-05-10 | 2011-11-15 | 0.51781 | 12 | 182 | 431 | 4.2 | 1.4 | 0.6 | 0 | 6.2 | 0.003 | 0.001 | 40 | 2.3681
交流220kV | 2011-05-10 | 2011-11-15 | 0.51781 | 16 | 813 | 492 | 31.2 | 2.8 | 3.9 | 0.2 | 38.1 | 0.003 | 0.001 | 54 | 0.60517
交流220kV | 2012-07-21 | 2013-01-31 | 0.53151 | 49.32 | 103.75 | 516.25 | 1.58 | 0.29 | 0.3 | 0 | 2.17 | 0.003 | 0 | 52 | 4.9759
交流220kV | 2011-11-10 | 2012-05-23 | 0.53425 | 2 | 72 | 843 | 4.9 | 0 | 0.9 | 0 | 5.8 | 0.067 | 0.071 | 61.6 | 11.7083
交流220kV | 2012-03-17 | 2012-09-28 | 0.53425 | 32 | 85 | 481 | 1.2 | 0.2 | 0.2 | 0 | 1.6 | 0.022 | 0.02 | 60 | 5.6588
交流220kV | 2013-05-26 | 2013-12-12 | 0.54795 | 34.78 | 217.23 | 1064.82 | 4.19 | 0.6 | 0.6 | 0 | 5.39 | 0 | 0.001 | 63 | 4.9018
交流220kV | 2012-05-26 | 2012-12-14 | 0.55342 | 7.63 | 58.26 | 200.81 | 1.39 | 0.36 | 0.44 | 0 | 2.19 | 0.001 | 0.2 | 41 | 3.4468
交流220kV | 2011-09-27 | 2012-04-16 | 0.55342 | 24 | 85 | 375 | 33.57 | 42.74 | 10.42 | 3.69 | 90.42 | 0.003 | 0.07 | 52 | 4.4118
交流220kV | 2011-05-31 | 2011-12-20 | 0.55616 | 21.18 | 111.81 | 287.4 | 2.91 | 2.68 | 0.33 | 0 | 5.92 | 0 | 0 | 35.1 | 2.5704
交流220kV | 2010-09-19 | 2011-04-11 | 0.5589 | 1 | 40 | 157 | 0.52 | 0 | 0 | 0 | 0.52 | 0.003 | 0.046 | 54 | 3.925
交流220kV | 2010-09-19 | 2011-04-11 | 0.5589 | 1 | 30 | 207 | 0.23 | 0.13 | 0 | 0 | 0.36 | 0.003 | 0.051 | 60 | 6.9
交流220kV | 2012-09-17 | 2013-04-09 | 0.5589 | 8.72 | 36.35 | 202.94 | 0.7 | 0.25 | 0 | 0 | 0.95 | 0.03 | 0.003 | 51 | 5.5829
交流220kV | 2011-07-28 | 2012-02-17 | 0.5589 | 16.75 | 112.82 | 245.14 | 1.49 | 0.27 | 0.45 | 0 | 2.21 | 0.021 | 0.001 | 62.5 | 2.1728
220 | 2011-11-28 | 2012-06-20 | 0.56164 | 0.4 | 17.31 | 262.88 | 0.71 | 0.38 | 0 | 0 | 1.09 | 0.008 | 0.001 | 60 | 15.1866
交流220kV | 2011-08-21 12:43 | 2012-03-14 | 0.56293 | 12.41 | 65.69 | 214.21 | 0.92 | 0.11 | 0.11 | 0 | 1.14 | 0.068 | 0.001 | 50.5 | 3.2609
交流220kV | 2012-06-19 | 2013-01-11 | 0.56438 | 12.39 | 5.3 | 355.03 | 1.2 | 0.89 | 1.28 | 0 | 3.37 | 0.013 | 1.075 | 60 | 66.9868
交流220kV | 2011-12-30 | 2012-07-23 | 0.56438 | 16.33 | 40.44 | 227.87 | 0.95 | 0.32 | 0.33 | 0 | 1.6 | 0.005 | 0.001 | 60 | 5.6348
交流220kV | 2012-10-22 | 2013-05-17 | 0.56712 | 14 | 231 | 1487 | 7.3 | 0 | 0 | 0 | 7.3 | 0.002 | 0.119 | 58 | 6.4372
交流220kV | 2012-09-17 | 2013-04-13 | 0.56986 | 13.39 | 55.75 | 420.83 | 2.47 | 0.33 | 0.2 | 0 | 3 | 0.008 | 0.071 | 60 | 7.5485
交流220kV | 2012-09-16 | 2013-04-13 | 0.5726 | 11.75 | 31 | 310.15 | 1.78 | 0.25 | 0.2 | 0 | 2.23 | 0.009 | 0.025 | 55 | 10.0048
交流220kV | 2011-05-19 09:04 | 2011-12-16 | 0.57705 | 23.79 | 147 | 876 | 2.47 | 0.45 | 0.54 | 0 | 3.46 | 0 | 0 | 0 | 5.9592
交流220kV | 2012-07-04 | 2013-02-01 | 0.58082 | 13 | 62 | 154 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 2.4839
交流220kV | 2011-03-28 | 2011-10-27 | 0.58356 | 10.86 | 147.26 | 622.24 | 10.29 | 0.49 | 0 | 0 | 10.78 | 0 | 0 | 0 | 4.2255
交流220kV | 2011-07-07 | 2012-02-06 | 0.5863 | 12.5 | 80.1 | 421.7 | 1.6 | 0.4 | 0.3 | 0 | 2.3 | 0.006 | 0.046 | 62.1 | 5.2647
交流220kV | 2011-09-14 | 2012-04-17 | 0.59178 | 8.53 | 29.95 | 202.48 | 1.06 | 0.14 | 1.8 | 0 | 3 | 0.005 | 0.007 | 82 | 6.7606
交流220kV | 2009-12-14 | 2010-07-23 | 0.60548 | 10.55 | 122.79 | 298.55 | 1.21 | 0.16 | 0.15 | 0 | 1.52 | 0.013 | 0.105 | 63 | 2.4314
交流220kV | 2013-03-26 | 2013-11-04 | 0.61096 | 3.19 | 62.62 | 228.69 | 1.46 | 0.15 | 0.09 | 0.12 | 1.82 | 0.009 | 0.058 | 68 | 3.652
交流220kV | 2013-03-26 | 2013-11-04 | 0.61096 | 140.03 | 87.93 | 455.37 | 9.08 | 0.14 | 1.31 | 0 | 10.53 | 0.012 | 0.047 | 69 | 5.1788
交流220kV | 2012-10-15 | 2013-05-27 | 0.6137 | 10.8 | 92 | 335.1 | 2 | 0.4 | 0.4 | 0 | 2.8 | 0.007 | 0 | 59.2 | 3.6424
交流220kV | 2012-10-12 | 2013-05-24 | 0.6137 | 11.8 | 35 | 190.5 | 1.3 | 0.2 | 0.2 | 0 | 1.7 | 0.01 | 0 | 58.4 | 5.4429
交流220kV | 2013-04-28 | 2013-12-10 | 0.61918 | 51.9 | 166.2 | 1012.2 | 2.8 | 0.4 | 0.7 | 0 | 3.9 | 0 | 0 | 0 | 6.0903
交流220kV | 2011-11-15 | 2012-06-29 | 0.62192 | 47.8 | 187.5 | 1 | 0.4 | 0.2 | 0 | 0 | 0.6 | 0.009 | 0.06 | 55.3 | 0.0053333
交流220kV | 2013-01-25 | 2013-09-10 | 0.62466 | 8.1 | 102.18 | 456.59 | 1.89 | 0.71 | 0.25 | 0 | 2.85 | 0 | 0 | 0 | 4.4685
交流220kV | 2010-11-15 | 2011-07-01 | 0.62466 | 14.45 | 219.99 | 681.89 | 3.27 | 0 | 0 | 0 | 3.27 | 0 | 0 | 0 | 3.0996
交流220kV | 2011-09-29 | 2012-05-16 | 0.63014 | 12 | 159 | 338 | 2.1 | 0.5 | 0.8 | 0 | 3.4 | 0.07 | 0 | 54 | 2.1258
交流220kV | 2011-05-31 | 2012-01-16 | 0.63014 | 7 | 43 | 344 | 7.56 | 0.07 | 0.09 | 0 | 7.72 | 0.001 | 0.001 | 59.7 | 8
交流220kV | 2011-09-29 | 2012-05-20 | 0.6411 | 16 | 168 | 388 | 1.85 | 0 | 0 | 0 | 1.85 | 0.08 | 0 | 51 | 2.3095
交流220kV | 2011-04-25 08:44 | 2011-12-16 | 0.64284 | 16.42 | 99.65 | 684.17 | 2.06 | 0.31 | 0.4 | 0 | 2.77 | 0 | 0 | 0 | 6.8657
220 | 2013-03-31 | 2013-11-25 | 0.65479 | 9.15 | 83.5 | 385.9 | 1.4 | 1.12 | 0.35 | 0 | 2.87 | 0.006 | 0.056 | 58 | 4.6216
220 | 2013-03-31 | 2013-11-25 | 0.65479 | 18.5 | 125.11 | 296.9 | 1.69 | 0.22 | 0.42 | 0 | 2.33 | 0.006 | 0.052 | 56 | 2.3731
交流220kV | 2012-08-15 | 2013-04-12 | 0.65753 | 26.25 | 62.02 | 462.99 | 0.52 | 0.12 | 0.15 | 0 | 0.79 | 0.004 | 0.003 | 58.2 | 7.4652
交流220kV | 2012-08-15 | 2013-04-12 | 0.65753 | 24.48 | 158.68 | 430.01 | 2.23 | 0.32 | 0.32 | 0 | 2.87 | 0.006 | 0.002 | 42.9 | 2.7099
交流220kV | 2011-08-30 | 2012-04-28 | 0.66301 | 25 | 46 | 181 | 25 | 0 | 0 | 0 | 25 | 0.034 | 0.45 | 44 | 3.9348
交流220kV | 2011-07-13 | 2012-03-12 | 0.66575 | 17.55 | 132.7 | 349.56 | 1.88 | 0 | 0 | 0 | 1.88 | 0 | 0 | 0 | 2.6342
交流220kV | 2012-09-13 | 2013-05-14 | 0.66575 | 11.01 | 29.9 | 290.9 | 5.01 | 2.18 | 1.66 | 0 | 8.85 | 0.007 | 0.202 | 60 | 9.7291
交流220kV | 2009-05-19 | 2010-01-18 | 0.66849 | 29 | 269 | 701 | 9.5 | 0.4 | 0.6 | 0 | 10.5 | 0.012 | 0.002 | 51 | 2.6059
交流220kV | 2012-07-25 | 2013-03-26 | 0.66849 | 10.35 | 92.92 | 244.4 | 1.22 | 0 | 0 | 0 | 1.22 | 0.009 | 0.022 | 55.4 | 2.6302
交流220kV | 2012-07-25 | 2013-03-26 | 0.66849 | 10.53 | 71.45 | 267.63 | 1.14 | 0 | 0 | 0 | 1.14 | 0.009 | 0.024 | 56.2 | 3.7457
交流220kV | 2007-10-31 | 2008-07-02 | 0.67123 | 16.56 | 128.24 | 414.01 | 1.42 | 0.41 | 0.58 | 0.07 | 2.48 | 0.008 | 0.001 | 62.4 | 3.2284
交流220kV | 1997-02-24 | 1997-10-28 | 0.67397 | 11.39 | 76.5 | 206.5 | 0.93 | 0.25 | 0.61 | 0.07 | 1.86 | 0.003 | 0.002 | 50 | 2.6993
交流220kV | 2013-04-01 | 2013-12-10 | 0.69315 | 12.31 | 193.18 | 821.67 | 3.16 | 0.72 | 0.48 | 0 | 4.36 | 0 | 0 | 0 | 4.2534
交流220kV | 2010-09-29 | 2011-06-09 | 0.69315 | 10 | 70 | 350 | 1.8 | 0.8 | 0 | 0 | 2.6 | 0.003 | 0.001 | 50 | 5
交流220kV | 2011-01-28 | 2011-10-10 | 0.69863 | 32.94 | 195 | 395 | 5.23 | 0.88 | 0.55 | 0.37 | 7.03 | 0.021 | 0.052 | 54.1 | 2.0256
交流220kV | 2012-03-22 | 2012-12-05 | 0.70685 | 11 | 130 | 322 | 2 | 0 | 0 | 0 | 2 | 0 | 0 | 0 | 2.4769
交流220kV | 2009-07-03 | 2010-03-18 | 0.70685 | 1.5 | 11.2 | 639.9 | 0.9 | 0.2 | 0.3 | 0 | 1.4 | 0.003 | 0.224 | 58.5 | 57.1339
交流220kV | 2011-06-25 15:41 | 2012-03-12 | 0.71328 | 12.27 | 60.39 | 144.22 | 1.15 | 0.25 | 0.16 | 0.56 | 2.12 | 0.009 | 0.001 | 52.9 | 2.3881
交流220kV | 2011-06-25 15:32 | 2012-03-12 | 0.7133 | 6.43 | 80.09 | 255.76 | 1.12 | 0.14 | 0.12 | 0 | 1.38 | 0.013 | 0.001 | 57.1 | 3.1934
交流220kV | 2013-04-03 | 2013-12-23 | 0.72329 | 24.27 | 112.1 | 434.57 | 1.92 | 0.29 | 0.39 | 0 | 2.6 | 0.012 | 0.044 | 60 | 3.8766
交流220kV | 2013-04-03 | 2013-12-23 | 0.72329 | 27.17 | 90.06 | 376.31 | 1.8 | 0.24 | 0 | 0 | 2.04 | 0.011 | 0.069 | 62 | 4.1784
交流220kV | 2010-07-23 | 2011-04-14 | 0.72603 | 33 | 78 | 219 | 41.38 | 46.85 | 12.08 | 0.6 | 100.91 | 0.001 | 0.001 | 50 | 2.8077
交流220kV | 2011-05-31 | 2012-02-22 | 0.73151 | 9 | 77 | 292 | 8.36 | 0.18 | 0.21 | 0 | 8.75 | 0.001 | 0.003 | 57.5 | 3.7922
交流220kV | 2010-12-28 | 2011-09-21 | 0.73151 | 34.49 | 84 | 348 | 1.12 | 0 | 0.23 | 0 | 1.35 | 0.021 | 0.026 | 55 | 4.1429
交流220kV | 2011-03-28 | 2011-12-22 | 0.73699 | 7.27 | 139.24 | 529.18 | 10.28 | 1.16 | 0 | 0 | 11.44 | 0 | 0 | 0 | 3.8005
交流220kV | 2013-01-29 | 2013-10-26 | 0.73973 | 10.1 | 45 | 691 | 1.4 | 0 | 0 | 0 | 1.4 | 0.006 | 0.001 | 47 | 15.3556
交流220kV | 2011-06-30 | 2012-03-28 | 0.74521 | 14.61 | 40.93 | 266.17 | 2.72 | 0.24 | 0 | 0 | 2.96 | 0 | 0 | 0 | 6.5031
交流220kV | 2013-03-31 | 2013-12-30 | 0.75068 | 9.45 | 48.02 | 197.11 | 0.81 | 0.14 | 0.11 | 0 | 1.06 | 0 | 0 | 0 | 4.1047
交流220kV | 2011-06-21 | 2012-03-22 | 0.75342 | 14.49 | 349.93 | 2891.76 | 17.22 | 17.23 | 3.09 | 0.8 | 38.34 | 0.019 | 0.155 | 57 | 8.2638
交流220kV | 2011-06-28 | 2012-03-30 | 0.75616 | 25.1 | 92.9 | 269.8 | 1.3 | 0.2 | 0.2 | 0 | 1.7 | 0.008 | 2.4 | 55 | 2.9042
交流220kV | 2012-07-05 | 2013-04-07 | 0.75616 | 17 | 201 | 809 | 2.2 | 0.4 | 0.3 | 0 | 2.9 | 0.009 | 0.1 | 58 | 4.0249
交流220kV | 2011-03-17 | 2011-12-20 | 0.76164 | 10.8 | 91.8 | 449.7 | 1.4 | 0.1 | 0 | 0 | 1.5 | 0.006 | 0 | 66.2 | 4.8987
交流220kV | 2011-03-17 | 2011-12-20 | 0.76164 | 21.4 | 82.1 | 305.5 | 1.5 | 0.2 | 0 | 0 | 1.7 | 0.008 | 0 | 61.5 | 3.7211
交流220kV | 2011-07-07 | 2012-04-11 | 0.76438 | 18.7 | 174.92 | 473.34 | 2.59 | 0.25 | 1.2 | 0 | 4.04 | 0.013 | 0.1 | 56 | 2.706
交流220kV | 2011-07-05 | 2012-04-11 | 0.76986 | 6.58 | 106.89 | 504.3 | 1.83 | 0.32 | 0.4 | 0 | 2.55 | 0.014 | 0.2 | 55 | 4.7179
交流220kV | 2010-11-28 | 2011-09-07 | 0.77534 | 26.97 | 53.61 | 495.85 | 1.54 | 0.26 | 0 | 0 | 1.8 | 0 | 0 | 0 | 9.2492
交流220kV | 2010-12-30 | 2011-10-11 | 0.78082 | 62.09 | 160.85 | 179.86 | 1.98 | 0.24 | 0.35 | 0 | 2.57 | 0.003 | 0.02 | 46 | 1.1182
交流220kV | 2011-12-28 | 2012-10-10 | 0.7863 | 15.74 | 98.61 | 345.1 | 1.07 | 0.24 | 0.35 | 0 | 1.66 | 0.042 | 0.051 | 46 | 3.4996
交流220kV | 2012-12-10 | 2013-09-25 | 0.79178 | 29.76 | 47.23 | 382.15 | 3.05 | 0.35 | 2.34 | 0 | 5.74 | 0 | 0 | 56.4 | 8.0913
交流220kV | 2011-07-01 | 2012-04-16 | 0.79452 | 6.95 | 84.31 | 196.26 | 0.98 | 0.07 | 0.25 | 0 | 1.3 | 0.01 | 0.07 | 69 | 2.3278
交流220kV | 2010-05-27 | 2011-03-14 | 0.79726 | 149.25 | 85.62 | 313.28 | 8.75 | 0.28 | 1.42 | 0 | 10.45 | 0.011 | 0.006 | 52 | 3.659
交流220kV | 2010-07-23 | 2011-05-10 | 0.79726 | 19.9 | 52.26 | 258.33 | 1.2 | 0.1 | 0.11 | 0 | 1.41 | 0.01 | 0.001 | 59 | 4.9432
交流220kV | 2011-05-19 | 2012-03-06 | 0.8 | 25.18 | 210.73 | 425.99 | 2.23 | 0.32 | 0.94 | 0 | 3.49 | 0.007 | 0.089 | 64.2 | 2.0215
交流220kV | 2011-01-20 | 2011-11-09 | 0.80274 | 21.45 | 166 | 429 | 1.75 | 0.2 | 0.23 | 0 | 2.18 | 0.023 | 0.045 | 55.8 | 2.5843
交流220kV | 2011-05-28 | 2012-03-17 | 0.80548 | 20.09 | 107.97 | 455.23 | 1.51 | 0.31 | 0.35 | 0 | 2.17 | 0.005 | 0.06 | 61 | 4.2163
交流220kV | 2011-05-28 | 2012-03-17 | 0.80548 | 10.12 | 80.36 | 414.66 | 1.45 | 0.33 | 0.34 | 0 | 2.12 | 0.005 | 0.06 | 61 | 5.16
交流220kV | 2011-05-23 | 2012-03-13 | 0.80822 | 30 | 300 | 578 | 6.54 | 0.5 | 1.03 | 0 | 8.07 | 0.016 | 0.047 | 50.6 | 1.9267
交流220kV | 2012-06-29 | 2013-04-22 | 0.8137 | 23.2 | 33.3 | 227.9 | 2.8 | 0 | 3 | 0 | 5.8 | 0.032 | 0 | 55 | 6.8438
220 | 2011-06-16 | 2012-04-09 | 0.81644 | 80.12 | 131.62 | 474.78 | 2.11 | 0.2 | 0.39 | 0 | 2.7 | 0.006 | 0.068 | 54 | 3.6072
220 | 2011-06-16 | 2012-04-09 | 0.81644 | 70.94 | 103.71 | 433.73 | 1.92 | 0.14 | 0.33 | 0 | 2.39 | 0.006 | 0.093 | 56 | 4.1821
交流220kV | 2011-07-01 | 2012-04-24 | 0.81644 | 7.85 | 96.46 | 203.18 | 1.05 | 0.1 | 0.21 | 0 | 1.36 | 0.009 | 0.05 | 68 | 2.1064
交流220kV | 2010-11-30 | 2011-09-28 | 0.8274 | 16 | 119 | 416 | 1.44 | 0.29 | 1.64 | 0 | 3.37 | 0.028 | 0.08 | 59.4 | 3.4958
交流220kV | 2011-12-13 | 2012-10-10 | 0.8274 | 44 | 134 | 428 | 1.5 | 0.2 | 0.2 | 0 | 1.9 | 0.008 | 0.1 | 62 | 3.194
交流220kV | 2011-12-13 | 2012-10-10 | 0.8274 | 38 | 137 | 466 | 1.5 | 0.1 | 0.2 | 0 | 1.8 | 0.007 | 0.1 | 61 | 3.4015
交流220kV | 2012-06-20 | 2013-04-22 | 0.83836 | 3 | 37 | 319 | 0.66 | 0 | 0.15 | 0 | 0.81 | 0.003 | 0.061 | 52 | 8.6216
交流220kV | 2013-05-15 | 2014-03-18 | 0.8411 | 10 | 313 | 423 | 23.07 | 3.52 | 5.46 | 0 | 32.05 | 0.001 | 0.14 | 50 | 1.3514
交流220kV | 2011-07-16 | 2012-05-21 | 0.84932 | 8.13 | 132.42 | 455.31 | 1.51 | 0.24 | 0.21 | 0 | 1.96 | 0.028 | 0.36 | 59 | 3.4384
交流220kV | 2011-05-31 | 2012-04-06 | 0.85205 | 20.85 | 143.3 | 360.81 | 1.74 | 0 | 0.26 | 0 | 2 | 0 | 0 | 0 | 2.5179
交流220kV | 2011-07-14 | 2012-05-21 | 0.85479 | 10.79 | 156.39 | 286.21 | 3.22 | 1.7 | 2.39 | 0.07 | 7.38 | 0.012 | 0.12 | 55 | 1.8301
交流220kV | 2011-06-30 | 2012-05-08 | 0.85753 | 11.77 | 41.27 | 297.47 | 2.79 | 0.25 | 0 | 0 | 3.04 | 0 | 0.098 | 62.4 | 7.2079
交流220kV | 2013-01-27 | 2013-12-10 | 0.86849 | 20.3 | 253.1 | 695.5 | 3.66 | 0.2 | 0.29 | 0 | 4.15 | 0 | 0 | 0 | 2.7479
交流220kV | 2012-07-11 | 2013-05-24 | 0.86849 | 37.87 | 137.41 | 565.58 | 3.62 | 0.64 | 2.42 | 0 | 6.68 | 0.009 | 0.057 | 61 | 4.116
交流220kV | 2010-09-01 | 2011-07-15 | 0.86849 | 15.34 | 152.04 | 505.67 | 2.51 | 0.14 | 1.34 | 0 | 3.99 | 0.01 | 0.006 | 49 | 3.3259
交流220kV | 2012-06-10 | 2013-04-27 | 0.87945 | 10 | 65 | 271.7 | 0.7 | 0 | 0 | 0 | 0.7 | 0 | 0 | 0 | 4.18
交流220kV | 2012-06-10 | 2013-04-27 | 0.87945 | 10.1 | 70.8 | 311 | 0.8 | 0 | 0 | 0 | 0.8 | 0 | 0 | 0 | 4.3927
交流220kV | 2010-09-01 | 2011-07-20 | 0.88219 | 14.65 | 144.76 | 527.24 | 2.51 | 0.13 | 1.6 | 0 | 4.24 | 0.03 | 0 | 50 | 3.6422
交流220kV | 2012-12-05 | 2013-10-25 | 0.88767 | 13 | 36 | 580 | 1.8 | 0.3 | 0.2 | 0 | 2.3 | 0.036 | 0.002 | 65 | 16.1111
交流220kV | 2011-10-21 | 2012-09-11 | 0.89315 | 10.73 | 87.65 | 384.67 | 1.56 | 0.32 | 0.3 | 0 | 2.18 | 0.025 | 0.419 | 44 | 4.3887
交流220kV | 2012-06-05 | 2013-04-28 | 0.89589 | 23.34 | 149.51 | 372.14 | 2.13 | 0.47 | 0.49 | 0 | 3.09 | 0.07 | 0.001 | 58 | 2.4891
交流220kV | 2013-01-25 | 2013-12-19 | 0.89863 | 12.36 | 16.48 | 47.12 | 2.49 | 0 | 0 | 0 | 2.49 | 0 | 0 | 70.1 | 2.8592
交流220kV | 2011-10-21 | 2012-09-13 | 0.89863 | 16.71 | 74.8 | 290.54 | 1.32 | 0.21 | 0.32 | 0 | 1.85 | 0.027 | 0.087 | 46 | 3.8842
交流220kV | 2010-11-17 | 2011-10-12 | 0.90137 | 62 | 668 | 230 | 20 | 2.3 | 7.3 | 0 | 29.6 | 0.001 | 0.002 | 44 | 0.34431
交流220kV | 2012-12-31 | 2013-11-26 | 0.90411 | 0.3 | 145.75 | 563.8 | 2.81 | 0.27 | 0.56 | 0 | 3.64 | 0.003 | 0.2 | 41 | 3.8683
交流220kV | 2012-10-10 | 2013-09-09 | 0.91507 | 24.7 | 156.2 | 692.6 | 2.3 | 0.8 | 0.8 | 1.8 | 5.7 | 0 | 0 | 56.2 | 4.4341
交流220kV | 2012-07-06 | 2013-06-06 | 0.91781 | 61.61 | 81.77 | 315.14 | 2.52 | 0.32 | 0.26 | 0 | 3.1 | 0 | 0 | 0 | 3.854
交流220kV | 2011-04-20 | 2012-03-20 | 0.91781 | 10.53 | 98.04 | 530.58 | 1.53 | 0.11 | 0.16 | 0 | 1.8 | 0.004 | 0.001 | 55.3 | 5.4119
交流220kV | 2011-04-20 | 2012-03-20 | 0.91781 | 6.96 | 81.29 | 328.87 | 1.39 | 0.1 | 0.14 | 0 | 1.63 | 0.003 | 0.001 | 54.8 | 4.0456
交流220kV | 2012-12-31 | 2013-12-04 | 0.92603 | 27.3 | 117 | 478 | 1.9 | 0.3 | 0.3 | 0 | 2.5 | 0.05 | 0.5 | 48 | 4.0855
交流220kV | 2011-07-13 | 2012-06-15 | 0.92603 | 20.31 | 350.7 | 542.56 | 2 | 0 | 0 | 0 | 2 | 0 | 0 | 0 | 1.5471
交流220kV | 2010-12-23 | 2011-11-27 | 0.92877 | 8.1 | 71 | 327 | 9.46 | 9.62 | 2.35 | 0 | 21.43 | 0.021 | 0 | 56.6 | 4.6056
交流220kV | 2012-05-15 | 2013-04-19 | 0.92877 | 7 | 60 | 314 | 0.3 | 0.29 | 0 | 0 | 0.59 | 0.003 | 0.12 | 60 | 5.2333
交流220kV | 2010-12-23 | 2011-11-28 | 0.93151 | 8.1 | 196.35 | 510.25 | 9.46 | 9.62 | 2.35 | 0 | 21.43 | 0.021 | 0 | 56.6 | 2.5987
交流220kV | 2011-06-28 | 2012-06-05 | 0.93973 | 11.64 | 111.67 | 496.44 | 1.04 | 0.23 | 0 | 0 | 1.27 | 0.007 | 0.048 | 58.1 | 4.4456
交流220kV | 2011-06-28 | 2012-06-05 | 0.93973 | 67.16 | 55.56 | 307.8 | 0.8 | 0 | 0 | 0 | 0.8 | 0.004 | 0.14 | 52.3 | 5.54
交流220kV | 2011-10-12 | 2012-09-19 | 0.93973 | 13.05 | 80.24 | 460.37 | 1.88 | 0.21 | 0.25 | 0 | 2.34 | 0.009 | 0.031 | 65.3 | 5.7374
交流220kV | 2011-10-12 | 2012-09-19 | 0.93973 | 14.88 | 105.76 | 505.48 | 2.01 | 0.21 | 0.26 | 0 | 2.48 | 0.009 | 0.041 | 63.2 | 4.7795
交流220kV | 2011-05-19 09:04 | 2012-04-27 | 0.94143 | 20.1 | 175.8 | 469.8 | 3.4 | 0.4 | 0.7 | 0 | 4.5 | 0.004 | 0 | 68 | 2.6724
交流220kV | 2011-12-31 | 2012-12-10 | 0.94521 | 28.05 | 116.82 | 346.73 | 1.47 | 0 | 0 | 0 | 1.47 | 0 | 0 | 0 | 2.9681
交流220kV | 2011-09-14 | 2012-08-24 | 0.94521 | 19.58 | 80.57 | 530.69 | 7.97 | 0.25 | 9.96 | 0 | 18.18 | 0.032 | 0.001 | 62 | 6.5867
交流220kV | 2011-12-30 | 2012-12-10 | 0.94795 | 10.15 | 74.03 | 232.38 | 0.69 | 0 | 0 | 0 | 0.69 | 0 | 0 | 0 | 3.139
交流220kV | 2011-12-29 | 2012-12-10 | 0.95068 | 5.57 | 60.15 | 167.56 | 0.61 | 0 | 0 | 0 | 0.61 | 0 | 0 | 0 | 2.7857
交流220kV | 2011-12-29 | 2012-12-10 | 0.95068 | 9.05 | 160.33 | 426.85 | 1.34 | 0 | 0 | 0 | 1.34 | 0 | 0 | 0 | 2.6623
交流220kV | 2010-10-16 | 2011-09-29 | 0.95342 | 20 | 45 | 467 | 1.1 | 0.2 | 0.4 | 0 | 1.7 | 0.016 | 0.002 | 57.2 | 10.3778
交流220kV | 2012-07-01 | 2013-06-15 | 0.95616 | 16.51 | 118.36 | 368.03 | 2.29 | 0.4 | 0.49 | 0 | 3.18 | 0 | 0 | 0 | 3.1094
交流220kV | 2012-07-01 | 2013-06-15 | 0.95616 | 16.51 | 118.36 | 368.03 | 2.29 | 0.4 | 0.49 | 0 | 3.18 | 0 | 0 | 50 | 3.1094
交流220kV | 2011-12-29 | 2012-12-13 | 0.9589 | 19.61 | 125.06 | 371.31 | 1.98 | 0.8 | 0.63 | 0 | 3.41 | 0.004 | 0.001 | 60 | 2.9691
交流220kV | 2010-06-30 | 2011-06-17 | 0.96438 | 16.29 | 103.99 | 427.23 | 4.85 | 0.57 | 10.37 | 0 | 15.79 | 0 | 0 | 0 | 4.1084
交流220kV | 2010-05-20 | 2011-05-11 | 0.97534 | 14 | 89 | 476 | 1.23 | 0.16 | 0.59 | 0 | 1.98 | 0.024 | 0.069 | 58.2 | 5.3483
交流220kV | 2011-10-27 | 2012-10-17 | 0.97534 | 11.86 | 72.49 | 312.9 | 2.22 | 0.12 | 0.22 | 0 | 2.56 | 0.006 | 0.002 | 62 | 4.3165
交流220kV | 2011-10-27 | 2012-10-17 | 0.97534 | 11.86 | 48.29 | 412.03 | 1.32 | 0.16 | 0.17 | 0 | 1.65 | 0.009 | 0.003 | 60 | 8.5324
交流220kV | 2011-06-28 | 2012-06-20 | 0.98082 | 22.2 | 105.2 | 380.1 | 2.2 | 0.3 | 0.7 | 0 | 3.2 | 0 | 0.05 | 56.2 | 3.6131
交流220kV | 2012-06-04 | 2013-05-28 | 0.98082 | 17.1 | 135 | 308.3 | 3.6 | 0.4 | 2.9 | 0 | 6.9 | 0.005 | 0 | 70.4 | 2.2837
交流220kV | 2011-01-12 | 2012-01-09 | 0.99178 | 4.53 | 290.75 | 2050.11 | 14 | 13.38 | 2.41 | 0 | 29.79 | 0.01 | 0.178 | 49.6 | 7.0511
交流220kV | 2011-01-12 | 2012-01-09 | 0.99178 | 9.88 | 546.15 | 2061.1 | 18.26 | 36.22 | 8.06 | 0 | 62.54 | 0.007 | 0.025 | 47.5 | 3.7739
交流220kV | 2010-12-23 | 2011-12-21 | 0.99452 | 7.66 | 281.72 | 652.02 | 8.29 | 5.61 | 1.82 | 0 | 15.72 | 0 | 0 | 0 | 2.3144
交流220kV | 2012-05-26 | 2013-05-24 | 0.99452 | 15.28 | 72.33 | 264.57 | 2.5 | 0.22 | 0.28 | 0 | 3 | 0.003 | 0.25 | 54 | 3.6578
交流220kV | 2012-10-10 | 2013-10-08 | 0.99452 | 23 | 162.3 | 748.1 | 2.6 | 0.8 | 0.6 | 1.5 | 5.5 | 0 | 0 | 0 | 4.6094
交流220kV | 2011-12-30 | 2012-12-27 | 0.99452 | 8 | 7 | 9 | 0.2 | 0.1 | 0.2 | 0 | 0.5 | 0.014 | 0.23 | 56 | 1.2857
交流220kV | 2011-12-30 | 2012-12-27 | 0.99452 | 9 | 5 | 6 | 0.2 | 0.1 | 0.1 | 0 | 0.4 | 0.025 | 0.23 | 55 | 1.2
交流220kV | 2012-07-04 | 2013-07-03 | 0.99726 | 23 | 121 | 210 | 2 | 0 | 0 | 0 | 2 | 0.062 | 0.038 | 53 | 1.7355
交流220kV | 2010-12-11 16:57 | 2011-12-12 | 1.0008 | 8 | 236.4 | 2746.6 | 9.1 | 9.9 | 3.5 | 0 | 22.5 | 0 | 0 | 0 | 11.6184
交流220kV | 2011-03-28 | 2012-03-28 | 1.0027 | 5.61 | 138.78 | 564.26 | 11.28 | 0.51 | 0 | 0 | 11.79 | 0 | 0 | 0 | 4.0659
交流220kV | 2011-12-04 | 2012-12-04 | 1.0027 | 9.74 | 79.84 | 411.58 | 1.45 | 0.19 | 0.16 | 0.05 | 1.85 | 0.012 | 0.005 | 62 | 5.1551
交流220kV | 2011-12-04 | 2012-12-04 | 1.0027 | 7.31 | 90.63 | 449.88 | 1.55 | 0.14 | 0.13 | 0 | 1.82 | 0.008 | 0.003 | 60 | 4.9639
交流220kV | 2011-04-25 08:44 | 2012-04-27 | 1.0072 | 12.1 | 110.1 | 318.9 | 2.4 | 0.3 | 0.5 | 0 | 3.2 | 0.004 | 0 | 67.9 | 2.8965
交流220kV | 2011-03-17 | 2012-03-19 | 1.0082 | 8.4 | 99.7 | 416.5 | 1.8 | 0.2 | 0.2 | 0 | 2.2 | 0.012 | 0 | 64.2 | 4.1775
交流220kV | 2011-03-17 | 2012-03-19 | 1.0082 | 18.7 | 99.6 | 359.2 | 0.4 | 0 | 0.3 | 0 | 0.7 | 0.012 | 0 | 59.6 | 3.6064
交流220kV | 2012-03-22 | 2013-03-29 | 1.0192 | 12 | 140 | 206 | 2 | 0 | 0 | 0 | 2 | 0 | 0 | 0 | 1.4714
交流220kV | 2010-04-28 | 2011-05-06 | 1.0219 | 10.24 | 302.72 | 1045.6 | 2.06 | 0.45 | 0.25 | 0 | 2.76 | 0.004 | 0.001 | 58.5 | 3.454
交流220kV | 2012-12-27 | 2014-01-07 | 1.0301 | 27 | 7 | 198 | 3.53 | 6.01 | 1.49 | 0 | 11.03 | 0.02 | 0.001 | 74 | 28.2857
交流220kV | 2012-04-21 | 2013-05-03 | 1.0329 | 6.4 | 101 | 684.1 | 2.5 | 0 | 0 | 0 | 2.5 | 0.006 | 0.03 | 54.6 | 6.7733
交流220kV | 2012-04-21 | 2013-05-03 | 1.0329 | 15.5 | 151.9 | 547.6 | 2 | 0.5 | 0.7 | 0 | 3.2 | 0.005 | 0.06 | 55.8 | 3.605
交流220kV | 2012-05-04 | 2013-05-16 | 1.0329 | 15 | 44 | 742 | 2 | 0.2 | 0 | 0 | 2.2 | 0.007 | 0.001 | 50 | 16.8636
交流220kV | 2006-02-21 | 2007-03-07 | 1.0384 | 12.5 | 164.7 | 464.3 | 1.8 | 0 | 0 | 0 | 1.8 | 0.008 | 0.003 | 56 | 2.8191
交流220kV | 2010-11-28 | 2011-12-14 | 1.0438 | 20 | 49.24 | 415.69 | 1.61 | 0.97 | 2.13 | 0 | 4.71 | 0 | 0 | 0 | 8.4421
交流220kV | 2010-04-13 | 2011-04-29 | 1.0438 | 22.37 | 216.37 | 904.38 | 10.29 | 0 | 0 | 0 | 10.29 | 0.005 | 0.158 | 53.9 | 4.1798
交流220kV | 2011-01-22 | 2012-02-07 | 1.0438 | 78.34 | 86.19 | 768.45 | 4.3 | 0.59 | 1.38 | 0 | 6.27 | 0.01 | 0.1 | 67 | 8.9158
交流220kV | 2011-11-22 | 2012-12-11 | 1.0548 | 10.5 | 120.6 | 703.9 | 2 | 0.4 | 0.3 | 0 | 2.7 | 0 | 0 | 0 | 5.8367
交流220kV | 2005-03-28 | 2006-04-17 | 1.0548 | 9.76 | 145.1 | 249.08 | 2.65 | 1.35 | 0 | 0 | 4 | 0.01 | 0.321 | 51.7 | 1.7166
交流220kV | 2006-03-13 | 2007-04-05 | 1.063 | 6.99 | 144.79 | 90.94 | 1.76 | 2.55 | 0 | 0 | 4.31 | 0.002 | 0.87 | 50.2 | 0.62808
交流220kV | 2011-06-10 | 2012-07-02 | 1.063 | 14.05 | 184.48 | 476.53 | 35.7 | 0.45 | 0.49 | 0 | 36.64 | 0.008 | 0.042 | 62 | 2.5831
交流220kV | 2012-08-06 | 2013-08-30 | 1.0658 | 12.41 | 145.97 | 443.68 | 2.38 | 0.21 | 0.5 | 0 | 3.09 | 0.002 | 0.001 | 56 | 3.0395
交流220kV | 2012-08-06 | 2013-08-30 | 1.0658 | 10.36 | 130.91 | 430.98 | 2.01 | 0.12 | 0.58 | 0 | 2.71 | 0.002 | 0.001 | 57 | 3.2922
交流220kV | 2010-09-17 | 2011-10-12 | 1.0685 | 17 | 206.1 | 1273.2 | 2.9 | 0.3 | 0.4 | 0 | 3.6 | 0.006 | 0.38 | 53 | 6.1776
交流220kV | 2010-09-17 | 2011-10-12 | 1.0685 | 4.2 | 22.3 | 350.6 | 3.8 | 0.5 | 0.5 | 0.4 | 5.2 | 0.003 | 0.23 | 51 | 15.722
交流220kV | 2010-11-20 | 2011-12-16 | 1.0712 | 86.6 | 159 | 1240 | 6.3 | 1.3 | 1.4 | 0 | 9 | 0 | 0 | 0 | 7.7987
交流220kV | 2013-01-17 | 2014-02-12 | 1.0712 | 2.6 | 126.2 | 1449.7 | 3 | 1 | 0.8 | 0 | 4.8 | 0.004 | 0.089 | 60 | 11.4873
交流220kV | 2011-01-20 | 2012-02-15 | 1.0712 | 57.02 | 260.37 | 680.73 | 2.18 | 0.21 | 0.44 | 0 | 2.83 | 0.003 | 0.003 | 52 | 2.6145
交流220kV | 2011-01-20 | 2012-02-15 | 1.0712 | 41.6 | 98.08 | 500.85 | 2.11 | 0.25 | 0.4 | 0 | 2.76 | 0.005 | 0.001 | 52 | 5.1065
交流220kV | 2011-01-22 | 2012-02-18 | 1.074 | 76.65 | 194.31 | 1197.21 | 3.91 | 0.62 | 0.88 | 0 | 5.41 | 0.01 | 0.1 | 65 | 6.1613
交流220kV | 2010-11-14 | 2011-12-13 | 1.0795 | 51.47 | 405.51 | 4125.25 | 10.92 | 1.73 | 3.06 | 0 | 15.71 | 0.002 | 0.03 | 49 | 10.173
交流220kV | 2011-01-07 | 2012-02-06 | 1.0822 | 2.8 | 35.4 | 349.2 | 1.5 | 0.2 | 0.3 | 0 | 2 | 0.004 | 0.136 | 72.3 | 9.8644
交流220kV | 2011-05-15 | 2012-06-13 | 1.0822 | 17.85 | 75.11 | 635.17 | 2.93 | 0.49 | 0.52 | 0 | 3.94 | 0.032 | 0.71 | 45 | 8.4565
交流220kV | 2011-01-10 | 2012-02-10 | 1.0849 | 14.41 | 341.42 | 510.37 | 2.84 | 0 | 0 | 0 | 2.84 | 0 | 0 | 0 | 1.4948
交流220kV | 2010-11-15 | 2011-12-17 | 1.0877 | 13.85 | 186.88 | 742.75 | 1.6 | 0.28 | 0.33 | 0 | 2.21 | 0 | 0 | 0 | 3.9745
交流220kV | 2011-05-31 | 2012-07-03 | 1.0932 | 15.49 | 204.04 | 509.08 | 3.61 | 0.5 | 4.88 | 0 | 8.99 | 0.003 | 0 | 65.8 | 2.495
交流220kV | 2012-03-22 | 2013-04-27 | 1.0986 | 10 | 131 | 211 | 2 | 0 | 0 | 0 | 2 | 0 | 0 | 0 | 1.6107
交流220kV | 2008-12-10 | 2010-01-21 | 1.1151 | 23 | 372 | 856 | 6.4 | 0.7 | 0.8 | 0 | 7.9 | 0.002 | 0.003 | 55 | 2.3011
交流220kV | 2011-01-18 | 2012-02-29 | 1.1151 | 17.72 | 233.03 | 377.99 | 2.01 | 0.22 | 0.19 | 0 | 2.42 | 0.02 | 0.06 | 50 | 1.6221
交流220kV | 2010-12-28 | 2012-02-10 | 1.1205 | 40.6 | 102 | 304 | 1.25 | 0.45 | 0.98 | 0.15 | 2.83 | 0.024 | 0.038 | 56 | 2.9804
交流220kV | 2010-09-26 | 2011-11-09 | 1.1205 | 25 | 154 | 356 | 3.6 | 0.4 | 0.4 | 0 | 4.4 | 0.003 | 0.002 | 50 | 2.3117
交流220kV | 2010-09-26 | 2011-11-09 | 1.1205 | 14 | 158 | 408 | 2.5 | 0.8 | 0.5 | 0 | 3.8 | 0.003 | 0.001 | 73 | 2.5823
交流220kV | 2012-12-30 | 2014-02-13 | 1.1233 | 5.22 | 79.21 | 365.42 | 1.58 | 0.25 | 0.38 | 0 | 2.21 | 0.005 | 0.045 | 58 | 4.6133
交流220kV | 2012-12-30 | 2014-02-13 | 1.1233 | 5.31 | 119.26 | 390.65 | 1.55 | 0.35 | 0.64 | 0 | 2.54 | 0.004 | 0.046 | 54.4 | 3.2756
交流220kV | 2013-01-14 | 2014-02-28 | 1.1233 | 16.33 | 108.66 | 470.31 | 4.69 | 0.6 | 1.02 | 0 | 6.31 | 0.007 | 0.07 | 56 | 4.3283
220 | 2011-02-24 | 2012-04-10 | 1.126 | 3 | 12 | 29 | 0 | 0 | 0 | 0 | 0 | 0.006 | 0.059 | 56 | 2.4167
交流220kV | 2013-01-29 | 2014-03-16 | 1.126 | 9.3 | 49.5 | 846 | 1.8 | 0.2 | 0 | 0 | 2 | 0.006 | 0.001 | 48 | 17.0909
交流220kV | 2011-10-27 | 2012-12-13 | 1.1315 | 21.59 | 214.98 | 608.58 | 2.44 | 0.31 | 0.35 | 0 | 3.1 | 0.003 | 0.025 | 48 | 2.8309
交流220kV | 2011-10-27 | 2012-12-13 | 1.1315 | 15.65 | 154.11 | 496.11 | 2.14 | 0.27 | 0.28 | 0 | 2.69 | 0.003 | 0.025 | 49 | 3.2192
交流220kV | 2010-04-13 | 2011-05-31 | 1.1315 | 23.46 | 224.78 | 843.35 | 12.15 | 0 | 0 | 0 | 12.15 | 0.006 | 0.269 | 49.6 | 3.7519
220 | 2011-01-20 | 2012-03-09 | 1.1342 | 8.19 | 102.43 | 357.81 | 1.32 | 0.19 | 0.32 | 0 | 1.83 | 0.003 | 0.68 | 58 | 3.4932
交流220kV | 2012-10-15 | 2013-12-05 | 1.1397 | 7.8 | 79.8 | 244.1 | 1.7 | 0.5 | 0.3 | 0 | 2.5 | 0 | 0 | 0 | 3.0589
交流220kV | 2012-05-26 | 2013-07-18 | 1.1452 | 16.08 | 88.19 | 315.58 | 2.19 | 0.28 | 0.41 | 0 | 2.88 | 0.003 | 0.025 | 51 | 3.5784
交流220kV | 2012-10-12 | 2013-12-04 | 1.1452 | 21.1 | 68.7 | 336.9 | 2.1 | 0.3 | 0.3 | 0 | 2.7 | 0 | 0 | 0 | 4.9039
交流220kV | 2011-05-19 | 2012-07-12 | 1.1507 | 17.45 | 238.64 | 717.81 | 2.66 | 0.24 | 0.36 | 0 | 3.26 | 0.008 | 0.083 | 71 | 3.0079
220 | 2010-09-16 | 2011-11-15 | 1.1644 | 13.73 | 111.43 | 422.49 | 1.61 | 0.32 | 0 | 0 | 1.93 | 0.004 | 0.028 | 62.8 | 3.7915
交流220kV | 2012-12-15 | 2014-02-14 | 1.1671 | 6.52 | 75.82 | 631.72 | 9.3 | 0.2 | 0.19 | 0 | 9.69 | 0.015 | 0.072 | 67 | 8.3318
交流220kV | 2012-12-15 | 2014-02-14 | 1.1671 | 8.4 | 84.67 | 660.74 | 9.73 | 0.14 | 0.17 | 0 | 10.04 | 0.027 | 0.056 | 79 | 7.8037
交流220kV | 2008-11-21 14:12 | 2010-01-22 | 1.1682 | 2 | 341 | 525 | 8.7 | 11.9 | 1.5 | 0 | 22.1 | 0.001 | 0.003 | 55 | 1.5396
交流220kV | 2012-03-13 | 2013-05-14 | 1.1699 | 11.29 | 62.35 | 159.88 | 0.5 | 0.24 | 0.27 | 0 | 1.01 | 0.07 | 0.001 | 60 | 2.5642
交流220kV | 2012-03-13 | 2013-05-14 | 1.1699 | 15.23 | 40.27 | 108.46 | 1.24 | 0.54 | 0.67 | 0 | 2.45 | 0.01 | 0.006 | 60 | 2.6933
交流220kV | 2012-09-13 | 2013-11-14 | 1.1699 | 9.87 | 210.37 | 645.44 | 2.36 | 0.27 | 0.19 | 0 | 2.82 | 0.01 | 0.01 | 48 | 3.0681
交流220kV | 2012-09-13 | 2013-11-14 | 1.1699 | 9.73 | 227.02 | 596.31 | 2.86 | 0.22 | 0.25 | 0 | 3.33 | 0.02 | 0.01 | 48 | 2.6267
交流220kV | 2012-09-13 | 2013-11-14 | 1.1699 | 10.48 | 233.06 | 737.11 | 2.56 | 0.26 | 0.21 | 0 | 3.03 | 0.02 | 0.01 | 48 | 3.1627
交流220kV | 2012-09-13 | 2013-11-15 | 1.1726 | 8.27 | 205.08 | 676.29 | 2.53 | 0.16 | 0.29 | 0 | 2.98 | 0.02 | 0.02 | 48 | 3.2977
交流220kV | 2012-09-13 | 2013-11-16 | 1.1753 | 8.35 | 206.4 | 771.05 | 2.5 | 0.17 | 0.23 | 0 | 2.9 | 0.01 | 0.03 | 49 | 3.7357
交流220kV | 2012-09-13 | 2013-11-16 | 1.1753 | 11.22 | 222.55 | 691.08 | 2.48 | 0.21 | 0.25 | 0 | 2.94 | 0.02 | 0.02 | 48 | 3.1053
交流220kV | 2010-10-13 | 2011-12-16 | 1.1753 | 21 | 329 | 951 | 2.5 | 0.6 | 0.3 | 0 | 3.4 | 0.003 | 0.003 | 39 | 2.8906
交流220kV | 2010-10-13 | 2011-12-16 | 1.1753 | 23 | 321 | 867 | 2.6 | 0.7 | 0.4 | 0 | 3.7 | 0.003 | 0.002 | 52 | 2.7009
交流220kV | 2012-03-25 | 2013-05-29 | 1.1781 | 12.55 | 178.67 | 505.82 | 1.68 | 0.18 | 0.14 | 0 | 2 | 0.009 | 0.041 | 61.3 | 2.831
交流220kV | 2012-03-25 | 2013-05-29 | 1.1781 | 7.94 | 104.91 | 394.1 | 1.24 | 0.12 | 0.12 | 0 | 1.48 | 0.008 | 0.065 | 55.6 | 3.7566
交流220kV | 2011-05-28 | 2012-08-02 | 1.1836 | 10.12 | 80.36 | 414.66 | 1.45 | 0.33 | 0.34 | 0 | 2.12 | 0.01 | 0.06 | 61 | 5.16
交流220kV | 2013-01-27 | 2014-04-04 | 1.1836 | 21.92 | 313.75 | 848.11 | 3.92 | 0.42 | 0.55 | 0 | 4.89 | 0.052 | 0.062 | 80 | 2.7031
交流220kV | 2011-04-07 | 2012-06-13 | 1.1863 | 13.49 | 279.91 | 1703.51 | 13.78 | 0.33 | 0 | 0 | 14.11 | 0.001 | 0.009 | 57.5 | 6.0859
交流220kV | 2011-09-29 | 2012-12-05 | 1.1863 | 13 | 270 | 551 | 3 | 0 | 0 | 0 | 3 | 0 | 0 | 0 | 2.0407
交流220kV | 2011-09-29 | 2012-12-05 | 1.1863 | 15 | 367 | 641 | 4 | 1 | 0 | 0 | 5 | 0 | 0 | 0 | 1.7466
交流220kV | 2012-01-05 | 2013-03-13 | 1.1863 | 13 | 154.3 | 399.6 | 1.8 | 0.3 | 0.3 | 0 | 2.4 | 0.008 | 0.039 | 47 | 2.5898
220 | 2012-01-13 | 2013-03-22 | 1.189 | 10.96 | 134.29 | 655.15 | 0.36 | 0.5 | 0.4 | 0 | 1.26 | 0.01 | 0.059 | 58 | 4.8786
交流220kV | 2010-12-22 | 2012-03-02 | 1.1945 | 20 | 67.98 | 366.86 | 1.38 | 0.2 | 0.26 | 0 | 1.84 | 0.015 | 0.004 | 58.6 | 5.3966
交流220kV | 2010-12-22 | 2012-03-02 | 1.1945 | 23.15 | 66.75 | 300.2 | 1.36 | 0.16 | 0.54 | 0 | 2.06 | 0.018 | 0.005 | 56.8 | 4.4974
交流220kV | 2011-03-28 | 2012-06-11 | 1.2082 | 12.03 | 21.74 | 449.85 | 12.37 | 1.27 | 0 | 0 | 13.64 | 0 | 0.524 | 55.8 | 20.6923
交流220kV | 2009-12-30 | 2011-03-17 | 1.211 | 16.39 | 110.26 | 1170.2 | 2.26 | 0.42 | 0.5 | 0 | 3.18 | 0.014 | 0.001 | 63 | 10.6131
交流220kV | 2012-07-25 | 2013-10-11 | 1.2137 | 17.59 | 213.98 | 489.26 | 2.65 | 0.19 | 0.35 | 0 | 3.19 | 0.005 | 0.061 | 60.8 | 2.2865
交流220kV | 2012-07-25 | 2013-10-11 | 1.2137 | 15.02 | 200.95 | 408.72 | 2.44 | 0.17 | 0.32 | 0 | 2.93 | 0.006 | 0.062 | 64.1 | 2.0339
交流220kV | 2012-07-05 | 2013-09-25 | 1.2247 | 18 | 312 | 1296 | 3.2 | 0.5 | 0.4 | 0 | 4.1 | 0.009 | 0.1 | 58 | 4.1538
交流220kV | 2010-06-02 | 2011-08-24 | 1.2274 | 8.33 | 44.82 | 138.09 | 1.55 | 0.15 | 0.19 | 0 | 1.89 | 0.004 | 0.001 | 62 | 3.081
交流220kV | 2010-06-02 | 2011-08-24 | 1.2274 | 7.16 | 28.4 | 151.37 | 1.35 | 0.21 | 0.21 | 0 | 1.77 | 0.005 | 0.001 | 62 | 5.3299
交流220kV | 2012-01-21 | 2013-04-17 | 1.2384 | 15.2 | 316.5 | 551.2 | 3 | 0.3 | 0.4 | 0 | 3.7 | 0.003 | 0.03 | 54.3 | 1.7415
交流220kV | 2012-01-21 | 2013-04-17 | 1.2384 | 7.2 | 260.4 | 715 | 3 | 0.4 | 0.5 | 0 | 3.9 | 0.006 | 0.04 | 54.5 | 2.7458
交流220kV | 2012-12-01 | 2014-02-28 | 1.2438 | 9.02 | 86.81 | 477.57 | 2.89 | 0.65 | 0.49 | 0 | 4.03 | 0.006 | 0.08 | 58 | 5.5013
交流220kV | 2010-12-25 | 2012-03-27 | 1.2548 | 32.99 | 275.12 | 910.81 | 3.35 | 0.29 | 1.66 | 0 | 5.3 | 0.007 | 0.025 | 57.7 | 3.3106
交流220kV | 2009-12-21 | 2011-03-25 | 1.2575 | 46.29 | 205.3 | 1061.21 | 3.32 | 0.82 | 0.69 | 0 | 4.83 | 0.001 | 0.28 | 62 | 5.1691
交流220kV | 2011-12-23 | 2013-03-27 | 1.2603 | 24 | 208 | 535 | 5.15 | 0.18 | 0.58 | 0 | 5.91 | 0.004 | 0.087 | 50 | 2.5721
交流220kV | 2012-12-28 | 2014-04-03 | 1.263 | 9.08 | 52.33 | 169.83 | 7.78 | 6.25 | 2.09 | 0 | 16.12 | 0.018 | 0.193 | 64.6 | 3.2454
交流220kV | 2010-06-15 | 2011-09-19 | 1.263 | 8.66 | 97.18 | 319.75 | 2.64 | 1.28 | 0.29 | 0 | 4.21 | 0.005 | 0.001 | 62 | 3.2903
交流220kV | 2010-03-26 | 2011-07-01 | 1.2658 | 34.66 | 188.2 | 431.08 | 2.54 | 0.17 | 0.29 | 0 | 3 | 0 | 0 | 0 | 2.2905
交流220kV | 2011-12-13 | 2013-03-21 | 1.2712 | 8 | 155 | 444 | 1.8 | 0.5 | 0.3 | 0 | 2.6 | 0.009 | 0.1 | 58 | 2.8645
交流220kV | 2011-12-13 | 2013-03-21 | 1.2712 | 10 | 161 | 465 | 1.8 | 0.3 | 0.3 | 0 | 2.4 | 0.009 | 0.1 | 59 | 2.8882
交流220kV | 2012-03-22 | 2013-07-02 | 1.2795 | 16 | 194 | 331 | 3 | 0 | 1 | 0 | 4 | 0.023 | 0.041 | 52 | 1.7062
220 | 2011-12-15 | 2013-03-28 | 1.2849 | 2 | 62 | 210 | 0.4 | 0 | 0 | 0 | 0.4 | 0.007 | 0.001 | 51 | 3.3871
交流220kV | 2010-12-13 | 2012-03-26 | 1.2849 | 23 | 80 | 296 | 1.54 | 0.15 | 0.44 | 0 | 2.13 | 0.001 | 0.001 | 50 | 3.7
220 | 2012-01-08 | 2013-04-23 | 1.2904 | 7.46 | 156.57 | 591.03 | 2.25 | 0.28 | 0.34 | 0 | 2.87 | 0.003 | 0.89 | 51 | 3.7749
交流220kV | 2012-12-10 | 2014-03-27 | 1.2932 | 27.06 | 92.06 | 328.5 | 3.16 | 0.61 | 1.36 | 0 | 5.13 | 0 | 0.001 | 52.6 | 3.5683
交流220kV | 2010-06-04 | 2011-09-19 | 1.2932 | 6.42 | 65.66 | 253.85 | 2.22 | 0.16 | 0.21 | 0 | 2.59 | 0.003 | 0.001 | 62 | 3.8661
交流220kV | 2010-06-29 | 2011-10-14 | 1.2932 | 86 | 219 | 1473 | 4.8 | 0.7 | 0.7 | 0 | 6.2 | 0.013 | 0.003 | 75 | 6.726
交流220kV | 2010-06-29 | 2011-10-14 | 1.2932 | 109 | 271 | 1593 | 4.4 | 0.6 | 0.6 | 0 | 5.6 | 0.015 | 0.034 | 73 | 5.8782
交流220kV | 2010-06-23 | 2011-10-12 | 1.3041 | 35 | 36 | 408 | 3.3 | 0.3 | 0.4 | 0 | 4 | 0.05 | 0.009 | 71 | 11.3333
交流220kV | 2010-06-23 | 2011-10-12 | 1.3041 | 35 | 41 | 269 | 2.8 | 0.5 | 0.3 | 0 | 3.6 | 0.048 | 0.007 | 67 | 6.561
交流220kV | 2010-07-27 | 2011-11-16 | 1.3068 | 8.79 | 54.6 | 160.87 | 0.85 | 0.2 | 0.78 | 0 | 1.83 | 0.009 | 0.146 | 63.6 | 2.9463
交流220kV | 2010-07-27 | 2011-11-16 | 1.3068 | 5.39 | 25.17 | 173.19 | 0.98 | 0.53 | 0.36 | 0.15 | 2.02 | 0.01 | 0.211 | 58.5 | 6.8808
交流220kV | 2010-05-30 | 2011-09-19 | 1.3068 | 5.13 | 68.63 | 399.85 | 2.39 | 0.26 | 0.25 | 0 | 2.9 | 0.004 | 0.001 | 58 | 5.8262
交流220kV | 2009-12-21 | 2011-04-13 | 1.3096 | 54.19 | 106.54 | 679.44 | 4.16 | 1.19 | 0.96 | 0 | 6.31 | 0.001 | 0.19 | 52 | 6.3773
交流220kV | 2011-04-01 | 2012-07-23 | 1.3123 | 23.97 | 183.92 | 534.79 | 1.92 | 0.32 | 0.29 | 0 | 2.53 | 0.027 | 0.001 | 60 | 2.9077
交流220kV | 2010-12-29 | 2012-04-21 | 1.3123 | 22.4 | 291.6 | 1716.7 | 2.5 | 0.5 | 0.4 | 0 | 3.4 | 0.002 | 0.001 | 60.3 | 5.8872
交流220kV | 2011-11-26 | 2013-03-20 | 1.3151 | 89.65 | 35.59 | 596.93 | 20.15 | 1.08 | 1.72 | 0 | 22.95 | 0.01 | 0.13 | 57 | 16.7724
交流220kV | 2010-01-28 | 2011-05-24 | 1.3178 | 8.24 | 69.15 | 426.13 | 1.89 | 0.3 | 0.64 | 0 | 2.83 | 0.01 | 0.001 | 59 | 6.1624
交流220kV | 2010-01-28 | 2011-05-24 | 1.3178 | 33.19 | 51.86 | 263.89 | 1.88 | 0.32 | 0.23 | 0 | 2.43 | 0.01 | 0.001 | 58 | 5.0885
交流220kV | 2010-12-30 | 2012-04-25 | 1.3205 | 14.02 | 96.11 | 400.38 | 1.16 | 0 | 0 | 0 | 1.16 | 0.002 | 0.25 | 46 | 4.1659
交流220kV | 2008-09-23 | 2010-01-19 | 1.3233 | 55 | 472 | 828 | 10.4 | 1.6 | 1.2 | 0 | 13.2 | 0.01 | 0.002 | 53 | 1.7542
交流220kV | 2010-11-28 | 2012-03-28 | 1.3315 | 21.07 | 51.67 | 444.56 | 2.87 | 0.43 | 1.57 | 0 | 4.87 | 0 | 0 | 0 | 8.6038
交流220kV | 2011-11-02 | 2013-03-02 | 1.3315 | 11.84 | 150.32 | 600.19 | 12.37 | 5.23 | 5.09 | 0 | 22.69 | 0.003 | 0.09 | 52 | 3.9927
交流220kV | 2009-11-02 | 2011-03-03 | 1.3315 | 338.21 | 82 | 307 | 19.96 | 0.38 | 2.03 | 0.12 | 22.49 | 0.024 | 0.031 | 51.2 | 3.7439
交流220kV | 2010-11-29 | 2012-04-01 | 1.3397 | 7.36 | 52.57 | 204.88 | 0.96 | 0.26 | 0.43 | 0 | 1.65 | 0.009 | 0.192 | 58 | 3.8973
交流220kV | 2011-09-19 | 2013-01-23 | 1.3479 | 65.47 | 121.61 | 498.79 | 2.86 | 0.22 | 0.92 | 0 | 4 | 0.003 | 0.001 | 52 | 4.1016
交流220kV | 2008-11-09 | 2010-03-18 | 1.3534 | 14 | 241 | 239 | 9.08 | 1.12 | 1.25 | 0 | 11.45 | 0.001 | 0.001 | 57 | 0.9917
交流220kV | 2012-11-17 | 2014-03-27 | 1.3562 | 25.5 | 68 | 513 | 4.13 | 0.28 | 0 | 0 | 4.41 | 0.005 | 0.002 | 50 | 7.5441
交流220kV | 2010-11-11 | 2012-03-21 | 1.3589 | 9.2 | 117.48 | 475.6 | 1.75 | 0.47 | 0.55 | 0 | 2.77 | 0.006 | 0.001 | 60 | 4.0483
交流220kV | 2010-11-30 | 2012-04-12 | 1.3671 | 4.6 | 197.1 | 509.1 | 2.4 | 0.5 | 0.3 | 0.05 | 3.25 | 0.007 | 0.03 | 55.6 | 2.583
交流220kV | 2010-10-27 | 2012-03-09 | 1.3671 | 18.26 | 788.5 | 1328.4 | 4.87 | 0.86 | 1.18 | 0 | 6.91 | 0.021 | 0 | 56.4 | 1.6847
交流220kV | 2011-11-07 | 2013-03-22 | 1.3726 | 10 | 73 | 310 | 4.07 | 0.16 | 0.1 | 0 | 4.33 | 0.001 | 0.6 | 50.5 | 4.2466
交流220kV | 2011-11-07 | 2013-03-22 | 1.3726 | 9 | 148 | 661 | 5.6 | 0.37 | 0.32 | 0 | 6.29 | 0.001 | 0.7 | 49.7 | 4.4662
交流220kV | 2011-11-26 | 2013-04-10 | 1.3726 | 60.65 | 245.59 | 595.93 | 19.15 | 1.17 | 1.17 | 0 | 21.49 | 0.01 | 0.135 | 56.8 | 2.4265
交流220kV | 2011-11-07 | 2013-03-22 | 1.3726 | 12 | 96 | 379 | 5.24 | 0.27 | 0.29 | 0 | 5.8 | 0.001 | 0.47 | 48.6 | 3.9479
交流220kV | 2010-11-26 | 2012-04-16 | 1.389 | 13 | 91 | 324 | 0.2 | 0.25 | 0.84 | 0 | 1.29 | 0.003 | 0.068 | 53 | 3.5604
交流220kV | 2011-06-30 | 2012-11-19 | 1.3918 | 9.25 | 230.58 | 1052.64 | 3.36 | 0.72 | 0.82 | 0 | 4.9 | 0.012 | 0.003 | 60 | 4.5652
交流220kV | 2011-11-17 15:25 | 2013-04-10 | 1.3955 | 80.21 | 525.18 | 625.3 | 20.12 | 2.25 | 3.71 | 0 | 26.08 | 0.01 | 0.109 | 55.6 | 1.1906
交流220kV | 2012-05-26 | 2013-10-18 | 1.3973 | 16.8 | 88 | 316 | 2 | 1 | 1 | 0 | 4 | 0 | 0 | 0 | 3.5909
交流220kV | 2010-10-26 | 2012-03-21 | 1.4027 | 19 | 68 | 312 | 12.86 | 0.24 | 0.3 | 0 | 13.4 | 0.026 | 0.041 | 51.2 | 4.5882
交流220kV | 2010-11-14 | 2012-04-11 | 1.4082 | 8.31 | 251.94 | 621.31 | 3.03 | 0.75 | 0.69 | 0 | 4.47 | 0.002 | 0.2 | 51 | 2.4661
交流220kV | 2011-05-26 | 2012-10-22 | 1.411 | 7.46 | 326.69 | 909.53 | 3.43 | 0.54 | 0.47 | 0 | 4.44 | 0.009 | 0.032 | 54.6 | 2.7841
交流220kV | 2011-05-26 | 2012-10-22 | 1.411 | 1.59 | 6.34 | 502.67 | 0.93 | 0.05 | 0.07 | 0 | 1.05 | 0.009 | 0.046 | 60.3 | 79.2855
交流220kV | 2011-11-11 | 2013-04-10 | 1.4137 | 32 | 45 | 1111 | 1 | 0 | 0 | 0 | 1 | 0.008 | 0.11 | 53 | 24.6889
交流220kV | 2011-10-26 | 2013-03-28 | 1.4219 | 4.86 | 86.03 | 372.78 | 1.26 | 0.24 | 0.23 | 0 | 1.73 | 0.007 | 0.001 | 52 | 4.3331
交流220kV | 2010-12-22 | 2012-05-24 | 1.4219 | 39.03 | 217.03 | 622.96 | 2.08 | 0.36 | 0.34 | 0 | 2.78 | 0.03 | 0.001 | 60 | 2.8704
交流220kV | 2007-10-31 | 2009-04-03 | 1.4247 | 20.74 | 173.38 | 515.07 | 2.02 | 0.33 | 0.25 | 0 | 2.6 | 0.017 | 0.001 | 62.1 | 2.9708
220 | 2011-10-14 | 2013-03-20 | 1.4329 | 7.34 | 62.67 | 471.07 | 2.79 | 0.76 | 1.26 | 0 | 4.81 | 0.009 | 0.11 | 51 | 7.5167
交流220kV | 2011-12-31 | 2013-06-06 | 1.4329 | 16.6 | 113.4 | 323.7 | 1.1 | 0 | 0 | 0 | 1.1 | 0.013 | 0.104 | 0 | 2.8545
交流220kV | 2011-12-30 | 2013-06-06 | 1.4356 | 3.3 | 236.4 | 814.3 | 9.9 | 0 | 0 | 0 | 9.9 | 0.013 | 0.1 | 0 | 3.4446
交流220kV | 2011-12-29 | 2013-06-06 | 1.4384 | 7.5 | 91.2 | 298.2 | 0.9 | 0 | 0 | 0 | 0.9 | 0.012 | 0.094 | 0 | 3.2697
交流220kV | 2011-12-29 | 2013-06-06 | 1.4384 | 10.5 | 198.8 | 490 | 1.4 | 0 | 0 | 0 | 1.4 | 0.013 | 0.143 | 0 | 2.4648
交流220kV | 2012-05-04 | 2013-10-11 | 1.4384 | 10 | 40 | 757 | 1.8 | 0.2 | 0 | 0 | 2 | 0.007 | 0.001 | 50 | 18.925
交流220kV | 2011-07-13 | 2012-12-20 | 1.4411 | 8.01 | 27.22 | 123.38 | 1.27 | 0 | 0 | 0 | 1.27 | 0 | 0 | 0 | 4.5327
交流220kV | 2011-01-22 | 2012-07-04 | 1.4493 | 13.38 | 75.04 | 269.58 | 1.86 | 0.59 | 0 | 0 | 2.45 | 0.007 | 0.001 | 60 | 3.5925
交流220kV | 2011-06-28 | 2012-12-10 | 1.4548 | 50.83 | 91.21 | 449.21 | 1.44 | 0.21 | 0 | 0 | 1.65 | 0 | 0 | 0 | 4.925
交流220kV | 2011-06-28 | 2012-12-10 | 1.4548 | 14.21 | 136.38 | 642.03 | 1.74 | 0 | 0 | 0 | 1.74 | 0 | 0 | 0 | 4.7077
交流220kV | 2011-06-28 | 2012-12-11 | 1.4575 | 41.3 | 131.9 | 478.6 | 2.8 | 0.4 | 0.3 | 0 | 3.5 | 0 | 0 | 0 | 3.6285
交流220kV | 2012-07-04 | 2013-12-18 | 1.4575 | 27 | 112 | 331 | 2 | 0 | 0 | 0 | 2 | 0 | 0 | 0 | 2.9554
交流220kV | 2011-01-10 | 2012-06-25 | 1.4575 | 8.35 | 296.58 | 817.03 | 3.14 | 0 | 0 | 0 | 3.14 | 0 | 0 | 45 | 2.7548
交流220kV | 2012-07-06 | 2013-12-20 | 1.4575 | 4.47 | 37.86 | 111.15 | 1.98 | 0 | 0 | 0 | 1.98 | 0 | 0 | 57.6 | 2.9358
交流220kV | 2011-05-08 | 2012-10-22 | 1.4603 | 0.94 | 6.41 | 499.32 | 0.88 | 0.06 | 0 | 0 | 0.94 | 0.011 | 0.002 | 60 | 77.897
交流220kV | 2011-05-08 | 2012-10-22 | 1.4603 | 3.82 | 219.24 | 1243.68 | 3.91 | 0.26 | 0.82 | 0 | 4.99 | 0.006 | 0.001 | 60 | 5.6727
交流220kV | 2011-06-26 | 2012-12-11 | 1.463 | 19.6 | 80.8 | 689.9 | 3.1 | 0.7 | 0.8 | 0 | 4.6 | 0 | 0 | 0 | 8.5384
交流220kV | 2010-06-30 | 2011-12-17 | 1.4658 | 24.37 | 163.72 | 525.29 | 1.56 | 0.21 | 0.29 | 0 | 2.06 | 0 | 0 | 0 | 3.2085
交流220kV | 2012-06-23 | 2013-12-10 | 1.4658 | 18.3 | 331.7 | 1472.1 | 5.1 | 0.6 | 1.2 | 0 | 6.9 | 0 | 0 | 0 | 4.438
交流220kV | 2012-06-29 | 2013-12-17 | 1.4685 | 32.2 | 36.5 | 294.8 | 2.4 | 0 | 0 | 0 | 2.4 | 0.03 | 0.8 | 45 | 8.0767
交流220kV | 2011-05-05 | 2012-10-22 | 1.4685 | 5.68 | 195.9 | 636.39 | 2.17 | 0.17 | 0.4 | 0 | 2.74 | 0.009 | 0.001 | 60 | 3.2485
交流220kV | 2011-05-05 | 2012-10-22 | 1.4685 | 6.54 | 218.81 | 643.83 | 2.31 | 0.17 | 0.27 | 0 | 2.75 | 0.012 | 0.002 | 62 | 2.9424
交流220kV | 2012-06-20 | 2013-12-10 | 1.474 | 8.6 | 244.8 | 1305.3 | 4.5 | 0.7 | 3.1 | 0 | 8.3 | 0 | 0 | 0 | 5.3321
交流220kV | 2011-11-05 | 2013-04-26 | 1.474 | 9 | 101 | 492 | 1.05 | 0.17 | 1.16 | 0 | 2.38 | 0.004 | 0.065 | 56 | 4.8713
交流220kV | 2010-05-20 | 2011-11-09 | 1.474 | 17.88 | 140 | 573 | 1.6 | 0.13 | 0.25 | 0 | 1.98 | 0.021 | 0.058 | 57.4 | 4.0929
交流220kV | 2009-09-22 | 2011-03-15 | 1.4767 | 7 | 120 | 467 | 1.9 | 0.2 | 0 | 0 | 2.1 | 0.005 | 0 | 52 | 3.8917
交流220kV | 2012-09-27 | 2014-03-21 | 1.4795 | 4.42 | 38.64 | 369.43 | 1.35 | 0.44 | 0 | 0 | 1.79 | 0.006 | 0.125 | 62 | 9.5608
交流220kV | 2010-06-23 | 2011-12-16 | 1.4822 | 4.5 | 76.2 | 300.2 | 2.4 | 0.1 | 0.4 | 0 | 2.9 | 0 | 0 | 0 | 3.9396
交流220kV | 2010-06-22 | 2011-12-16 | 1.4849 | 5.4 | 110.3 | 288.6 | 3.5 | 0.1 | 0.4 | 0 | 4 | 0 | 0 | 0 | 2.6165
交流220kV | 2011-12-30 | 2013-06-24 | 1.4849 | 8.5 | 41.8 | 250.8 | 1.2 | 0.2 | 0.2 | 0 | 1.6 | 0.01 | 0.15 | 55.2 | 6
交流220kV | 2011-12-30 | 2013-06-27 | 1.4932 | 14.5 | 53 | 216.4 | 1.2 | 0.2 | 0.3 | 0 | 1.7 | 0.001 | 0.09 | 45.6 | 4.083
交流220kV | 2011-08-26 | 2013-02-21 | 1.4932 | 58.72 | 111.41 | 441.01 | 2.24 | 0.56 | 0.62 | 0 | 3.42 | 0.021 | 0.01 | 56.4 | 3.9584
交流220kV | 2008-12-13 | 2010-06-12 | 1.4959 | 86.87 | 355.48 | 756.5 | 4.78 | 0.99 | 3.69 | 0 | 9.46 | 0.008 | 0.044 | 62.4 | 2.1281
交流220kV | 2011-08-25 | 2013-02-21 | 1.4959 | 43.62 | 99.32 | 355.74 | 2.38 | 2.06 | 1.61 | 0 | 6.05 | 0.021 | 0.05 | 58 | 3.5818
交流220kV | 2011-11-22 | 2013-05-22 | 1.4986 | 10.5 | 124.4 | 1255.4 | 2.6 | 0.5 | 0.4 | 0 | 3.5 | 0.017 | 0 | 64.8 | 10.0916
交流220kV | 2010-05-11 | 2011-11-10 | 1.5014 | 41 | 340 | 779 | 4.8 | 0.6 | 0.9 | 0 | 6.3 | 0.003 | 0.001 | 74 | 2.2912
交流220kV | 2012-05-26 | 2013-11-26 | 1.5041 | 13.71 | 106.04 | 327.25 | 2.37 | 0.33 | 0.49 | 0 | 3.19 | 0.001 | 0.2 | 41 | 3.0861
交流220kV | 2010-12-23 | 2012-06-24 | 1.5041 | 8.34 | 210 | 665.16 | 11.96 | 9.86 | 2.83 | 0 | 24.65 | 0.025 | 0.253 | 50 | 3.1674
交流220kV | 2010-12-11 16:57 | 2012-06-14 | 1.5077 | 29.1 | 273.7 | 3001 | 9.5 | 9.6 | 3.6 | 0 | 22.7 | 0.009 | 0.06 | 52 | 10.9646
交流220kV | 2010-09-28 | 2012-04-01 | 1.5096 | 3.33 | 27.87 | 84.56 | 0.58 | 0.05 | 0.1 | 0 | 0.73 | 0.007 | 0.048 | 58 | 3.0341
交流220kV | 2010-09-28 | 2012-04-01 | 1.5096 | 4.83 | 37.77 | 62.58 | 0.54 | 0.05 | 0 | 0 | 0.59 | 0.006 | 0.039 | 57 | 1.6569
交流220kV | 2009-12-24 | 2011-06-28 | 1.5096 | 16 | 301.8 | 990.9 | 2.8 | 0.4 | 0.4 | 0 | 3.6 | 0.01 | 0.11 | 61 | 3.2833
交流220kV | 2011-06-10 | 2012-12-12 | 1.5096 | 15.46 | 219.09 | 578.78 | 39.88 | 0.52 | 0.59 | 0 | 40.99 | 0.008 | 0.042 | 62 | 2.6417
交流220kV | 2009-07-03 | 2011-01-06 | 1.5123 | 3.7 | 67.5 | 846.5 | 2 | 0.4 | 0.6 | 0 | 3 | 0.009 | 0.631 | 58.7 | 12.5407
交流220kV | 2011-11-03 | 2013-05-09 | 1.5151 | 42 | 70 | 1039 | 1.3 | 0 | 0 | 0 | 1.3 | 0.003 | 0.011 | 60 | 14.8429
交流220kV | 2011-10-28 | 2013-05-03 | 1.5151 | 2.9 | 47.2 | 127.5 | 0.8 | 0.07 | 0 | 0 | 0.87 | 0.007 | 0.064 | 48.4 | 2.7013
交流220kV | 2011-10-28 | 2013-05-03 | 1.5151 | 1.6 | 59.3 | 279.5 | 1.2 | 0.09 | 0.1 | 0 | 1.39 | 0.004 | 0.074 | 52.6 | 4.7133
交流220kV | 2012-06-10 | 2013-12-17 | 1.5205 | 11.4 | 85.8 | 333.9 | 1.5 | 0 | 0 | 0 | 1.5 | 0.03 | 0.07 | 47 | 3.8916
交流220kV | 2012-06-04 | 2013-12-11 | 1.5205 | 17.9 | 175.8 | 377.5 | 2.7 | 0.8 | 0.4 | 0 | 3.9 | 0 | 0 | 0 | 2.1473
交流220kV | 2012-06-10 | 2013-12-17 | 1.5205 | 3.1 | 71.9 | 444.2 | 1.7 | 0 | 0 | 0 | 1.7 | 0.04 | 0.7 | 48 | 6.178
交流220kV | 2002-09-28 | 2004-04-08 | 1.5288 | 18.3 | 694.6 | 950.2 | 7.1 | 1.4 | 4.2 | 0 | 12.7 | 0.006 | 0.171 | 53.2 | 1.368
交流220kV | 2011-12-30 20:55 | 2013-07-12 | 1.5319 | 11.23 | 132.06 | 512.39 | 2.03 | 0.45 | 0.19 | 0 | 2.67 | 0.006 | 0.021 | 60 | 3.88
交流220kV | 2012-06-20 | 2014-01-07 | 1.5507 | 8 | 31 | 286 | 1.69 | 0.35 | 0.34 | 0 | 2.38 | 0.02 | 0.002 | 71.6 | 9.2258
交流220kV | 2012-09-10 | 2014-03-31 | 1.5534 | 19.7 | 19.2 | 254.9 | 5.2 | 5.2 | 3.7 | 0 | 14.1 | 0.02 | 0.003 | 58 | 13.276
交流220kV | 2011-05-31 | 2012-12-20 | 1.5589 | 7.01 | 60.38 | 171.61 | 2.17 | 0.31 | 0 | 0 | 2.48 | 0 | 0 | 0 | 2.8422
交流220kV | 2011-05-19 09:04 | 2012-12-10 | 1.5633 | 12.6 | 227.8 | 620.5 | 3.9 | 0.5 | 0.6 | 0 | 5 | 0 | 0 | 0 | 2.7239
交流220kV | 2008-06-26 | 2010-01-19 | 1.5671 | 29 | 316 | 266 | 16.4 | 0.5 | 1 | 0 | 17.9 | 0.011 | 0.003 | 52 | 0.84177
交流220kV | 2006-02-21 | 2007-09-16 | 1.5671 | 15.5 | 165.3 | 418.5 | 2.1 | 0 | 0 | 0 | 2.1 | 0.008 | 0.004 | 55 | 2.5318
交流220kV | 2010-04-06 | 2011-11-02 | 1.5753 | 14 | 140 | 1058 | 1.9 | 0.5 | 0.4 | 0 | 2.8 | 0.058 | 0.004 | 55 | 7.5571
交流220kV | 2010-09-19 | 2012-04-17 | 1.5781 | 3 | 56 | 287 | 0.6 | 0 | 0.17 | 0 | 0.77 | 0.004 | 0.09 | 60 | 5.125
交流220kV | 2011-07-10 | 2013-02-05 | 1.5781 | 4.6 | 126.2 | 619.8 | 1.7 | 0.3 | 0.4 | 0 | 2.4 | 0.003 | 0.243 | 63.2 | 4.9113
交流220kV | 2010-10-26 | 2012-05-24 | 1.5781 | 10 | 104 | 413 | 1.83 | 0.6 | 0.43 | 0.21 | 3.07 | 0.024 | 0.089 | 46.7 | 3.9712
交流220kV | 2011-07-10 | 2013-02-05 | 1.5781 | 4.5 | 98 | 602.3 | 1.5 | 0.2 | 0.4 | 0 | 2.1 | 0.004 | 0.152 | 62.6 | 6.1459
交流220kV | 2009-12-05 | 2011-07-05 | 1.5808 | 16.26 | 60.95 | 159.93 | 2.48 | 0.37 | 0.39 | 0 | 3.24 | 0.004 | 0.001 | 63 | 2.624
交流220kV | 2009-12-05 | 2011-07-05 | 1.5808 | 21.13 | 45.45 | 134.62 | 2.28 | 0.25 | 0.32 | 0 | 2.85 | 0.005 | 0.001 | 50 | 2.9619
交流220kV | 2011-07-29 | 2013-02-26 | 1.5836 | 43.9 | 337.23 | 479.46 | 4.23 | 0.67 | 1.02 | 0 | 5.92 | 0.021 | 0.05 | 63 | 1.4218
交流220kV | 2011-07-28 | 2013-02-26 | 1.5863 | 32.28 | 263.23 | 458.07 | 3.38 | 0.67 | 0.92 | 0 | 4.97 | 0.021 | 0.05 | 60 | 1.7402
交流220kV | 2011-07-07 | 2013-02-06 | 1.589 | 9.6 | 106.8 | 640.8 | 2.2 | 0.6 | 0.4 | 0 | 3.2 | 0.006 | 0.051 | 60.6 | 6
交流220kV | 2008-11-08 | 2010-06-12 | 1.5918 | 68.95 | 290.97 | 844.39 | 5.03 | 0.66 | 3.13 | 0 | 8.82 | 0.009 | 0.044 | 60.6 | 2.902
交流220kV | 2010-11-28 | 2012-07-02 | 1.5945 | 20.76 | 51.35 | 627.13 | 2.47 | 0.72 | 2.18 | 0 | 5.37 | 0 | 0.018 | 41.9 | 12.2129
交流220kV | 2011-08-08 | 2013-03-12 | 1.5945 | 12.81 | 70.18 | 353.57 | 2.32 | 0.22 | 0.67 | 0 | 3.21 | 0.012 | 0.001 | 82 | 5.038
交流220kV | 2009-09-01 | 2011-04-08 | 1.6 | 8 | 210 | 680 | 10 | 0.5 | 0.5 | 0 | 11 | 0.006 | 0.06 | 50 | 3.2381
交流220kV | 2009-09-01 | 2011-04-08 | 1.6 | 10 | 230 | 508 | 10 | 0.3 | 0.5 | 0 | 10.8 | 0.006 | 0.06 | 52 | 2.2087
交流220kV | 2011-09-14 | 2013-04-20 | 1.6 | 17.8 | 107.49 | 356.88 | 1.67 | 0.17 | 1.76 | 0 | 3.6 | 0.016 | 0.008 | 51 | 3.3201
交流220kV | 2010-10-15 | 2012-05-22 | 1.6027 | 3 | 35 | 409 | 2.74 | 0.24 | 0.15 | 0.55 | 3.68 | 0.01 | 0.002 | 50 | 11.6857
交流220kV | 2010-07-23 | 2012-02-28 | 1.6027 | 145 | 40 | 220 | 7.29 | 0.8 | 1.35 | 0 | 9.44 | 0.004 | 0.001 | 65.8 | 5.5
交流220kV | 2011-10-27 | 2013-06-05 | 1.6082 | 12 | 166 | 658 | 4 | 1 | 4 | 0 | 9 | 0.001 | 0.1 | 45 | 3.9639
交流220kV | 2011-10-27 | 2013-06-05 | 1.6082 | 18 | 239 | 861 | 5 | 1 | 6 | 0 | 12 | 0.001 | 0.1 | 45 | 3.6025
交流220kV | 2010-04-01 | 2011-11-10 | 1.611 | 26 | 253 | 636 | 3.8 | 0.4 | 0.4 | 0 | 4.6 | 0.003 | 0.009 | 75 | 2.5138
交流220kV | 2010-11-15 | 2012-06-27 | 1.6164 | 6.2 | 72.31 | 381.61 | 1.38 | 0.39 | 0.75 | 0 | 2.52 | 0 | 0 | 57.1 | 5.2774
交流220kV | 2012-04-09 | 2013-11-21 | 1.6192 | 4.55 | 245.25 | 1223.3 | 3.23 | 0.72 | 1.66 | 0 | 5.61 | 0.018 | 0.37 | 62 | 4.988
交流220kV | 2010-05-28 | 2012-01-09 | 1.6192 | 21 | 452 | 1145 | 1.2 | 0.6 | 0.3 | 0 | 2.1 | 0.048 | 0.032 | 70 | 2.5332
交流220kV | 2011-01-20 | 2012-09-03 | 1.6219 | 25.05 | 199 | 582 | 2.83 | 0.32 | 2.87 | 0 | 6.02 | 0.028 | 0.313 | 52.2 | 2.9246
交流220kV | 2011-04-25 08:44 | 2012-12-10 | 1.6291 | 10.4 | 163.6 | 429.6 | 3.2 | 0.3 | 1.4 | 0 | 4.9 | 0 | 0 | 0 | 2.6259
交流220kV | 2010-11-29 | 2012-07-19 | 1.6384 | 33.65 | 363.93 | 1163.28 | 3.29 | 0.6 | 0.64 | 0 | 4.53 | 0.008 | 0.001 | 60 | 3.1964
交流220kV | 2011-08-21 12:43 | 2013-04-15 | 1.6506 | 16.86 | 15.42 | 290.24 | 1.77 | 0.17 | 0.22 | 0 | 2.16 | 0.021 | 0.05 | 65.6 | 18.8223
交流220kV | 2011-04-19 | 2012-12-12 | 1.6521 | 12.69 | 204.16 | 890.69 | 3.22 | 0.47 | 0.3 | 0.06 | 4.05 | 0.012 | 0.005 | 58 | 4.3627
交流220kV | 2011-04-19 | 2012-12-12 | 1.6521 | 7.56 | 140.55 | 627.95 | 2.62 | 0.66 | 0.44 | 0 | 3.72 | 0.009 | 0.002 | 60 | 4.4678
交流220kV | 2009-05-19 | 2011-01-17 | 1.6658 | 21.15 | 710.42 | 1519.62 | 15.67 | 0.71 | 1.29 | 0 | 17.67 | 0.011 | 0.004 | 53.5 | 2.139
交流220kV | 2011-04-07 | 2012-12-10 | 1.6795 | 19.48 | 479.6 | 2111.38 | 20.44 | 0.39 | 0.07 | 0 | 20.9 | 0 | 0 | 0 | 4.4024
交流220kV | 2010-03-26 | 2011-11-30 | 1.6822 | 34.72 | 221.27 | 545.77 | 2.16 | 0.28 | 0.5 | 0 | 2.94 | 0.008 | 0.01 | 50.5 | 2.4665
交流220kV | 2006-03-15 | 2007-11-20 | 1.6849 | 12 | 376.2 | 937 | 4.9 | 1.3 | 1.2 | 0 | 7.4 | 0.008 | 0.002 | 55.3 | 2.4907
交流220kV | 2010-06-29 | 2012-03-06 | 1.6877 | 15 | 52 | 339 | 1.1 | 0.2 | 0.3 | 0 | 1.6 | 0.014 | 0.102 | 45 | 6.5192
交流220kV | 2010-02-09 | 2011-10-20 | 1.6932 | 23 | 514 | 1280 | 6.1 | 0.7 | 0.8 | 0 | 7.6 | 0.048 | 0.01 | 59.8 | 2.4903
交流220kV | 2010-02-09 | 2011-10-20 | 1.6932 | 31 | 750 | 1839 | 8.2 | 0.9 | 1 | 0 | 10.1 | 0.051 | 0.011 | 45.4 | 2.452
交流220kV | 2010-09-16 | 2012-06-02 | 1.7123 | 16.8 | 308.4 | 1649.6 | 16.7 | 0.6 | 1.3 | 0 | 18.6 | 0.007 | 0.121 | 59 | 5.3489
交流220kV | 2010-09-16 | 2012-06-02 | 1.7123 | 27.2 | 273.1 | 1668.6 | 14.4 | 1.9 | 1.6 | 0 | 17.9 | 0.01 | 0.113 | 53 | 6.1098
交流220kV | 2011-06-25 15:41 | 2013-03-15 | 1.7215 | 17.3 | 123.94 | 197.36 | 2.27 | 0.37 | 0.29 | 0.32 | 3.25 | 0.058 | 0.067 | 66.1 | 1.5924
交流220kV | 2011-06-25 15:32 | 2013-03-15 | 1.7215 | 11.05 | 160.65 | 374.43 | 2.46 | 0.22 | 0.3 | 0 | 2.98 | 0.01 | 0.098 | 65.3 | 2.3307
220 | 2011-06-16 | 2013-03-06 | 1.7233 | 86.34 | 214.45 | 592.55 | 3.35 | 0.27 | 1.06 | 0 | 4.68 | 0.006 | 0.071 | 60 | 2.7631
220 | 2011-06-16 | 2013-03-06 | 1.7233 | 85.77 | 171.26 | 935.77 | 3.6 | 0.35 | 0.47 | 0 | 4.42 | 0.006 | 0.072 | 52 | 5.464
交流220kV | 2010-05-21 | 2012-02-09 | 1.7233 | 26.99 | 424.47 | 1519.21 | 48 | 0.29 | 3.79 | 0 | 52.08 | 0.008 | 0.144 | 60 | 3.5791
交流220kV | 2010-03-31 | 2011-12-20 | 1.7233 | 22 | 218 | 603 | 5.6 | 0.8 | 0 | 0 | 6.4 | 0.005 | 0.004 | 60 | 2.7661
交流220kV | 2010-03-16 | 2011-12-08 | 1.7315 | 17 | 148 | 410 | 1.8 | 0.2 | 0.4 | 0 | 2.4 | 0.003 | 0.001 | 63 | 2.7703
交流220kV | 2010-03-16 | 2011-12-08 | 1.7315 | 15 | 110 | 245 | 1.6 | 0.7 | 1.4 | 0 | 3.7 | 0.003 | 0.001 | 75 | 2.2273
交流220kV | 2011-09-13 | 2013-06-07 | 1.7342 | 11.44 | 98.16 | 226 | 2.15 | 0.4 | 0.54 | 0 | 3.09 | 0.02 | 0.048 | 51.7 | 2.3024
交流220kV | 2012-06-25 | 2014-03-21 | 1.737 | 7.47 | 182.29 | 572.93 | 2.31 | 1.07 | 0.39 | 0 | 3.77 | 0.026 | 0.208 | 65 | 3.143
交流220kV | 2012-03-22 | 2013-12-17 | 1.7397 | 13 | 147 | 338 | 2 | 0 | 0 | 0 | 2 | 0 | 0 | 0 | 2.2993
交流220kV | 2011-03-17 | 2012-12-13 | 1.7452 | 21 | 140.7 | 448.9 | 3.3 | 0.6 | 0.4 | 0 | 4.3 | 0 | 0 | 0 | 3.1905
交流220kV | 2011-03-17 | 2012-12-13 | 1.7452 | 10.9 | 153.1 | 672.3 | 3 | 1.6 | 0.7 | 0 | 5.3 | 0 | 0 | 0 | 4.3912
交流220kV | 2011-09-29 | 2013-07-02 | 1.7589 | 16 | 521 | 985 | 5 | 1 | 5 | 0 | 11 | 0.062 | 0.043 | 52 | 1.8906
交流220kV | 2011-09-29 | 2013-07-02 | 1.7589 | 14 | 354 | 729 | 4 | 1 | 3 | 0 | 8 | 0.076 | 0.09 | 53 | 2.0593
交流220kV | 2011-07-07 | 2013-04-10 | 1.7616 | 9.39 | 275.14 | 1068.6 | 3.7 | 0.32 | 0.56 | 0 | 4.58 | 0.014 | 0.13 | 61 | 3.8838
交流220kV | 2011-07-05 | 2013-04-10 | 1.7671 | 7.8 | 246.27 | 1300.06 | 3.26 | 0.68 | 0.75 | 0 | 4.69 | 0.016 | 0.17 | 51 | 5.279
交流220kV | 2011-12-07 | 2013-09-12 | 1.7671 | 15.28 | 88.19 | 829.27 | 14.3 | 0.42 | 0.46 | 0 | 15.18 | 0.002 | 0.001 | 56 | 9.4032
交流220kV | 2011-12-07 | 2013-09-12 | 1.7671 | 18.69 | 339.06 | 1286.55 | 16.92 | 0.43 | 0.44 | 0 | 17.79 | 0.003 | 0.001 | 58 | 3.7945
交流220kV | 2009-04-02 | 2011-01-09 | 1.7726 | 34.6 | 194.6 | 767.2 | 2.4 | 0.6 | 0.5 | 0 | 3.5 | 0.008 | 0.06 | 60 | 3.9424
交流220kV | 2009-04-02 | 2011-01-09 | 1.7726 | 28.9 | 249.7 | 653.3 | 2.8 | 0.8 | 0.6 | 0 | 4.2 | 0.007 | 0.12 | 60 | 2.6163
交流220kV | 2011-05-30 | 2013-03-09 | 1.7781 | 9.95 | 180.93 | 369.08 | 9.34 | 6.08 | 6.27 | 0 | 21.69 | 0.005 | 0.25 | 44.6 | 2.0399
交流220kV | 2009-09-05 | 2011-06-20 | 1.789 | 16 | 232 | 656 | 2.8 | 0 | 0 | 0 | 2.8 | 0.02 | 0 | 0 | 2.8276
交流220kV | 2009-09-20 | 2011-07-07 | 1.7945 | 19.1 | 328.5 | 1094.1 | 3.7 | 0.6 | 0.8 | 0 | 5.1 | 0 | 0 | 0 | 3.3306
交流220kV | 2011-05-31 | 2013-03-18 | 1.8 | 9 | 144 | 300 | 13.98 | 0.37 | 0.42 | 0 | 14.77 | 0.004 | 0.13 | 64.5 | 2.0833
交流220kV | 2008-05-30 | 2010-03-18 | 1.8 | 36 | 199 | 179 | 23.84 | 0.76 | 1.54 | 0.04 | 26.18 | 0.001 | 0.07 | 50 | 0.8995
交流220kV | 2011-05-31 | 2013-03-20 | 1.8055 | 13 | 147 | 299 | 11.98 | 0.26 | 0.73 | 0 | 12.97 | 0.001 | 0.22 | 60 | 2.034
交流220kV | 2011-05-23 | 2013-03-12 | 1.8055 | 31 | 477 | 803 | 9.95 | 0.73 | 1.52 | 0 | 12.2 | 0.015 | 0.047 | 51.2 | 1.6834
交流220kV | 2012-03-28 | 2014-01-16 | 1.8055 | 6 | 9 | 301 | 1.55 | 0.17 | 0.21 | 0 | 1.93 | 0.1 | 0.01 | 70 | 33.4444
交流220kV | 2010-04-20 | 2012-02-09 | 1.8082 | 37.79 | 688.31 | 1967.17 | 19.66 | 0.49 | 2.12 | 0 | 22.27 | 0.02 | 0.056 | 56.8 | 2.858
交流220kV | 2010-04-19 | 2012-02-10 | 1.8137 | 6.65 | 90.52 | 299.74 | 3.83 | 0 | 0 | 0 | 3.83 | 0 | 0 | 0 | 3.3113
交流220kV | 2010-07-23 | 2012-05-15 | 1.8137 | 34.32 | 293.46 | 1004.95 | 2.85 | 0.36 | 0.47 | 0 | 3.68 | 0.04 | 0.001 | 60 | 3.4245
交流220kV | 2011-07-16 | 2013-05-09 | 1.8164 | 9.96 | 243.57 | 562.66 | 2.32 | 0.33 | 0.24 | 0 | 2.89 | 0.03 | 0.33 | 66 | 2.3101
交流220kV | 2011-12-19 | 2013-10-14 | 1.8219 | 6 | 16.5 | 453 | 1.5 | 0 | 0.4 | 0 | 1.9 | 0.007 | 0.001 | 50 | 27.4545
交流220kV | 2011-07-14 | 2013-05-09 | 1.8219 | 7.99 | 223.07 | 318.74 | 3.02 | 1.32 | 0.57 | 0 | 4.91 | 0.014 | 0.17 | 56 | 1.4289
交流220kV | 2010-04-15 | 2012-02-10 | 1.8247 | 8.98 | 159.9 | 332.03 | 3.11 | 0.25 | 0.84 | 0 | 4.2 | 0.03 | 0 | 50 | 2.0765
交流220kV | 2012-05-23 | 2014-03-21 | 1.8274 | 19 | 55 | 166 | 1.78 | 0.29 | 0.21 | 0 | 2.28 | 0.02 | 0.388 | 57 | 3.0182
交流220kV | 2012-05-23 | 2014-03-21 | 1.8274 | 25 | 60 | 252 | 1.18 | 0.26 | 0.17 | 0 | 1.61 | 0.018 | 0.403 | 56 | 4.2
交流220kV | 2009-12-28 | 2011-10-26 | 1.8274 | 26 | 203 | 769 | 4.3 | 1.3 | 0.8 | 0 | 6.4 | 0.05 | 0.023 | 69 | 3.7882
交流220kV | 2009-12-28 | 2011-10-26 | 1.8274 | 19 | 138 | 783 | 3.1 | 0.9 | 0.5 | 0 | 4.5 | 0.048 | 0.032 | 75 | 5.6739
220 | 2011-12-11 | 2013-10-11 | 1.8356 | 21.37 | 169.44 | 629.9 | 4.78 | 0.28 | 0.32 | 0 | 5.38 | 0.071 | 0.051 | 68 | 3.7175
220 | 2010-08-19 | 2012-06-19 | 1.8356 | 26.19 | 374.82 | 622.38 | 3.83 | 0.2 | 0.52 | 0 | 4.55 | 0.007 | 0.089 | 54 | 1.6605
交流220kV | 2009-11-02 | 2011-09-03 | 1.8356 | 316.29 | 91 | 632 | 23.94 | 0.48 | 3.86 | 0.1 | 28.38 | 0.021 | 0.036 | 50.4 | 6.9451
交流220kV | 2007-06-20 | 2009-04-24 | 1.8466 | 39.85 | 610.29 | 1357.14 | 7.21 | 1.16 | 0.72 | 0 | 9.09 | 0.013 | 0.07 | 49 | 2.2238
交流220kV | 2011-05-28 | 2013-04-09 | 1.8685 | 20.09 | 107.97 | 455.23 | 1.51 | 0.31 | 0.35 | 0 | 2.17 | 0.008 | 0.08 | 66 | 4.2163
交流220kV | 2009-09-19 | 2011-08-05 | 1.8767 | 7.71 | 59.54 | 344.27 | 2.54 | 0.39 | 0.2 | 0 | 3.13 | 0.003 | 0.001 | 58 | 5.7822
交流220kV | 2010-04-29 | 2012-03-14 | 1.8767 | 26.6 | 224.73 | 420.36 | 3.3 | 0.38 | 0.75 | 0.11 | 4.54 | 0.004 | 0.003 | 52 | 1.8705
交流220kV | 2011-06-30 | 2013-05-17 | 1.8822 | 24.02 | 47.85 | 368.54 | 5.55 | 0.43 | 5.48 | 0 | 11.46 | 0 | 0.001 | 55.6 | 7.702
交流220kV | 2008-04-30 | 2010-03-18 | 1.8822 | 37 | 348 | 239 | 29.94 | 0.91 | 2.14 | 0 | 32.99 | 0.001 | 0.002 | 50 | 0.68678
交流220kV | 2009-08-27 | 2011-07-15 | 1.8822 | 31.1 | 226.5 | 1099 | 3.6 | 0.6 | 0.6 | 0 | 4.8 | 0.008 | 0.12 | 61 | 4.8521
交流220kV | 2011-12-14 | 2013-11-01 | 1.8849 | 20 | 16 | 35 | 0.92 | 0.62 | 0.62 | 0 | 2.16 | 0.03 | 0.293 | 74.5 | 2.1875
交流220kV | 2011-04-04 | 2013-02-23 | 1.8932 | 5.31 | 440.56 | 1923.42 | 5.31 | 5.78 | 1.79 | 0 | 12.88 | 0.036 | 0.26 | 55 | 4.3659
交流220kV | 2012-03-30 | 2014-02-20 | 1.8959 | 8 | 105 | 305 | 3 | 0.1 | 0.2 | 0 | 3.3 | 0.1 | 0.013 | 67 | 2.9048
交流220kV | 2011-12-14 | 2013-11-05 | 1.8959 | 28 | 130 | 387 | 2.98 | 0.42 | 0.29 | 0.06 | 3.75 | 0.03 | 0.236 | 68.3 | 2.9769
交流220kV | 2011-07-13 | 2013-06-06 | 1.9014 | 49.03 | 61.77 | 246.83 | 1.79 | 0.51 | 0.21 | 0 | 2.51 | 0 | 0 | 0 | 3.996
交流220kV | 2009-09-09 | 2011-08-05 | 1.9041 | 11.19 | 43.08 | 239.39 | 2.02 | 0.31 | 0.14 | 0 | 2.47 | 0.004 | 0.001 | 60 | 5.5569
交流220kV | 2009-09-09 | 2011-08-05 | 1.9041 | 12.67 | 48.45 | 333.35 | 2.14 | 0.3 | 0.17 | 0 | 2.61 | 0.002 | 0.001 | 60 | 6.8803
交流220kV | 2011-06-28 | 2013-05-24 | 1.9068 | 47.6 | 129 | 476.7 | 3.2 | 0.3 | 0.9 | 0 | 4.4 | 0.007 | 0.08 | 52.1 | 3.6953
交流220kV | 2011-04-01 | 2013-03-06 | 1.9315 | 18 | 173 | 908 | 4.09 | 2.06 | 0.77 | 1.3 | 8.22 | 0.014 | 0.036 | 53.6 | 5.2486
交流220kV | 2010-12-20 13:08 | 2012-11-25 | 1.9327 | 20.9 | 686.8 | 2121.6 | 4.4 | 0.7 | 0.8 | 0 | 5.9 | 0.009 | 0.001 | 63.2 | 3.0891
交流220kV | 2010-04-26 | 2012-04-01 | 1.9342 | 5.73 | 53.36 | 152.71 | 0.86 | 0.07 | 0.11 | 0 | 1.04 | 0.007 | 0.088 | 59 | 2.8619
交流220kV | 2010-04-26 | 2012-04-01 | 1.9342 | 4.41 | 12.73 | 108.64 | 0.79 | 0.09 | 0 | 0 | 0.88 | 0.008 | 0.076 | 59 | 8.5342
交流220kV | 2011-07-13 | 2013-06-21 | 1.9425 | 6 | 169 | 531 | 3.5 | 0.36 | 0.46 | 0 | 4.32 | 0.025 | 0.712 | 68 | 3.142
交流220kV | 2011-06-26 | 2013-06-05 | 1.9452 | 21.6 | 79.4 | 1142.4 | 3.7 | 0.4 | 0.6 | 0 | 4.7 | 0.034 | 0 | 56.1 | 14.3879
交流220kV | 2011-12-31 | 2013-12-11 | 1.9479 | 32 | 179.6 | 430.6 | 2.3 | 0 | 0 | 0 | 2.3 | 0 | 0 | 0 | 2.3976
交流220kV | 2011-12-30 | 2013-12-11 | 1.9507 | 35.5 | 150.7 | 469.8 | 2.2 | 0 | 0 | 0 | 2.2 | 0 | 0 | 0 | 3.1175
交流220kV | 2011-01-07 | 2012-12-20 | 1.9534 | 19.52 | 73.43 | 542.51 | 2.04 | 0.22 | 0.35 | 0 | 2.61 | 0 | 0.01 | 49 | 7.3881
交流220kV | 2011-12-29 | 2013-12-11 | 1.9534 | 7.47 | 214.74 | 477.45 | 2.04 | 0 | 0 | 0 | 2.04 | 0 | 0 | 0 | 2.2234
交流220kV | 2011-12-29 | 2013-12-11 | 1.9534 | 11.56 | 189.09 | 394.4 | 1.84 | 0 | 0 | 0 | 1.84 | 0 | 0 | 0 | 2.0858
交流220kV | 2011-06-21 | 2013-06-03 | 1.9534 | 16.91 | 729.5 | 3689.8 | 29.72 | 46.2 | 8.57 | 1.02 | 85.51 | 0.008 | 0.097 | 59 | 5.058
交流220kV | 2011-07-13 | 2013-06-27 | 1.9589 | 16 | 275 | 596 | 4.88 | 0.44 | 0.44 | 0 | 5.76 | 0.023 | 1.91 | 64 | 2.1673
交流220kV | 2011-06-28 | 2013-06-14 | 1.9644 | 3.04 | 193.65 | 782 | 1.67 | 0.06 | 0 | 0 | 1.73 | 0.001 | 0.068 | 61.5 | 4.0382
交流220kV | 2010-04-19 | 2012-04-06 | 1.9671 | 13.6 | 57.8 | 233.7 | 1.5 | 0.3 | 0.4 | 0 | 2.2 | 0.01 | 0.14 | 60 | 4.0433
交流220kV | 2011-10-27 | 2013-10-15 | 1.9699 | 17.55 | 143.61 | 364.53 | 3.04 | 0.2 | 0.27 | 0 | 3.51 | 0.005 | 0.037 | 68 | 2.5383
交流220kV | 2011-10-27 | 2013-10-15 | 1.9699 | 13.7 | 125.77 | 306.46 | 3.2 | 0.12 | 0.27 | 0 | 3.59 | 0.006 | 0.061 | 58 | 2.4367
交流220kV | 2009-12-30 | 2011-12-20 | 1.9726 | 26 | 105 | 645 | 3.6 | 0 | 0 | 0 | 3.6 | 0.003 | 0.005 | 70 | 6.1429
交流220kV | 2011-12-29 | 2013-12-20 | 1.9781 | 21.66 | 227.2 | 485.55 | 3.44 | 0.86 | 0.7 | 0 | 5 | 0.008 | 0.003 | 58 | 2.1371
交流220kV | 2009-07-17 | 2011-07-11 | 1.9836 | 16.4 | 399.7 | 1187 | 4.1 | 0.5 | 0.7 | 0 | 5.3 | 0.01 | 0.15 | 55 | 2.9697
交流220kV | 2010-12-23 | 2012-12-18 | 1.989 | 1.94 | 205.68 | 845.07 | 9.25 | 9.05 | 0 | 0 | 18.3 | 0.007 | 0.28 | 59 | 4.1087
交流220kV | 2010-04-28 | 2012-04-23 | 1.989 | 9.5 | 394.2 | 1521.4 | 2.3 | 0.6 | 0.4 | 0 | 3.3 | 0.006 | 0.001 | 60.1 | 3.8595
交流220kV | 2012-03-28 | 2014-03-25 | 1.9918 | 13.7 | 136 | 390 | 1.4 | 0.2 | 0.2 | 0 | 1.8 | 0.002 | 0.07 | 58.3 | 2.8676
交流220kV | 2012-03-28 | 2014-03-25 | 1.9918 | 13.1 | 140.4 | 359.4 | 1.4 | 0.2 | 0.2 | 0 | 1.8 | 0.002 | 0.12 | 60.8 | 2.5598
交流220kV | 2011-01-22 | 2013-01-18 | 1.9918 | 79.32 | 87.6 | 876.43 | 4.37 | 0.54 | 1.5 | 0 | 6.41 | 0.01 | 0.1 | 65 | 10.0049
交流220kV | 2010-01-13 | 2012-01-11 | 1.9945 | 34.2 | 237.92 | 654.78 | 4.17 | 0.37 | 0.63 | 0 | 5.17 | 0.004 | 0.008 | 52 | 2.7521
220 | 2010-06-19 | 2012-06-19 | 2.0027 | 17.18 | 374.33 | 831.88 | 4.54 | 0.57 | 0.65 | 0 | 5.76 | 0.007 | 0.097 | 56 | 2.2223
交流220kV | 2011-01-10 | 2013-01-10 | 2.0027 | 14.38 | 168.52 | 657.35 | 1.54 | 0.28 | 0.41 | 0 | 2.23 | 0.008 | 0.063 | 55 | 3.9007
交流220kV | 2011-01-10 | 2013-01-10 | 2.0027 | 11.52 | 167.37 | 308.63 | 1.38 | 0.27 | 0.25 | 0 | 1.9 | 0.009 | 0.05 | 57 | 1.844
交流220kV | 2008-06-20 | 2010-06-22 | 2.0055 | 41 | 1042 | 2324 | 11.4 | 1 | 3.9 | 0 | 16.3 | 0.006 | 0.001 | 52 | 2.2303
交流220kV | 2009-01-19 | 2011-01-21 | 2.0055 | 20.46 | 645.8 | 1008.52 | 8.94 | 0.98 | 1.6 | 0 | 11.52 | 0.011 | 0.006 | 53.5 | 1.5617
交流220kV | 2010-12-11 16:57 | 2012-12-13 | 2.0063 | 10.2 | 326.9 | 2801.5 | 11.8 | 10 | 3.9 | 0 | 25.7 | 0 | 0 | 0 | 8.5699
交流220kV | 2009-12-18 | 2011-12-22 | 2.011 | 59.05 | 105.08 | 747.86 | 3.82 | 0.59 | 0.63 | 0 | 5.04 | 0 | 0 | 0 | 7.1171
交流220kV | 2011-05-31 | 2013-06-06 | 2.0192 | 16.52 | 188.42 | 423.77 | 2.58 | 0 | 0 | 0 | 2.58 | 0 | 0 | 0 | 2.2491
交流220kV | 2010-06-30 | 2012-07-06 | 2.0192 | 14.6 | 139.87 | 617.49 | 1.98 | 0.43 | 0.32 | 0 | 2.73 | 0.017 | 0.071 | 53 | 4.4147
交流220kV | 2011-07-27 | 2013-08-05 | 2.0274 | 33 | 31 | 489 | 1.66 | 0.6 | 0.29 | 0 | 2.55 | 0.022 | 0.215 | 56 | 15.7742
交流220kV | 2011-10-12 | 2013-10-23 | 2.0329 | 18.18 | 94.33 | 328.26 | 2.02 | 0.16 | 0.22 | 0 | 2.4 | 0.01 | 0.025 | 64.9 | 3.4799
交流220kV | 2011-10-12 | 2013-10-23 | 2.0329 | 15.42 | 122.29 | 331.52 | 2.13 | 0.41 | 0.22 | 0 | 2.76 | 0.009 | 0.043 | 67.3 | 2.7109
交流220kV | 2011-11-22 | 2013-12-10 | 2.0521 | 7.3 | 505.4 | 3512.5 | 11.7 | 0.8 | 2.9 | 0 | 15.4 | 0 | 0 | 0 | 6.9499
交流220kV | 2009-09-22 | 2011-10-12 | 2.0548 | 8 | 104 | 790 | 0 | 2.8 | 0.4 | 0 | 3.2 | 0.005 | 0 | 52 | 7.5962
交流220kV | 2011-12-04 | 2013-12-23 | 2.0548 | 9.04 | 143.54 | 518.46 | 2.32 | 0.31 | 0.23 | 0 | 2.86 | 0.011 | 0.034 | 48.1 | 3.612
交流220kV | 2011-12-04 | 2013-12-23 | 2.0548 | 12.14 | 116.82 | 396.04 | 1.98 | 0.29 | 0.17 | 0 | 2.44 | 0.009 | 0.058 | 65.6 | 3.3902
交流220kV | 2010-11-20 | 2012-12-11 | 2.0603 | 69 | 142.9 | 739.8 | 5.1 | 0.8 | 1.5 | 0 | 7.4 | 0 | 0 | 0 | 5.177
交流220kV | 2010-12-29 | 2013-01-21 | 2.0658 | 18.34 | 389.41 | 1311.45 | 3.09 | 0.43 | 0.54 | 0 | 4.06 | 0.013 | 0.005 | 46.9 | 3.3678
交流220kV | 2011-10-27 | 2013-11-21 | 2.0712 | 25.09 | 252.79 | 954.63 | 4.44 | 0.51 | 0.65 | 0 | 5.6 | 0.003 | 0.25 | 51 | 3.7764
交流220kV | 2011-10-27 | 2013-11-21 | 2.0712 | 15.88 | 170.72 | 721.63 | 3.28 | 0.34 | 0.6 | 0 | 4.22 | 0.003 | 0.25 | 51 | 4.227
交流220kV | 2002-03-01 | 2004-03-29 | 2.0795 | 16.5 | 504.5 | 643.2 | 5 | 7.3 | 4.1 | 0 | 16.4 | 0.004 | 0.215 | 50 | 1.2749
交流220kV | 2007-12-24 | 2010-01-22 | 2.0822 | 15 | 122 | 274 | 12.5 | 1.7 | 1.1 | 0 | 15.3 | 0.006 | 0.004 | 55 | 2.2459
交流220kV | 2010-12-02 | 2012-12-31 | 2.0822 | 20 | 210 | 570 | 2.2 | 0.31 | 0.29 | 0 | 2.8 | 0.003 | 0.196 | 69.8 | 2.7143
交流220kV | 2011-05-19 09:04 | 2013-06-20 | 2.0894 | 13.5 | 264.1 | 1128.1 | 4.7 | 1.2 | 1 | 0 | 6.9 | 0.005 | 0 | 60.7 | 4.2715
交流220kV | 2007-12-24 | 2010-01-25 | 2.0904 | 14 | 89 | 213 | 8 | 1.1 | 0.6 | 0 | 9.7 | 0.011 | 0.004 | 51 | 2.3933
交流220kV | 2012-01-19 | 2014-02-20 | 2.0904 | 3 | 96 | 477 | 0.4 | 0.1 | 0.1 | 0 | 0.6 | 0.1 | 0.013 | 75 | 4.9688
交流220kV | 2010-11-15 | 2012-12-24 | 2.1096 | 9.32 | 207.6 | 1277.8 | 2.22 | 0.34 | 0.36 | 0 | 2.92 | 0 | 0 | 0 | 6.1551
交流220kV | 2011-01-20 | 2013-03-06 | 2.126 | 72.37 | 488.28 | 1335.36 | 5.57 | 0.47 | 1.65 | 0 | 7.69 | 0.003 | 0.003 | 52 | 2.7348
交流220kV | 2011-01-20 | 2013-03-06 | 2.126 | 49.95 | 148.64 | 594.02 | 6.95 | 0.7 | 1.73 | 0 | 9.38 | 0.003 | 0.004 | 52 | 3.9964
交流220kV | 2010-01-23 | 2012-03-14 | 2.1397 | 12.87 | 174.12 | 255.19 | 2.62 | 0.29 | 0.22 | 0 | 3.13 | 0.009 | 0.115 | 59 | 1.4656
交流220kV | 2011-04-01 | 2013-05-23 | 2.1452 | 14.24 | 174.23 | 568.97 | 2.45 | 0.51 | 0.45 | 0 | 3.41 | 0.05 | 0.001 | 59 | 3.2656
220 | 2011-02-24 | 2013-04-18 | 2.1479 | 16 | 63 | 189 | 0.8 | 0 | 0 | 0 | 0.8 | 0.007 | 0.001 | 52 | 3
交流220kV | 2011-04-25 08:44 | 2013-06-20 | 2.1552 | 12.8 | 201 | 810.1 | 3.9 | 0.7 | 0.8 | 0 | 5.4 | 0.004 | 0 | 58.5 | 4.0303
交流220kV | 2010-02-05 | 2012-04-05 | 2.1644 | 30.5 | 263.9 | 575.4 | 3.3 | 0.5 | 0.4 | 0.12 | 4.32 | 0.01 | 0.127 | 58 | 2.1804
交流220kV | 2010-02-05 | 2012-04-05 | 2.1644 | 127.7 | 230.6 | 448.5 | 8.9 | 0.3 | 0.9 | 0.12 | 10.22 | 0.02 | 0.087 | 52 | 1.9449
交流220kV | 2010-06-29 | 2012-08-28 | 2.1671 | 7.66 | 237.56 | 872.21 | 2.94 | 0.31 | 0.65 | 0 | 3.9 | 0.008 | 0.002 | 62 | 3.6715
交流220kV | 2011-04-07 | 2013-06-08 | 2.1726 | 16 | 479.17 | 2343.26 | 20.94 | 0.5 | 0.45 | 0 | 21.89 | 0.001 | 0.019 | 63.7 | 4.8902
交流220kV | 2011-06-28 | 2013-08-30 | 2.1753 | 38.7 | 125.4 | 799.9 | 3.4 | 0.3 | 0.7 | 0 | 4.4 | 0 | 0 | 0 | 6.3788
交流220kV | 2010-04-19 | 2012-06-25 | 2.1863 | 19.8 | 61.58 | 285.76 | 6.65 | 0 | 0 | 0 | 6.65 | 0 | 0 | 45 | 4.6405
交流220kV | 2010-12-29 | 2013-03-08 | 2.1918 | 14.14 | 43 | 669 | 1.5 | 0.5 | 0 | 0 | 2 | 0.008 | 0.001 | 50 | 15.5581
交流220kV | 2009-12-28 | 2012-03-09 | 2.1973 | 22.92 | 357.81 | 1287.54 | 4.26 | 0.39 | 0.55 | 0 | 5.2 | 0.01 | 0.063 | 50.9 | 3.5984
交流220kV | 2009-12-28 | 2012-03-09 | 2.1973 | 24.73 | 365.36 | 1369.16 | 4.31 | 0.28 | 0.53 | 0 | 5.12 | 0.01 | 0.222 | 53.3 | 3.7474
交流220kV | 2010-01-16 | 2012-03-29 | 2.2 | 22.1 | 303.73 | 225.9 | 4.23 | 0.94 | 0.39 | 0 | 5.56 | 0.011 | 0.071 | 57 | 0.74375
交流220kV | 2011-12-27 | 2014-03-10 | 2.2027 | 13.18 | 194.65 | 493.58 | 4.85 | 0.44 | 0 | 0 | 5.29 | 0.01 | 0.12 | 43.3 | 2.5357
交流220kV | 2009-11-05 | 2012-01-18 | 2.2027 | 7 | 12 | 521 | 2.4 | 0 | 0 | 0 | 2.4 | 0.034 | 0.47 | 46 | 43.4167
交流220kV | 2009-12-30 | 2012-03-17 | 2.2137 | 17.27 | 186.79 | 1728.35 | 3.1 | 0.73 | 1.06 | 0 | 4.89 | 0.01 | 0.001 | 55.2 | 9.2529
交流220kV | 2011-09-29 | 2013-12-17 | 2.2192 | 11 | 517 | 887 | 4 | 1 | 1 | 0 | 6 | 0 | 0 | 0 | 1.7157
交流220kV | 2011-09-29 | 2013-12-17 | 2.2192 | 11 | 325 | 678 | 3 | 0 | 0 | 0 | 3 | 0 | 0 | 0 | 2.0862
交流220kV | 2011-12-02 | 2014-02-21 | 2.2247 | 14.44 | 158.87 | 528.72 | 2.21 | 0.42 | 0.39 | 0 | 3.02 | 0.011 | 0.001 | 57.1 | 3.328
交流220kV | 2011-03-28 | 2013-06-18 | 2.2274 | 12.03 | 461.33 | 1393.83 | 23.53 | 0.81 | 0.67 | 0 | 25.01 | 0 | 0.005 | 55.8 | 3.0213
交流220kV | 2010-02-02 | 2012-04-27 | 2.2329 | 33.67 | 186.71 | 654.01 | 3.57 | 0.67 | 0 | 0 | 4.24 | 0.007 | 0.001 | 53 | 3.5028
交流220kV | 2011-12-30 | 2014-03-25 | 2.2356 | 6.8 | 48.5 | 294.1 | 1.5 | 0.2 | 0.2 | 0 | 1.9 | 0.001 | 0.1 | 56.3 | 6.0639
交流220kV | 2011-12-30 | 2014-03-25 | 2.2356 | 15.1 | 68.8 | 202.7 | 1.4 | 0.2 | 0.2 | 0 | 1.8 | 0.002 | 0.07 | 68 | 2.9462
交流220kV | 2006-09-06 | 2008-12-01 | 2.2384 | 11 | 152 | 449 | 2.12 | 0.52 | 0.52 | 0 | 3.16 | 0.01 | 0.1 | 49 | 2.9539
交流220kV | 2010-09-26 | 2012-12-26 | 2.2521 | 5 | 145 | 244 | 0.2 | 0.1 | 0.2 | 0 | 0.5 | 0.031 | 0.21 | 56 | 1.6828
交流220kV | 2010-09-26 | 2012-12-26 | 2.2521 | 5 | 45 | 128 | 0.3 | 0.2 | 0.1 | 0 | 0.6 | 0.023 | 0.23 | 56 | 2.8444
交流220kV | 2009-09-20 | 2011-12-22 | 2.2548 | 19.5 | 406.6 | 604.23 | 4.56 | 0.65 | 0.48 | 0 | 5.69 | 0 | 0 | 38.2 | 1.4861
交流220kV | 2010-12-13 | 2013-03-15 | 2.2548 | 17 | 125 | 347 | 2.43 | 0.41 | 0.54 | 0 | 3.38 | 0.035 | 0.38 | 50 | 2.776
交流220kV | 2010-03-26 | 2012-06-27 | 2.2575 | 22.93 | 205.93 | 506.82 | 2.56 | 0 | 0 | 0 | 2.56 | 0.019 | 0.071 | 49 | 2.4611
交流220kV | 2011-12-23 | 2014-03-26 | 2.2575 | 12 | 177 | 552 | 5.22 | 1.09 | 1.03 | 0 | 7.34 | 0.003 | 0.094 | 50 | 3.1186
交流220kV | 2011-01-12 | 2013-04-16 | 2.2603 | 8.71 | 567.43 | 2798.41 | 12.99 | 27.49 | 5.89 | 0 | 46.37 | 0.012 | 0.036 | 49.7 | 4.9317
交流220kV | 2009-11-04 | 2012-02-08 | 2.263 | 30.45 | 603.53 | 1519.93 | 13.54 | 0.73 | 2 | 0 | 16.27 | 0.022 | 0.051 | 57.2 | 2.5184
交流220kV | 2011-01-22 | 2013-04-28 | 2.2658 | 11.67 | 75.02 | 268.73 | 2 | 0.34 | 0.34 | 0 | 2.68 | 0.05 | 0.001 | 58 | 3.5821
交流220kV | 2010-12-20 13:08 | 2013-03-27 | 2.267 | 13.5 | 554.5 | 1760.1 | 3.8 | 0.6 | 0.7 | 0 | 5.1 | 0.01 | 0.001 | 59.8 | 3.1742
交流220kV | 2010-12-26 | 2013-04-02 | 2.2685 | 19 | 292 | 391 | 1.82 | 0.61 | 0.45 | 0 | 2.88 | 0.005 | 0.009 | 50 | 1.339
交流220kV | 2009-09-05 | 2011-12-13 | 2.2712 | 8.51 | 332.93 | 1034.62 | 3.48 | 0 | 0 | 0 | 3.48 | 0.012 | 0 | 0 | 3.1076
交流220kV | 2011-01-12 | 2013-04-22 | 2.2767 | 10.44 | 257.63 | 1942.42 | 11.22 | 9.54 | 2.51 | 0 | 23.27 | 0.012 | 0.041 | 56.5 | 7.5396
交流220kV | 2009-12-17 | 2012-03-28 | 2.2795 | 2.7 | 50.5 | 346.6 | 1.6 | 0 | 0 | 0 | 1.6 | 0 | 0 | 0 | 6.8634
交流220kV | 2009-12-18 | 2012-03-29 | 2.2795 | 87.33 | 124.2 | 809.6 | 4.34 | 0.76 | 1.07 | 0 | 6.17 | 0 | 0 | 0 | 6.5185
交流220kV | 2011-12-08 | 2014-03-20 | 2.2822 | 4.35 | 125.67 | 303.37 | 2.12 | 0.3 | 0.37 | 0 | 2.79 | 0.008 | 0.17 | 58 | 2.414
交流220kV | 2009-04-02 | 2011-07-15 | 2.2849 | 30.1 | 343.4 | 1667.7 | 3.2 | 1.1 | 1.1 | 0 | 5.4 | 0.01 | 0.1 | 61 | 4.8564
交流220kV | 2006-03-15 | 2008-06-26 | 2.2849 | 3.61 | 285.87 | 911.97 | 5.99 | 1.4 | 1.17 | 0 | 8.56 | 0.008 | 0.002 | 42.7 | 3.1902
交流220kV | 2008-11-09 | 2011-02-24 | 2.2932 | 14 | 289 | 133 | 11.37 | 1.25 | 2.1 | 0 | 14.72 | 0.001 | 0.001 | 50 | 0.46021
交流220kV | 2010-05-20 | 2012-09-03 | 2.2932 | 21.85 | 217 | 672 | 2.95 | 0.26 | 2.35 | 0 | 5.56 | 0.031 | 0.127 | 55.8 | 3.0968
交流220kV | 2010-11-14 | 2013-03-01 | 2.2959 | 6.83 | 318.03 | 910.37 | 4.11 | 0.58 | 0.5 | 0 | 5.19 | 0 | 0 | 0 | 2.8625
交流220kV | 2008-11-21 14:12 | 2011-03-10 | 2.297 | 1.91 | 501.83 | 553.38 | 9.61 | 14.42 | 1.71 | 0 | 25.74 | 0.011 | 0.007 | 55.2 | 1.1027
交流220kV | 2009-04-02 | 2011-07-20 | 2.2986 | 25.7 | 371.2 | 1391 | 3.3 | 1.1 | 0.9 | 0 | 5.3 | 0.01 | 0.12 | 62 | 3.7473
交流220kV | 2009-07-17 | 2011-11-03 | 2.2986 | 37 | 101 | 673 | 2.9 | 0.6 | 1.1 | 0.1 | 4.7 | 0.003 | 0.009 | 61 | 6.6634
交流220kV | 2010-11-30 | 2013-03-20 | 2.3041 | 4.5 | 232.7 | 587.4 | 3.2 | 0.6 | 0.5 | 0.06 | 4.36 | 0.006 | 0.093 | 49.2 | 2.5243
交流220kV | 2011-06-30 | 2013-10-18 | 2.3041 | 8.44 | 311.22 | 1111.83 | 4.12 | 0.64 | 0.51 | 0 | 5.27 | 0.01 | 0.109 | 57.5 | 3.5725
交流220kV | 2010-12-04 | 2013-03-27 | 2.3123 | 28 | 74 | 310 | 1.1 | 0.4 | 1.2 | 0 | 2.7 | 0.032 | 0.003 | 75 | 4.1892
交流220kV | 2010-12-04 | 2013-03-27 | 2.3123 | 52 | 128 | 802 | 2.9 | 0.4 | 0.4 | 0.13 | 3.83 | 0.029 | 0.047 | 71 | 6.2656
交流220kV | 2011-04-28 | 2013-08-21 | 2.3178 | 10.84 | 346.73 | 1408.59 | 5.59 | 0.59 | 0.73 | 0 | 6.91 | 0.01 | 0.047 | 58 | 4.0625
交流220kV | 2007-11-13 | 2010-03-09 | 2.3205 | 22.15 | 174.49 | 337.25 | 3.84 | 3.49 | 6.48 | 0 | 13.81 | 0.009 | 0.116 | 46 | 1.9328
交流220kV | 2007-11-16 | 2010-03-12 | 2.3205 | 15.77 | 108.27 | 181.52 | 3.66 | 0.88 | 2.05 | 0 | 6.59 | 0.012 | 0.005 | 51 | 1.6765
交流220kV | 2009-01-19 | 2011-05-17 | 2.3233 | 22.97 | 648.94 | 1046.01 | 9.64 | 0.55 | 1.68 | 0 | 11.87 | 0.02 | 0.04 | 50.2 | 1.6119
交流220kV | 2011-11-02 | 2014-03-02 | 2.3315 | 12.46 | 167.44 | 880.36 | 10.18 | 4.96 | 4.39 | 0 | 19.53 | 0.003 | 0.23 | 42.2 | 5.2578
交流220kV | 2009-11-12 | 2012-03-15 | 2.3397 | 41.33 | 227.69 | 773.04 | 4.47 | 0.66 | 0.67 | 0 | 5.8 | 0.011 | 0.07 | 50.6 | 3.3951
交流220kV | 2009-11-12 | 2012-03-15 | 2.3397 | 48.25 | 413.38 | 943.77 | 8.32 | 12.74 | 5.35 | 0 | 26.41 | 0.013 | 0.056 | 50.5 | 2.2831
交流220kV | 2011-11-24 | 2014-03-27 | 2.3397 | 3.85 | 56.24 | 389.37 | 2.44 | 0.35 | 0.56 | 0 | 3.35 | 0.004 | 0.001 | 53.1 | 6.9234
交流220kV | 2010-06-15 | 2012-10-18 | 2.3452 | 8.5 | 365.35 | 981.9 | 3.58 | 0.5 | 0.46 | 0 | 4.54 | 0.006 | 0.002 | 62 | 2.6876
交流220kV | 2011-11-07 | 2014-03-19 | 2.3644 | 5 | 212 | 619 | 8.11 | 0.39 | 0.6 | 0 | 9.1 | 0.001 | 0.07 | 50 | 2.9198
交流220kV | 2011-11-07 | 2014-03-19 | 2.3644 | 12 | 187 | 469 | 7.85 | 0.49 | 0.5 | 0 | 8.84 | 0.001 | 0.07 | 50 | 2.508
交流220kV | 2011-11-07 | 2014-03-19 | 2.3644 | 13 | 184 | 441 | 8.85 | 0.36 | 0.4 | 0 | 9.61 | 0.001 | 0.07 | 50 | 2.3967
交流220kV | 2010-11-29 | 2013-04-11 | 2.3671 | 14.35 | 70.78 | 372.07 | 2.87 | 0.37 | 3.34 | 0 | 6.58 | 0.02 | 0.066 | 60 | 5.2567
交流220kV | 2009-11-18 | 2012-03-31 | 2.3671 | 5.06 | 36.42 | 195.89 | 1.08 | 0.22 | 0.35 | 0 | 1.65 | 0.014 | 0.001 | 67.6 | 5.3786
交流220kV | 2009-06-22 | 2011-11-03 | 2.3671 | 28 | 114 | 543 | 3 | 0.3 | 0.3 | 0 | 3.6 | 0.003 | 0.03 | 62 | 4.7632
交流220kV | 2011-01-20 | 2013-06-05 | 2.3753 | 22.31 | 256 | 698 | 4.3 | 0.54 | 6.53 | 0.08 | 11.45 | 0.038 | 0.037 | 52.4 | 2.7266
交流220kV | 2010-12-29 | 2013-05-14 | 2.3753 | 16.82 | 407.09 | 1485.58 | 3.28 | 0.47 | 0.57 | 0 | 4.32 | 0.007 | 0.001 | 58.8 | 3.6493
交流220kV | 2010-06-04 | 2012-10-18 | 2.3753 | 8.07 | 248.31 | 647.6 | 2.44 | 0.17 | 0.33 | 0 | 2.94 | 0.009 | 0.001 | 60 | 2.608
交流220kV | 2009-11-28 | 2012-04-14 | 2.3781 | 67 | 182 | 371 | 9.9 | 1.7 | 5.6 | 0 | 17.2 | 0.034 | 0.034 | 45 | 2.0385
交流220kV | 2010-11-29 | 2013-04-15 | 2.3781 | 19.58 | 385.25 | 934.34 | 3.73 | 0.57 | 0.76 | 0 | 5.06 | 0.08 | 0.001 | 60 | 2.4253
交流220kV | 2009-04-23 | 2011-09-08 | 2.3781 | 24 | 52 | 425 | 3.7 | 1.4 | 1.3 | 0.7 | 7.1 | 0.025 | 0.026 | 61 | 8.1731
交流220kV | 2009-04-23 | 2011-09-08 | 2.3781 | 19 | 83 | 500 | 2.3 | 0.8 | 0 | 3.4 | 6.5 | 0.021 | 0.027 | 65 | 6.0241
220 | 2009-06-15 | 2011-11-02 | 2.3836 | 10.79 | 183.9 | 1040.74 | 3.13 | 0.25 | 0 | 0 | 3.38 | 0.009 | 0.033 | 64 | 5.6593
交流220kV | 2010-05-30 | 2012-10-18 | 2.389 | 4.81 | 16.86 | 509.93 | 1.12 | 0.05 | 0 | 0 | 1.17 | 0.008 | 0.002 | 61 | 30.245
交流220kV | 2010-06-02 | 2012-10-22 | 2.3918 | 5.07 | 198.17 | 1040.94 | 3.93 | 0.28 | 0.8 | 0 | 5.01 | 0.009 | 0.001 | 61 | 5.2528
交流220kV | 2010-06-02 | 2012-10-22 | 2.3918 | 4.63 | 247.73 | 1206.73 | 4.15 | 0.29 | 0.81 | 0 | 5.25 | 0.008 | 0.003 | 59 | 4.8712
交流220kV | 2011-10-27 | 2014-03-24 | 2.4082 | 20.5 | 76.2 | 805.2 | 4.3 | 1.3 | 1.5 | 0 | 7.1 | 0.03 | 0.002 | 56 | 10.5669
220 | 2011-10-14 | 2014-03-13 | 2.4137 | 6.18 | 77.15 | 616.9 | 3.49 | 0.87 | 0.48 | 0 | 4.84 | 0.011 | 0.014 | 60 | 7.9961
交流220kV | 2010-01-28 | 2012-06-27 | 2.4137 | 62.98 | 72.64 | 362.26 | 2.32 | 0.42 | 0.5 | 0 | 3.24 | 0.006 | 0.001 | 59 | 4.9871
交流220kV | 2010-01-28 | 2012-06-27 | 2.4137 | 39.89 | 231.16 | 668.87 | 3.08 | 0.57 | 0.51 | 0 | 4.16 | 0.008 | 0.001 | 60 | 2.8935
交流220kV | 2011-01-07 | 2013-06-07 | 2.4164 | 21.6 | 78.7 | 613 | 2.5 | 0.3 | 0.5 | 0 | 3.3 | 0 | 0 | 0 | 7.7891
交流220kV | 2010-12-30 | 2013-05-30 | 2.4164 | 11.32 | 91.46 | 588.92 | 2.15 | 0.36 | 0.48 | 0 | 2.99 | 0.003 | 0.25 | 51 | 6.4391
交流220kV | 2010-11-26 | 2013-04-26 | 2.4164 | 2 | 78 | 410 | 0.53 | 0.86 | 0.3 | 0 | 1.69 | 0.003 | 0.067 | 58 | 5.2564
交流220kV | 2010-11-26 | 2013-04-26 | 2.4164 | 2 | 78 | 410 | 0.53 | 0.86 | 0.3 | 0 | 1.69 | 0.003 | 0.061 | 58 | 5.2564
交流220kV | 2010-10-15 | 2013-03-15 | 2.4164 | 9 | 238 | 1249 | 3.57 | 0.41 | 1.36 | 0.1 | 5.44 | 0.008 | 0.07 | 51.5 | 5.2479
交流220kV | 2010-12-22 | 2013-05-23 | 2.4192 | 49.74 | 203.56 | 969.1 | 2.96 | 0.45 | 0.49 | 0 | 3.9 | 0.07 | 0.001 | 58 | 4.7608
交流220kV | 2009-01-15 | 2011-06-20 | 2.4274 | 31 | 172 | 805 | 2.7 | 0 | 0 | 0 | 2.7 | 0.01 | 0 | 0 | 4.6802
交流220kV | 2011-01-10 | 2013-06-15 | 2.4301 | 11.05 | 352.06 | 1333.55 | 4.46 | 0.96 | 1.09 | 0 | 6.51 | 0 | 0 | 58 | 3.7878
交流220kV | 2011-01-10 | 2013-06-15 | 2.4301 | 11.05 | 352.06 | 1333.55 | 4.46 | 0.96 | 1.09 | 0 | 6.51 | 0 | 0 | 55 | 3.7878
交流220kV | 2010-07-27 | 2012-12-31 | 2.4329 | 11.92 | 66.77 | 308.59 | 1.49 | 0.31 | 0.5 | 0.06 | 2.36 | 0.01 | 0.106 | 59 | 4.6217
交流220kV | 2009-08-04 | 2012-01-09 | 2.4329 | 21 | 364 | 1021 | 2.7 | 0.4 | 0.2 | 0 | 3.3 | 0.047 | 0.06 | 63 | 2.8049
交流220kV | 2009-07-10 | 2011-12-16 | 2.4356 | 26.5 | 64.5 | 539.3 | 2.4 | 0.5 | 0.7 | 0 | 3.6 | 0 | 0 | 0 | 8.3612
220 | 2011-10-19 | 2014-03-27 | 2.4384 | 12.17 | 214.89 | 753.58 | 2.75 | 0.27 | 0.4 | 0 | 3.42 | 0.014 | 0.024 | 54 | 3.5068
交流220kV | 2011-07-13 | 2013-12-19 | 2.4384 | 6.6 | 7.64 | 25.57 | 1.63 | 0 | 0 | 0 | 1.63 | 0 | 0 | 68.5 | 3.3469
交流220kV | 2011-04-19 | 2013-09-26 | 2.4411 | 6.61 | 251.1 | 989.26 | 4.2 | 0.65 | 0.63 | 0 | 5.48 | 0.015 | 0.115 | 44.3 | 3.9397
交流220kV | 2011-04-19 | 2013-09-26 | 2.4411 | 11.69 | 303.73 | 1040.96 | 4.12 | 0.56 | 0.33 | 0 | 5.01 | 0.018 | 0.013 | 59.2 | 3.4273
交流220kV | 2011-06-26 | 2013-12-04 | 2.4438 | 21.5 | 110.4 | 798.5 | 3.9 | 1.3 | 0.7 | 0 | 5.9 | 0 | 0 | 0 | 7.2328
交流220kV | 2010-12-28 | 2013-06-07 | 2.4438 | 41.82 | 148 | 386 | 2.32 | 0.37 | 0.51 | 0 | 3.2 | 0.019 | 0.056 | 52 | 2.6081
220 | 2009-10-28 | 2012-04-09 | 2.4493 | 4.69 | 146.59 | 542.98 | 2.24 | 0.42 | 0.32 | 0 | 2.98 | 0.011 | 0.001 | 60 | 3.7041
交流220kV | 2010-12-11 16:57 | 2013-05-24 | 2.4501 | 9.7 | 362.2 | 3268.9 | 13 | 10.2 | 3.3 | 0 | 26.5 | 0.015 | 0.08 | 44.9 | 9.0251
交流220kV | 2010-12-23 | 2013-06-06 | 2.4548 | 2.81 | 249.45 | 906.38 | 10.78 | 10.08 | 2.82 | 0 | 23.68 | 0.007 | 0.28 | 59.3 | 3.6335
交流220kV | 2011-06-28 | 2013-12-10 | 2.4548 | 10.24 | 105.97 | 850.55 | 2.43 | 0 | 0 | 0 | 2.43 | 0 | 0 | 0 | 8.0263
交流220kV | 2011-06-28 | 2013-12-10 | 2.4548 | 55.79 | 116.74 | 709.84 | 0.8 | 0 | 0 | 0 | 0.8 | 0 | 0 | 0 | 6.0805
交流220kV | 2010-12-23 | 2013-06-06 | 2.4548 | 2.81 | 205.45 | 906.38 | 10.78 | 10.08 | 2.82 | 0 | 23.68 | 0.007 | 0.28 | 59.3 | 4.4117
交流220kV | 2010-06-23 | 2012-12-11 | 2.4712 | 4.6 | 90.5 | 416.2 | 3.4 | 0.2 | 0.4 | 0 | 4 | 0 | 0 | 0 | 4.5989
交流220kV | 2010-06-22 | 2012-12-11 | 2.474 | 4.9 | 142.5 | 337.4 | 4.7 | 0.2 | 0.3 | 0 | 5.2 | 0 | 0 | 0 | 2.3677
交流220kV | 2009-06-25 | 2011-12-16 | 2.4767 | 11 | 492 | 2606 | 5.2 | 1.3 | 1.3 | 0.1 | 7.9 | 0.003 | 0.003 | 40 | 5.2967
交流220kV | 2008-12-26 | 2011-06-21 | 2.4849 | 14.6 | 295.1 | 1435.7 | 0.9 | 0 | 0 | 0 | 0.9 | 0.01 | 0 | 58.4 | 4.8651
交流220kV | 2008-12-26 | 2011-06-21 | 2.4849 | 11.4 | 155.4 | 898.1 | 1.7 | 0.2 | 0.7 | 0 | 2.6 | 0.01 | 0 | 58.8 | 5.7793
交流220kV | 2009-06-21 | 2011-12-16 | 2.4877 | 9.9 | 232.7 | 805.8 | 3.1 | 0.3 | 0.5 | 0 | 3.9 | 0 | 0 | 0 | 3.4628
交流220kV | 2009-04-30 | 2011-10-26 | 2.4904 | 28 | 76 | 598 | 78.1 | 77.8 | 26.4 | 0.3 | 182.6 | 0.003 | 0.003 | 74 | 7.8684
交流220kV | 2010-03-29 | 2012-09-24 | 2.4932 | 4.07 | 105.84 | 628.85 | 2.06 | 0.17 | 0.24 | 0 | 2.47 | 0.008 | 0.003 | 63 | 5.9415
交流220kV | 2010-03-29 | 2012-09-24 | 2.4932 | 5.03 | 106.93 | 658.43 | 2.11 | 0.21 | 0.21 | 0 | 2.53 | 0.006 | 0.001 | 62 | 6.1576
交流220kV | 2011-08-25 | 2014-02-20 | 2.4932 | 12.08 | 40.18 | 216.29 | 3.5 | 3.9 | 1.57 | 0 | 8.97 | 0.006 | 0.06 | 66 | 5.383
交流220kV | 2006-03-15 | 2008-09-11 | 2.4959 | 7.8 | 359.1 | 974.9 | 7 | 1.3 | 1.2 | 0 | 9.5 | 0.002 | 0.003 | 51.4 | 2.7148
交流220kV | 2009-08-06 | 2012-02-06 | 2.5041 | 2.4 | 21.2 | 341.5 | 2.1 | 0.4 | 0.3 | 0 | 2.8 | 0.008 | 0.05 | 65.8 | 16.1085
交流220kV | 2010-06-30 | 2012-12-31 | 2.5068 | 7.93 | 127.57 | 695.99 | 1.59 | 0.22 | 0.33 | 0 | 2.14 | 0 | 0 | 0 | 5.4557
220 | 2009-10-15 | 2012-04-18 | 2.5096 | 27.5 | 161.87 | 638.43 | 2.84 | 0.31 | 0.25 | 0 | 3.4 | 0.006 | 0.084 | 60 | 3.9441
220 | 2009-10-15 | 2012-04-18 | 2.5096 | 18.47 | 179.86 | 732.68 | 3.33 | 0.47 | 0.32 | 0 | 4.12 | 0.006 | 0.073 | 60 | 4.0736
交流220kV | 2009-01-19 | 2011-07-25 | 2.5123 | 13.69 | 168.1 | 551.44 | 6.83 | 0.46 | 1.17 | 0 | 8.46 | 0.005 | 0.001 | 63 | 3.2804
交流220kV | 2009-01-19 | 2011-07-25 | 2.5123 | 15.96 | 145.11 | 484.11 | 15.19 | 0.84 | 1.28 | 0 | 17.31 | 0.004 | 0.002 | 62 | 3.3362
交流220kV | 2009-09-20 | 2012-03-26 | 2.5151 | 13.95 | 314.75 | 484.71 | 3.57 | 0.47 | 1.52 | 0 | 5.56 | 0 | 0 | 0 | 1.54
交流220kV | 2010-11-14 | 2013-05-20 | 2.5151 | 3.2 | 344.83 | 1157.63 | 4.83 | 0.67 | 0.62 | 0 | 6.12 | 0.002 | 0.1 | 43 | 3.3571
交流220kV | 2009-01-19 | 2011-07-29 | 2.5233 | 19.38 | 641.38 | 976.23 | 9.52 | 0.59 | 1.33 | 0 | 11.44 | 0.011 | 0.007 | 53.5 | 1.5221
220 | 2010-08-19 | 2013-03-01 | 2.5342 | 25.83 | 563.31 | 666.11 | 5.4 | 0.43 | 0.82 | 0 | 6.65 | 0.007 | 0.076 | 60 | 1.1825
交流220kV | 2010-03-15 | 2012-09-28 | 2.5425 | 20 | 125 | 817 | 2.6 | 0.2 | 0.3 | 0 | 3.1 | 0.047 | 0.028 | 59.8 | 6.536
交流220kV | 2010-03-15 | 2012-09-28 | 2.5425 | 43 | 155 | 887 | 3 | 0.5 | 0.5 | 0 | 4 | 0.046 | 0.026 | 61.2 | 5.7226
交流220kV | 2009-12-18 | 2012-07-06 | 2.5507 | 86.71 | 133.86 | 1018.49 | 5.58 | 0.84 | 1.17 | 0 | 7.59 | 0 | 0.041 | 58.3 | 7.6086
交流220kV | 2011-05-19 09:04 | 2013-12-06 | 2.5524 | 10.3 | 311.4 | 977.8 | 5.3 | 0.6 | 0.9 | 0 | 6.8 | 0 | 0 | 0 | 3.14
220 | 2009-09-20 | 2012-04-09 | 2.5534 | 9.63 | 192.41 | 215.68 | 13.45 | 0.81 | 0.62 | 0 | 14.88 | 0.01 | 0.001 | 60 | 1.1209
交流220kV | 2009-08-31 | 2012-03-20 | 2.5534 | 62.21 | 106.7 | 447.06 | 11.35 | 2.68 | 1.83 | 0 | 15.86 | 0.003 | 0.001 | 55.3 | 4.1899
交流220kV | 2009-08-31 | 2012-03-20 | 2.5534 | 110.26 | 44.08 | 283.64 | 15.17 | 2.39 | 3.43 | 0 | 20.99 | 0.003 | 0.001 | 54.7 | 6.4347
交流220kV | 2011-05-31 | 2013-12-19 | 2.5562 | 7.26 | 30.23 | 56.29 | 2.59 | 0.35 | 0 | 0 | 2.94 | 0 | 0 | 54.2 | 1.8621
220 | 2011-08-25 | 2014-03-16 | 2.5589 | 6.22 | 139.33 | 415.71 | 2.51 | 0.25 | 0.36 | 0 | 3.12 | 0.006 | 0.023 | 66 | 2.9836
交流220kV | 2010-11-15 | 2013-06-09 | 2.5671 | 13.9 | 243.14 | 1608.02 | 2.73 | 0.75 | 0.76 | 0 | 4.24 | 0 | 0 | 0 | 6.6136
交流220kV | 2009-05-20 | 2011-12-13 | 2.5671 | 23.1 | 205.2 | 640.8 | 3.8 | 0.4 | 0.4 | 0 | 4.6 | 0 | 0 | 0 | 3.1228
交流220kV | 2006-02-21 | 2008-09-16 | 2.5699 | 16.5 | 987.5 | 874.6 | 1.8 | 0 | 0.1 | 0 | 1.9 | 0.009 | 0.004 | 57.5 | 0.88567
交流220kV | 2011-07-29 | 2014-02-28 | 2.589 | 9.9 | 107.03 | 255.69 | 3.2 | 0.67 | 1.38 | 0 | 5.25 | 0.009 | 0.09 | 62.4 | 2.389
交流220kV | 2011-07-10 | 2014-02-10 | 2.5918 | 4 | 108.5 | 639.8 | 2.3 | 0.3 | 0.5 | 0 | 3.1 | 0.003 | 0.106 | 69.2 | 5.8968
交流220kV | 2011-07-28 | 2014-02-28 | 2.5918 | 7.4 | 101.87 | 235.7 | 2.76 | 0.49 | 1.06 | 0 | 4.31 | 0.009 | 0.05 | 62 | 2.3137
交流220kV | 2010-05-28 | 2012-12-30 | 2.5945 | 38 | 101 | 415 | 2.25 | 0.37 | 0.54 | 0 | 3.16 | 0.05 | 0.103 | 69.7 | 4.1089
交流220kV | 2010-11-20 | 2013-06-25 | 2.5973 | 84.6 | 145.2 | 1170.9 | 6.1 | 0.8 | 2.5 | 0 | 9.4 | 0.021 | 0 | 66.6 | 8.064
交流220kV | 2010-11-28 | 2013-07-04 | 2.6 | 33.16 | 46.2 | 707.36 | 2.67 | 0.26 | 0.5 | 0 | 3.43 | 0 | 0.002 | 41.9 | 15.3108
交流220kV | 2009-04-10 | 2011-11-17 | 2.6055 | 55 | 233 | 2974 | 6.9 | 0.9 | 1.8 | 0.1 | 9.7 | 0.024 | 0.001 | 41 | 12.7639
交流220kV | 2011-04-25 08:44 | 2013-12-06 | 2.6182 | 10.6 | 244.7 | 791.8 | 4.3 | 0.5 | 0.8 | 0 | 5.6 | 0 | 0 | 0 | 3.2358
交流220kV | 2011-05-08 | 2013-12-23 | 2.6301 | 34.13 | 143.44 | 560.74 | 2.48 | 0.53 | 0 | 0 | 3.01 | 0.01 | 0.275 | 54.4 | 3.9092
交流220kV | 2011-05-08 | 2013-12-23 | 2.6301 | 7.32 | 261.25 | 658.68 | 4.44 | 0.71 | 0.57 | 0 | 5.72 | 0.012 | 0.218 | 69 | 2.5213
交流220kV | 2011-05-05 | 2013-12-23 | 2.6384 | 18.45 | 207.58 | 385.93 | 2.81 | 0.26 | 0.47 | 0 | 3.54 | 0.009 | 0.12 | 64 | 1.8592
交流220kV | 2011-05-05 | 2013-12-23 | 2.6384 | 20.84 | 228.18 | 470.84 | 2.83 | 0.34 | 0.39 | 0 | 3.56 | 0.011 | 0.269 | 65.6 | 2.0635
220 | 2009-03-06 | 2011-11-02 | 2.6603 | 24.2 | 223.73 | 1273.75 | 3.78 | 0.64 | 0.77 | 0 | 5.19 | 0.013 | 0.063 | 61.6 | 5.6932
交流220kV | 2010-07-23 | 2013-03-20 | 2.6603 | 148 | 102 | 480 | 17.52 | 1.8 | 3.76 | 0 | 23.08 | 0.001 | 0.06 | 62.5 | 4.7059
交流220kV | 2009-05-19 | 2012-01-17 | 2.6658 | 16.87 | 732.64 | 1538.8 | 23.92 | 1.05 | 1.93 | 0 | 26.9 | 0.01 | 0.005 | 53.2 | 2.1003
220 | 2009-03-10 | 2011-11-11 | 2.674 | 26.08 | 1043.06 | 2840.2 | 7.9 | 0.59 | 0.98 | 0 | 9.47 | 0.03 | 0.68 | 57 | 2.7229
交流220kV | 2011-04-07 | 2013-12-10 | 2.6795 | 10.11 | 572.45 | 2688.01 | 21.93 | 0.58 | 0.64 | 0 | 23.15 | 0 | 0 | 0 | 4.6956
交流220kV | 2011-03-22 | 2013-11-25 | 2.6822 | 18 | 88 | 153 | 5.5 | 4.9 | 0.8 | 0.1 | 11.3 | 0.043 | 0.08 | 56 | 1.7386
交流220kV | 2006-06-30 | 2009-03-06 | 2.6849 | 7.83 | 273.29 | 899.32 | 3.02 | 0 | 0 | 0 | 3.02 | 0.018 | 0.108 | 52.8 | 3.2907
交流220kV | 2006-06-30 | 2009-03-06 | 2.6849 | 8.97 | 304.44 | 891.15 | 3.12 | 0 | 0 | 0 | 3.12 | 0.024 | 0.115 | 59.4 | 2.9272
交流220kV | 2009-03-01 | 2011-11-09 | 2.6932 | 16.3 | 323.4 | 1652.88 | 4.01 | 0.63 | 0.94 | 0 | 5.58 | 0.009 | 0.135 | 57.3 | 5.1109
交流220kV | 2009-03-01 | 2011-11-09 | 2.6932 | 10.54 | 334.53 | 1845.54 | 5.96 | 0.78 | 1.06 | 0 | 7.8 | 0.009 | 0.632 | 60.4 | 5.5168
220 | 2010-06-19 | 2013-03-01 | 2.7014 | 13.72 | 560.73 | 906.77 | 6.59 | 0.82 | 1.02 | 0 | 8.43 | 0.007 | 0.102 | 54 | 1.6171
交流220kV | 2008-06-18 | 2011-03-02 | 2.7041 | 18 | 333 | 650 | 3.9 | 0.3 | 0.5 | 0 | 4.7 | 0.004 | 0.004 | 48 | 1.952
交流220kV | 2011-04-28 | 2014-01-09 | 2.7041 | 10 | 481 | 1312 | 5.1 | 0.4 | 0.6 | 0 | 6.1 | 0.009 | 0.2 | 59 | 2.7277
交流220kV | 2010-09-26 | 2013-06-10 | 2.7068 | 6 | 175 | 258 | 0.2 | 0.3 | 0.4 | 0 | 0.9 | 0.014 | 0.23 | 55 | 1.4743
交流220kV | 2009-06-26 | 2012-03-13 | 2.7151 | 13.77 | 325.7 | 459.56 | 4.19 | 0.67 | 0.48 | 0 | 5.34 | 0.008 | 0.002 | 58 | 1.411
交流220kV | 2010-03-31 | 2012-12-16 | 2.7151 | 22 | 66 | 574 | 2.16 | 0.42 | 0.4 | 0 | 2.98 | 0.042 | 0.523 | 64.4 | 8.697
交流220kV | 2011-06-30 | 2014-03-18 | 2.7178 | 39.35 | 71.03 | 535.05 | 5.63 | 0.42 | 1.76 | 0 | 7.81 | 0 | 0.098 | 45.2 | 7.5327
交流220kV | 2011-06-25 15:41 | 2014-03-15 | 2.7215 | 15.37 | 127.84 | 248 | 2.87 | 0.43 | 0.42 | 0.16 | 3.88 | 0.004 | 0.064 | 65.3 | 1.9399
交流220kV | 2011-06-25 15:32 | 2014-03-15 | 2.7215 | 10.7 | 173.95 | 430 | 3.11 | 0.27 | 0.43 | 0 | 3.81 | 0.017 | 0.463 | 65.2 | 2.472
交流220kV | 2011-03-17 | 2013-12-06 | 2.726 | 10.7 | 208.4 | 917.3 | 5.2 | 0.4 | 1.7 | 0 | 7.3 | 0 | 0 | 0 | 4.4016
交流220kV | 2011-03-17 | 2013-12-06 | 2.726 | 16.1 | 183.4 | 572.5 | 4.9 | 0.6 | 1.9 | 0 | 7.4 | 0 | 0 | 0 | 3.1216
交流220kV | 2007-10-31 | 2010-07-26 | 2.737 | 49.8 | 223.2 | 737.8 | 3.9 | 1.6 | 0.6 | 0 | 6.1 | 0.014 | 0 | 56.7 | 3.3056
交流220kV | 2008-05-30 | 2011-02-24 | 2.7397 | 16 | 169 | 207 | 24.95 | 0.94 | 2.05 | 0 | 27.94 | 0.001 | 0.05 | 50 | 1.2249
交流220kV | 2008-06-20 | 2011-03-18 | 2.7425 | 30 | 116 | 603 | 2.9 | 0 | 0.5 | 0 | 3.4 | 0.007 | 0.001 | 56 | 5.1983
交流220kV | 2008-09-27 | 2011-06-27 | 2.7479 | 14.7 | 275.3 | 1777.4 | 4 | 0 | 0 | 0 | 4 | 0.02 | 0 | 68 | 6.4562
交流220kV | 2008-09-27 | 2011-06-27 | 2.7479 | 11.6 | 221.1 | 1598.5 | 3 | 0 | 0 | 0 | 3 | 0.02 | 0 | 55.7 | 7.2298
交流220kV | 2009-06-15 | 2012-03-16 | 2.7534 | 25.93 | 282.19 | 543.06 | 3.27 | 0.57 | 0.65 | 0 | 4.49 | 0.005 | 0.001 | 52 | 1.9244
交流220kV | 2009-09-05 | 2012-06-07 | 2.7562 | 14.34 | 371.85 | 981.15 | 3.77 | 0 | 0 | 0 | 3.77 | 0.02 | 0.074 | 0 | 2.6386
交流220kV | 2007-11-16 | 2010-08-20 | 2.7616 | 85.82 | 94.16 | 271.01 | 5.07 | 1.91 | 4.72 | 0.31 | 12.01 | 0.008 | 0.095 | 62 | 2.8782
交流220kV | 2010-03-26 | 2012-12-31 | 2.7699 | 31.87 | 367.54 | 723.57 | 3.47 | 0.22 | 0.65 | 0 | 4.34 | 0 | 0 | 0 | 1.9687
交流220kV | 2010-08-31 | 2013-06-08 | 2.7726 | 10.54 | 137.94 | 500.75 | 2.01 | 0 | 0.43 | 0 | 2.44 | 0.01 | 0.2 | 70.7 | 3.6302
交流220kV | 2010-08-31 | 2013-06-08 | 2.7726 | 4.55 | 53.12 | 314.85 | 1.68 | 0 | 0.49 | 0 | 2.17 | 0.011 | 0.1 | 75.4 | 5.9271
交流220kV | 2008-12-05 | 2011-09-16 | 2.7808 | 56 | 350 | 1265 | 6.6 | 0.8 | 1.3 | 0 | 8.7 | 0.003 | 0.001 | 75 | 3.6143
交流220kV | 2008-12-05 | 2011-09-16 | 2.7808 | 29 | 170 | 1390 | 4.9 | 0.7 | 1 | 0 | 6.6 | 0.003 | 0.001 | 75 | 8.1765
交流220kV | 2009-01-05 | 2011-10-18 | 2.7836 | 54.67 | 81.64 | 875.53 | 4.04 | 0.65 | 1.82 | 0 | 6.51 | 0.048 | 0.118 | 62 | 10.7243
交流220kV | 2009-09-20 | 2012-07-03 | 2.7863 | 11.6 | 432.89 | 761.6 | 2.67 | 0 | 0 | 0 | 2.67 | 0.002 | 0 | 56.3 | 1.7593
交流220kV | 2006-09-06 | 2009-06-19 | 2.7863 | 18 | 239 | 566 | 2.65 | 0.83 | 0.59 | 0 | 4.07 | 0.01 | 0.08 | 53 | 2.3682
交流220kV | 2008-12-05 | 2011-09-19 | 2.789 | 29 | 170 | 1390 | 4.9 | 0.7 | 1 | 0 | 6.6 | 0.003 | 0.007 | 75 | 8.1765
交流220kV | 2009-01-05 | 2011-10-20 | 2.789 | 54.7 | 81.6 | 875.5 | 4.04 | 0.7 | 1.8 | 0 | 6.54 | 0.048 | 0.02 | 62 | 10.7292
交流220kV | 2009-07-10 | 2012-04-24 | 2.7918 | 34.3 | 91.9 | 803 | 4.3 | 0.8 | 0.8 | 0 | 5.9 | 0.006 | 0 | 66 | 8.7378
交流220kV | 2009-06-15 | 2012-04-01 | 2.7973 | 33.14 | 291.31 | 500.25 | 5.08 | 0.41 | 0.79 | 0 | 6.28 | 0.007 | 0.003 | 56.3 | 1.7172
交流220kV | 2009-07-05 | 2012-04-24 | 2.8055 | 19.9 | 303.3 | 696.3 | 3.7 | 0.2 | 0.2 | 0 | 4.1 | 0.018 | 0.024 | 54.8 | 2.2957
交流220kV | 2010-05-21 | 2013-03-11 | 2.8082 | 16.85 | 619.47 | 1721.71 | 67.95 | 0.54 | 4.2 | 0 | 72.69 | 0.014 | 0.05 | 55.6 | 2.7793
交流220kV | 2011-05-31 | 2014-03-21 | 2.8082 | 15 | 176 | 389 | 16.46 | 0.29 | 0.5 | 0 | 17.25 | 0.001 | 0.14 | 50 | 2.2102
交流220kV | 2011-05-31 | 2014-03-21 | 2.8082 | 13 | 182 | 392 | 19.63 | 0.34 | 0.75 | 0 | 20.72 | 0.001 | 0.07 | 50 | 2.1538
交流220kV | 2009-07-03 | 2012-04-24 | 2.811 | 19.6 | 303.6 | 749.4 | 3.6 | 0.3 | 0.3 | 0 | 4.2 | 0.02 | 0.04 | 58.8 | 2.4684
220 | 2009-06-16 | 2012-04-11 | 2.8219 | 39.33 | 389.93 | 541.83 | 4.77 | 3.26 | 3.94 | 0 | 11.97 | 0.016 | 0.001 | 60 | 1.3896
交流220kV | 2008-04-30 | 2011-02-24 | 2.8219 | 22 | 336 | 224 | 35.04 | 1.07 | 3.27 | 0 | 39.38 | 0.001 | 0.001 | 50 | 0.66667
交流220kV | 2009-04-14 | 2012-02-10 | 2.8274 | 13.5 | 272.3 | 684 | 4.41 | 0.26 | 0.64 | 0 | 5.31 | 0.011 | 0.145 | 61.6 | 2.5119
交流220kV | 2009-04-14 | 2012-02-10 | 2.8274 | 15.25 | 100.51 | 201.23 | 1.4 | 0 | 0 | 0 | 1.4 | 0.011 | 0.066 | 64.8 | 2.0021
交流220kV | 2010-07-23 | 2013-05-21 | 2.8301 | 15.69 | 298.32 | 2183.72 | 5.64 | 0.59 | 0.86 | 0 | 7.09 | 0.06 | 0.001 | 60 | 7.3201
交流220kV | 2009-06-21 | 2012-04-24 | 2.8438 | 15.1 | 358.7 | 1212.6 | 6.5 | 0.6 | 1.3 | 0 | 8.4 | 0.005 | 0 | 67.6 | 3.3805
交流220kV | 2010-04-19 | 2013-02-21 | 2.8466 | 14.3 | 140.8 | 328.6 | 1.6 | 0.2 | 0.4 | 0 | 2.2 | 0.04 | 0.13 | 60.8 | 2.3338
220 | 2008-12-27 | 2011-11-02 | 2.8493 | 26.21 | 491.79 | 1821.07 | 5.91 | 3.42 | 1.35 | 0 | 10.68 | 0.004 | 0.1 | 58.8 | 3.7029
交流220kV | 2009-07-15 | 2012-05-24 | 2.8603 | 31.08 | 200.62 | 546.62 | 9.12 | 2.73 | 0.89 | 0 | 12.74 | 0.005 | 0.001 | 59 | 2.7247
交流220kV | 2009-12-28 | 2012-11-07 | 2.863 | 11 | 481.9 | 959.4 | 5.9 | 0 | 0.7 | 0 | 6.6 | 0.012 | 0.062 | 54.8 | 1.9909
交流220kV | 2009-12-28 | 2012-11-07 | 2.863 | 10.2 | 428.8 | 637.2 | 5.1 | 0 | 0.5 | 0 | 5.6 | 0.012 | 0.043 | 52.3 | 1.486
交流220kV | 2009-12-05 | 2012-10-18 | 2.8712 | 21.95 | 392.34 | 715.01 | 3.88 | 0.42 | 0.47 | 0 | 4.77 | 0.011 | 0.001 | 61 | 1.8224
交流220kV | 2009-12-05 | 2012-10-18 | 2.8712 | 19.39 | 365.54 | 666.54 | 3.72 | 0.46 | 0.48 | 0 | 4.66 | 0.006 | 0.002 | 60 | 1.8234
交流220kV | 2008-10-20 | 2011-09-07 | 2.8822 | 22 | 129 | 998 | 5.5 | 0.6 | 0.9 | 0 | 7 | 0.05 | 0.018 | 61 | 7.7364
交流220kV | 2009-01-15 | 2011-12-13 | 2.9096 | 17.05 | 204.57 | 1161.47 | 2.9 | 0 | 0 | 0 | 2.9 | 0.008 | 0 | 0 | 5.6776
交流220kV | 2009-04-10 | 2012-03-07 | 2.9096 | 31.9 | 126.7 | 292.2 | 14.6 | 12.1 | 1.9 | 0.2 | 28.8 | 0.006 | 0.022 | 60.4 | 2.3062
交流220kV | 2009-04-10 | 2012-03-07 | 2.9096 | 16.5 | 100.3 | 385.2 | 3.3 | 1.5 | 0.8 | 0 | 5.6 | 0.007 | 0.029 | 62.4 | 3.8405
交流220kV | 2011-01-07 | 2013-12-05 | 2.9123 | 29.2 | 68.5 | 558 | 2.3 | 0.2 | 0.4 | 0 | 2.9 | 0.05 | 0.6 | 47 | 8.146
交流220kV | 2010-04-20 | 2013-03-20 | 2.9178 | 23.72 | 823.35 | 2500.3 | 23.04 | 0.8 | 2.42 | 0 | 26.26 | 0.017 | 0.075 | 59.2 | 3.0367
交流220kV | 2010-12-30 | 2013-12-03 | 2.9288 | 21.32 | 187.32 | 669.96 | 2.07 | 0.27 | 0.54 | 0 | 2.88 | 0.003 | 0.25 | 51 | 3.5766
交流220kV | 2011-04-20 | 2014-03-25 | 2.9315 | 9.89 | 178.35 | 794.26 | 2.77 | 0.25 | 0.32 | 0 | 3.34 | 0.005 | 0.001 | 58.8 | 4.4534
交流220kV | 2010-06-30 | 2013-06-09 | 2.9452 | 7.82 | 132.32 | 827 | 1.7 | 0.44 | 0.45 | 0 | 2.59 | 0 | 0 | 0 | 6.25
交流220kV | 2009-03-15 | 2012-02-24 | 2.9479 | 80.58 | 57.11 | 548.47 | 34.09 | 30.73 | 9.02 | 0 | 73.84 | 0.021 | 0 | 57.2 | 9.6037
交流220kV | 2008-06-28 | 2011-06-10 | 2.9507 | 31.38 | 289 | 2366.05 | 8.85 | 0.81 | 1.92 | 0 | 11.58 | 0 | 0 | 0 | 8.187
交流220kV | 2008-12-26 | 2011-12-16 | 2.9726 | 24.7 | 244 | 1218 | 3.4 | 0.9 | 0.7 | 0 | 5 | 0 | 0 | 0 | 4.9918
交流220kV | 2008-12-26 | 2011-12-16 | 2.9726 | 16.3 | 262 | 1410 | 4.4 | 0.5 | 0.6 | 0 | 5.5 | 0 | 0 | 0 | 5.3817
交流220kV | 2009-11-12 | 2012-11-02 | 2.9753 | 30.9 | 424.5 | 871.9 | 8.3 | 15 | 5 | 0 | 28.3 | 0.012 | 0.072 | 55.3 | 2.0539
交流220kV | 2009-11-12 | 2012-11-02 | 2.9753 | 25.5 | 241.3 | 739.1 | 5.1 | 0 | 0.5 | 0 | 5.6 | 0.012 | 0.042 | 54.4 | 3.063
交流220kV | 2010-04-19 | 2013-04-10 | 2.9781 | 9.2 | 110.6 | 313.3 | 1.6 | 0.2 | 0.3 | 0 | 2.1 | 0.02 | 0.14 | 57.6 | 2.8327
交流220kV | 2008-06-26 | 2011-06-20 | 2.9836 | 6.2 | 339 | 753 | 5.4 | 0.8 | 0 | 0 | 6.2 | 0.01 | 0 | 0 | 2.2212
交流220kV | 2009-02-12 | 2012-02-06 | 2.9836 | 4 | 93.2 | 644.2 | 6.5 | 0.4 | 1.1 | 0 | 8 | 0.004 | 0.039 | 65.3 | 6.912
交流220kV | 2007-08-10 | 2010-08-04 | 2.9863 | 3 | 15 | 248 | 1.1 | 0 | 0 | 0 | 1.1 | 0.005 | 0 | 50 | 16.5333
交流220kV | 2009-03-01 | 2012-02-24 | 2.9863 | 12.68 | 362.25 | 1453.71 | 5.93 | 0.72 | 1 | 0 | 7.65 | 0.008 | 0.501 | 55.6 | 4.013
交流220kV | 2009-03-01 | 2012-02-24 | 2.9863 | 17.66 | 299.63 | 1321.42 | 3.95 | 0.52 | 0.83 | 0 | 5.3 | 0.009 | 0.105 | 54.7 | 4.4102
交流220kV | 2008-10-31 | 2011-10-26 | 2.9863 | 39 | 192 | 739 | 5.3 | 2.6 | 1.5 | 0.1 | 9.5 | 0.003 | 0.009 | 64 | 3.849
交流220kV | 2010-06-26 | 2013-06-21 | 2.989 | 25.75 | 594.89 | 1017.71 | 6.87 | 0.6 | 0.8 | 0 | 8.27 | 0.005 | 0.087 | 66 | 1.7108
220 | 2009-03-31 | 2012-03-27 | 2.9918 | 112.02 | 342.07 | 860.37 | 4.48 | 0.41 | 0.83 | 0 | 5.72 | 0.008 | 0.084 | 54 | 2.5152
交流220kV | 2010-04-19 | 2013-04-15 | 2.9918 | 9.8 | 63.8 | 240.6 | 1.7 | 0.4 | 0.4 | 0.1 | 2.6 | 0.03 | 0.15 | 62 | 3.7712
交流220kV | 2010-06-23 | 2013-06-20 | 2.9945 | 6 | 87.1 | 645.1 | 4.2 | 0.3 | 0.4 | 0 | 4.9 | 0.014 | 0 | 61 | 7.4064
交流220kV | 2010-06-22 | 2013-06-20 | 2.9973 | 4.9 | 118.3 | 816.1 | 5.1 | 0.4 | 0.6 | 0 | 6.1 | 0.011 | 0 | 60.2 | 6.8986
交流220kV | 2008-12-19 | 2011-12-21 | 3.0055 | 20.49 | 639.38 | 2102.89 | 7.57 | 1.11 | 0.86 | 0 | 9.54 | 0 | 0.005 | 50 | 3.289
交流220kV | 2009-05-20 | 2012-05-23 | 3.011 | 24.7 | 220.7 | 754 | 4.3 | 0.3 | 0.5 | 0 | 5.1 | 0.005 | 0.03 | 58.2 | 3.4164
220 | 2010-04-14 | 2013-04-18 | 3.0137 | 58.38 | 114.16 | 1069.76 | 3.23 | 0.46 | 0.82 | 0 | 4.51 | 0.011 | 0.093 | 58.9 | 9.3707
交流220kV | 2009-04-24 | 2012-05-04 | 3.0301 | 31 | 308 | 1758 | 4.5 | 1.3 | 0 | 0 | 5.8 | 0.016 | 0.002 | 58 | 5.7078
交流220kV | 2009-07-09 | 2012-07-19 | 3.0301 | 34.02 | 767.76 | 1557.5 | 9.44 | 4 | 1.48 | 0 | 14.92 | 0.006 | 0.001 | 60 | 2.0286
交流220kV | 2010-01-13 | 2013-01-23 | 3.0301 | 43.06 | 205.91 | 920.15 | 5.7 | 0.42 | 1.42 | 0 | 7.54 | 0.005 | 0.009 | 52 | 4.4687
交流220kV | 2008-04-29 | 2011-05-11 | 3.0329 | 9.5 | 409.49 | 865.06 | 5.14 | 0.85 | 1.82 | 0 | 7.81 | 0.01 | 0.001 | 60 | 2.1125
交流220kV | 2010-11-14 | 2013-11-27 | 3.0384 | 3.89 | 420.7 | 1388.29 | 5.36 | 0.67 | 0.74 | 0 | 6.77 | 0.003 | 0.1 | 42 | 3.3
交流220kV | 2010-05-20 | 2013-06-05 | 3.0466 | 25.94 | 253 | 588 | 4.75 | 0.73 | 9.23 | 0 | 14.71 | 0.033 | 0.087 | 51.2 | 2.3241
交流220kV | 2007-04-25 | 2010-05-11 | 3.0466 | 0.69 | 362.17 | 579.68 | 4.99 | 1.04 | 1.65 | 0 | 7.68 | 0.002 | 0.122 | 77.7 | 1.6006
交流220kV | 2008-11-12 | 2011-12-01 | 3.0521 | 38 | 143 | 665 | 2.3 | 0.5 | 0.3 | 0 | 3.1 | 0.003 | 0.014 | 45 | 4.6503
交流220kV | 2008-11-12 | 2011-12-01 | 3.0521 | 54 | 194 | 953 | 3.5 | 1.1 | 0.8 | 0 | 5.4 | 0.003 | 0.002 | 52 | 4.9124
交流220kV | 2008-06-30 | 2011-07-22 | 3.0603 | 34.4 | 406.8 | 1439.3 | 9.9 | 0 | 0.9 | 0 | 10.8 | 0.019 | 0 | 61.4 | 3.5381
交流220kV | 2008-06-30 | 2011-07-22 | 3.0603 | 40.5 | 531.1 | 2328.9 | 13.1 | 0 | 0.7 | 0 | 13.8 | 0.018 | 0 | 42.8 | 4.385
交流220kV | 2010-11-20 | 2013-12-12 | 3.063 | 79.1 | 150.1 | 1178.1 | 6.1 | 0.9 | 1.2 | 0 | 8.2 | 0 | 0 | 0 | 7.8488
交流220kV | 2008-06-02 | 2011-06-27 | 3.0685 | 36.8 | 217.7 | 1362.4 | 3 | 0 | 0 | 0 | 3 | 0.02 | 0 | 48.3 | 6.2582
交流220kV | 2002-03-01 | 2005-03-26 | 3.0712 | 13.25 | 527.19 | 850.94 | 5.16 | 4.07 | 1.74 | 0 | 10.97 | 0.004 | 1.581 | 52.4 | 1.6141
交流220kV | 2008-05-31 | 2011-06-27 | 3.074 | 84.6 | 2574 | 1294.9 | 3 | 0 | 0.6 | 0 | 3.6 | 0.022 | 0 | 55.8 | 0.50307
交流220kV | 2008-12-10 | 2012-01-12 | 3.0904 | 18.67 | 830.23 | 1794.99 | 13.89 | 1.26 | 1.85 | 0 | 17 | 0.01 | 0.126 | 53.1 | 2.162
220 | 2010-03-29 | 2013-05-03 | 3.0986 | 14.8 | 181.26 | 958.93 | 4.25 | 0.49 | 2.32 | 0 | 7.06 | 0.009 | 0.05 | 65.2 | 5.2904
交流220kV | 2009-01-23 | 2012-03-02 | 3.1068 | 280.09 | 119.12 | 320.81 | 11.85 | 0.87 | 2.86 | 0.13 | 15.71 | 0.021 | 0.249 | 53.1 | 2.6932
交流220kV | 2009-01-23 | 2012-03-02 | 3.1068 | 90.24 | 150.67 | 385.66 | 4.82 | 0.52 | 0.79 | 0 | 6.13 | 0.018 | 0.308 | 52.1 | 2.5596
交流220kV | 2007-01-30 | 2010-03-11 | 3.1123 | 18 | 373 | 331 | 13.95 | 1.67 | 1.83 | 0 | 17.45 | 0.001 | 0.001 | 50 | 0.8874
交流220kV | 2008-06-12 | 2011-07-25 | 3.1178 | 14.4 | 110.84 | 164.7 | 4.37 | 0.9 | 0.42 | 0 | 5.69 | 0.005 | 0.001 | 60 | 1.4859
交流220kV | 2009-01-10 | 2012-02-24 | 3.1233 | 55.05 | 195.96 | 769.07 | 14.35 | 1.19 | 3.44 | 0.36 | 19.34 | 0.021 | 0.001 | 61.6 | 3.9246
交流220kV | 2010-11-15 | 2013-12-30 | 3.126 | 3.86 | 90.75 | 660.29 | 1.6 | 0.11 | 0.29 | 0 | 2 | 0 | 0 | 0 | 7.2759
交流220kV | 2010-02-05 | 2013-03-22 | 3.126 | 32.9 | 360.1 | 703.5 | 4.1 | 0.4 | 0.5 | 0.1 | 5.1 | 0.006 | 0.097 | 44 | 1.9536
交流220kV | 2008-06-19 | 2011-08-05 | 3.1288 | 8.06 | 86.65 | 283.91 | 3.31 | 0.41 | 0.23 | 0 | 3.95 | 0.006 | 0.001 | 62 | 3.2765
交流220kV | 2008-10-26 | 2011-12-13 | 3.1315 | 28.4 | 286.8 | 671 | 4 | 0.5 | 0.5 | 0 | 5 | 0 | 0 | 0 | 2.3396
交流220kV | 2008-12-20 | 2012-02-06 | 3.1315 | 4.8 | 226.8 | 359.4 | 9.3 | 0.6 | 1 | 0 | 10.9 | 0.007 | 0.049 | 67 | 1.5847
交流220kV | 2008-11-17 | 2012-01-09 | 3.1452 | 22 | 536 | 1276 | 6.1 | 0.4 | 0.6 | 0 | 7.1 | 0.045 | 0.028 | 61.2 | 2.3806
交流220kV | 2008-04-30 | 2011-06-23 | 3.1479 | 44.6 | 285.2 | 1719 | 7.2 | 0 | 0 | 0 | 7.2 | 0.02 | 0 | 63.2 | 6.0273
交流220kV | 2008-04-30 | 2011-06-23 | 3.1479 | 39.7 | 300.9 | 1458.3 | 7.1 | 0 | 0.7 | 0 | 7.8 | 0.02 | 0 | 53.2 | 4.8465
交流220kV | 2010-04-19 | 2013-06-15 | 3.1589 | 26.37 | 57.1 | 513.44 | 6.64 | 0.52 | 0.69 | 0 | 7.85 | 0 | 0 | 50 | 8.9919
交流220kV | 2010-04-19 | 2013-06-15 | 3.1589 | 26.37 | 57.1 | 513.44 | 6.64 | 0.52 | 0.69 | 0 | 7.85 | 0 | 0 | 55 | 8.9919
交流220kV | 2007-10-31 | 2010-12-29 | 3.1644 | 14.54 | 224.33 | 912.95 | 3.65 | 0.68 | 0.46 | 0 | 4.79 | 0.014 | 0.001 | 53.6 | 4.0697
交流220kV | 2009-10-20 | 2012-12-20 | 3.1699 | 10.11 | 25.53 | 391.01 | 1.64 | 0.12 | 0.48 | 0 | 2.24 | 0 | 0.02 | 49 | 15.3157
交流220kV | 2009-09-19 | 2012-11-19 | 3.1699 | 6.65 | 214.86 | 985.05 | 3.37 | 0.62 | 0.31 | 0 | 4.3 | 0.009 | 0.002 | 62 | 4.5846
220 | 2010-04-27 | 2013-06-28 | 3.1726 | 2.13 | 56.58 | 668.43 | 1.41 | 0.25 | 0.16 | 0 | 1.82 | 0.009 | 0 | 50 | 11.8139
交流220kV | 2008-12-30 | 2012-03-02 | 3.1726 | 26.82 | 581.24 | 1830.41 | 7.68 | 0.96 | 0.65 | 0 | 9.29 | 0.008 | 0.148 | 51.5 | 3.1491
交流220kV | 2008-12-30 | 2012-03-02 | 3.1726 | 15.93 | 546.59 | 2252.99 | 7.99 | 1.19 | 0.77 | 0 | 9.95 | 0.008 | 0.249 | 54.1 | 4.1219
交流220kV | 2008-11-09 | 2012-01-12 | 3.1753 | 26.07 | 832.94 | 2926.88 | 18.99 | 1.54 | 2.25 | 0 | 22.78 | 0.01 | 0.089 | 51.6 | 3.5139
交流220kV | 2006-03-15 | 2009-05-17 | 3.1753 | 2.32 | 221.68 | 1003.72 | 4.47 | 1.35 | 1.1 | 0 | 6.92 | 0.01 | 0.002 | 57.8 | 4.5278
交流220kV | 2007-12-27 | 2011-03-03 | 3.1836 | 33.7 | 1129.6 | 2480.7 | 9.3 | 1.4 | 1.5 | 0 | 12.2 | 0.009 | 0.02 | 53 | 2.1961
交流220kV | 2009-08-11 | 2012-10-18 | 3.189 | 20.96 | 158.82 | 446.47 | 3.38 | 0.71 | 0.61 | 0 | 4.7 | 0.007 | 0.001 | 60 | 2.8112
交流220kV | 2009-08-11 | 2012-10-18 | 3.189 | 20.98 | 190.77 | 485.68 | 4.02 | 0.78 | 1.54 | 0 | 6.34 | 0.007 | 0.001 | 62 | 2.5459
交流220kV | 2008-06-30 | 2011-09-07 | 3.189 | 40 | 165 | 1162 | 9.8 | 1.1 | 8.1 | 0 | 19 | 0.05 | 0.178 | 58 | 7.0424
交流220kV | 2008-12-21 | 2012-03-02 | 3.1973 | 11.57 | 123.14 | 324.13 | 1.95 | 0.28 | 0.24 | 0 | 2.47 | 0.008 | 0.16 | 50.4 | 2.6322
交流220kV | 2009-09-09 | 2012-11-19 | 3.1973 | 15.93 | 193.02 | 1077.22 | 3.59 | 0.74 | 0.88 | 0 | 5.21 | 0.009 | 0.002 | 61 | 5.5809
交流220kV | 2008-12-21 | 2012-03-02 | 3.1973 | 16.76 | 145.4 | 280.13 | 2.3 | 0.3 | 0.28 | 0 | 2.88 | 0.009 | 0.113 | 51.7 | 1.9266
交流220kV | 2009-09-09 | 2012-11-19 | 3.1973 | 12.8 | 157.24 | 945.01 | 2.66 | 0.33 | 0.35 | 0 | 3.34 | 0.011 | 0.003 | 62 | 6.01
220 | 2010-09-16 | 2013-11-27 | 3.2 | 10.04 | 317.19 | 497.26 | 3.13 | 0.37 | 0.41 | 0 | 3.91 | 0.005 | 0.046 | 62.8 | 1.5677
220 | 2010-09-16 | 2013-11-27 | 3.2 | 8.47 | 267.95 | 452.42 | 3.49 | 0.22 | 0.4 | 0 | 4.11 | 0.005 | 0.071 | 62.4 | 1.6884
交流220kV | 2009-05-20 | 2012-08-02 | 3.2055 | 18.5 | 206.7 | 933.9 | 4.3 | 0.4 | 0.6 | 0 | 5.3 | 0 | 0 | 0 | 4.5181
交流220kV | 2010-03-26 | 2013-06-08 | 3.2055 | 27.8 | 383.17 | 798.23 | 4.16 | 0.3 | 0.68 | 0 | 5.14 | 0 | 0 | 0 | 2.0832
交流220kV | 2010-12-29 | 2014-03-13 | 3.2055 | 15.67 | 510.76 | 1962.6 | 5.04 | 0.61 | 0.74 | 0 | 6.39 | 0.01 | 0.001 | 57.7 | 3.8425
交流220kV | 2008-12-12 | 2012-03-02 | 3.2219 | 135.29 | 217.98 | 685.38 | 3.67 | 0.43 | 0.62 | 0 | 4.72 | 0.01 | 0.284 | 51.7 | 3.1442
交流220kV | 2008-09-27 | 2011-12-20 | 3.2301 | 19.5 | 236.1 | 1093.6 | 4.1 | 0.6 | 0.6 | 0 | 5.3 | 0 | 0 | 0 | 4.6319
交流220kV | 2008-09-27 | 2011-12-20 | 3.2301 | 14.2 | 233.5 | 1143.8 | 4.2 | 0.9 | 0.6 | 0 | 5.7 | 0 | 0 | 0 | 4.8985
交流220kV | 2010-12-22 | 2014-03-15 | 3.2301 | 37.19 | 235.67 | 1016.57 | 3.69 | 0.62 | 0.7 | 0 | 5.01 | 0.005 | 0.069 | 68.5 | 4.3135
交流220kV | 2010-12-22 | 2014-03-15 | 3.2301 | 33.07 | 181.34 | 710.55 | 3.18 | 0.34 | 0.91 | 0 | 4.43 | 0.004 | 0.094 | 58.5 | 3.9183
交流220kV | 2009-11-26 | 2013-02-22 | 3.2438 | 29.11 | 487.87 | 718.72 | 5.87 | 0.53 | 0.86 | 0 | 7.26 | 0.001 | 0.001 | 52 | 1.4732
交流220kV | 2008-11-25 | 2012-02-23 | 3.2466 | 3.94 | 160.33 | 270.19 | 3.1 | 0.6 | 0.25 | 0 | 3.95 | 0.007 | 0.11 | 57 | 1.6852
交流220kV | 2009-09-20 | 2012-12-20 | 3.2521 | 10.85 | 149.23 | 294.74 | 3.85 | 0.57 | 0.44 | 0 | 4.86 | 0 | 0 | 0 | 1.9751
交流220kV | 2008-11-21 | 2012-02-22 | 3.2548 | 17.78 | 423.48 | 492.73 | 20.14 | 0.68 | 2.29 | 0 | 23.11 | 0.006 | 0.025 | 65.6 | 1.1635
交流220kV | 2009-09-05 | 2012-12-10 | 3.2658 | 4.05 | 358.65 | 1038.39 | 3.65 | 0 | 0 | 0 | 3.65 | 0 | 0 | 0 | 2.8953
交流220kV | 2010-12-13 | 2014-03-19 | 3.2658 | 16 | 174 | 582 | 3.48 | 1.2 | 1 | 0 | 5.68 | 0.001 | 0.051 | 50 | 3.3448
交流220kV | 2009-11-20 | 2013-03-02 | 3.2822 | 6.19 | 154.91 | 425.16 | 15.99 | 3.57 | 3.66 | 0 | 23.22 | 0.005 | 0.29 | 49.2 | 2.7446
交流220kV | 2009-11-20 | 2013-03-02 | 3.2822 | 4.18 | 280.84 | 2162.72 | 9.36 | 4.31 | 4.27 | 0 | 17.94 | 0.008 | 0.23 | 46 | 7.7009
交流220kV | 2008-11-09 | 2012-02-22 | 3.2877 | 7 | 264 | 138 | 13.74 | 1.58 | 2.75 | 0 | 18.07 | 0.001 | 0.001 | 57 | 0.52273
交流220kV | 2008-09-12 | 2011-12-27 | 3.2904 | 63 | 111 | 451 | 4 | 0 | 0 | 0 | 4 | 0 | 0 | 0 | 4.0631
交流220kV | 2008-11-29 | 2012-03-14 | 3.2904 | 64.54 | 267.31 | 520.3 | 4.05 | 0.83 | 0.66 | 0 | 5.54 | 0.029 | 0.002 | 52.5 | 1.9464
交流220kV | 2008-11-08 | 2012-02-23 | 3.2932 | 12.21 | 413.99 | 645.47 | 7.49 | 1.01 | 1.17 | 0 | 9.67 | 0.004 | 0.08 | 56 | 1.5591
交流220kV | 2008-12-29 | 2012-04-16 | 3.2986 | 15 | 249 | 506 | 7.25 | 2.17 | 1.17 | 0.23 | 10.82 | 0.003 | 0.053 | 60 | 2.0321
交流220kV | 2008-11-12 | 2012-02-29 | 3.2986 | 99.8 | 228.07 | 274.42 | 7.53 | 0.74 | 1.88 | 0 | 10.15 | 0.016 | 0.025 | 55 | 1.2032
交流220kV | 2008-11-12 | 2012-02-29 | 3.2986 | 97.58 | 174.94 | 175.22 | 5.63 | 0.49 | 1.12 | 0 | 7.24 | 0.012 | 0.057 | 54.6 | 1.0016
交流220kV | 2008-10-31 | 2012-02-20 | 3.3068 | 39.3 | 596.3 | 1113.1 | 3.8 | 0.4 | 0.7 | 0 | 4.9 | 6.98 | 0.072 | 60.8 | 1.8667
交流220kV | 2008-09-23 | 2012-01-16 | 3.3151 | 25.51 | 832.01 | 1526.56 | 19.51 | 2.1 | 2.55 | 0 | 24.16 | 0.011 | 0.005 | 54 | 1.8348
交流220kV | 2010-01-28 | 2013-05-24 | 3.3205 | 33.07 | 61.82 | 297.68 | 2.19 | 0.4 | 0.41 | 0 | 3 | 0.06 | 0.001 | 60 | 4.8153
交流220kV | 2010-01-28 | 2013-05-24 | 3.3205 | 28.87 | 222.31 | 811.51 | 3.83 | 0.78 | 0.66 | 0 | 5.27 | 0.05 | 0.001 | 59 | 3.6504
220 | 2008-12-11 | 2012-04-11 | 3.3342 | 74.4 | 438.12 | 571.66 | 4.85 | 1.65 | 1.89 | 0 | 8.39 | 0.02 | 0.001 | 60 | 1.3048
交流220kV | 2010-04-06 | 2013-08-05 | 3.3342 | 38 | 89 | 1614 | 2.1 | 0.89 | 0.6 | 0 | 3.59 | 0.025 | 0.469 | 37 | 18.1348
交流220kV | 2008-02-04 | 2011-06-14 | 3.3589 | 42.9 | 538.5 | 3224.8 | 18.1 | 0 | 1.3 | 0 | 19.4 | 0.01 | 0 | 54.1 | 5.9885
交流220kV | 2009-10-25 | 2013-03-05 | 3.3616 | 14.3 | 190.2 | 1206.3 | 4.1 | 0.5 | 0.9 | 0 | 5.5 | 0.006 | 0.274 | 67.7 | 6.3423
交流220kV | 2008-06-18 | 2011-10-28 | 3.3616 | 20 | 416 | 879 | 4.7 | 0.4 | 0.6 | 0 | 5.7 | 0.004 | 0.004 | 51 | 2.113
交流220kV | 2008-06-05 | 2011-10-18 | 3.3699 | 9.93 | 414.68 | 2052.75 | 4.91 | 1.32 | 0.72 | 0 | 6.95 | 0 | 0 | 0 | 4.9502
交流220kV | 2010-01-16 | 2013-05-31 | 3.3726 | 16.07 | 363.88 | 628.42 | 5.42 | 1.31 | 0.85 | 0 | 7.58 | 0.044 | 0.061 | 50 | 1.727
交流220kV | 2010-06-02 | 2013-10-16 | 3.3753 | 8.03 | 220.69 | 548.08 | 2.86 | 0.23 | 0.36 | 0 | 3.45 | 0.006 | 0.054 | 62 | 2.4835
交流220kV | 2010-06-02 | 2013-10-16 | 3.3753 | 3.14 | 103.89 | 447.06 | 1.99 | 0.28 | 0.32 | 0 | 2.59 | 0.007 | 0.11 | 64 | 4.3032
220 | 2009-12-16 | 2013-05-03 | 3.3808 | 16.9 | 349.38 | 1332.64 | 4.73 | 0.64 | 0.84 | 0 | 6.21 | 0.012 | 0.029 | 64.8 | 3.8143
交流220kV | 2008-12-26 | 2012-05-16 | 3.389 | 23 | 288.8 | 831.2 | 4.3 | 0.7 | 0.5 | 0 | 5.5 | 0.006 | 0 | 78.1 | 2.8781
交流220kV | 2008-12-26 | 2012-05-16 | 3.389 | 10.6 | 283.5 | 924.9 | 4.9 | 0.4 | 0.5 | 0 | 5.8 | 0.003 | 0 | 73.8 | 3.2624
220 | 2009-10-15 | 2013-03-07 | 3.3945 | 15.22 | 200.98 | 776.65 | 3.75 | 0.5 | 0.41 | 0 | 4.66 | 0.011 | 0.074 | 60 | 3.8643
220 | 2009-10-15 | 2013-03-07 | 3.3945 | 22.6 | 195.94 | 877.37 | 3.42 | 0.43 | 0.48 | 0 | 4.33 | 0.008 | 0.085 | 57 | 4.4777
交流220kV | 2009-01-15 | 2012-06-07 | 3.3945 | 23.26 | 249.55 | 1216 | 3.26 | 0 | 0 | 0 | 3.26 | 0.01 | 0.153 | 0 | 4.8728
交流220kV | 2010-10-15 | 2014-03-08 | 3.3973 | 8 | 36 | 525 | 1.9 | 0.13 | 6.12 | 0.05 | 8.2 | 0.001 | 0.54 | 50 | 14.5833
交流220kV | 2009-05-26 | 2012-10-17 | 3.3973 | 14.79 | 235.01 | 542.77 | 4.09 | 0.63 | 0.6 | 0 | 5.32 | 0.006 | 0.001 | 60 | 2.3096
交流220kV | 2008-10-20 | 2012-03-14 | 3.4 | 18 | 565 | 206 | 10.87 | 0.9 | 1.67 | 0 | 13.44 | 0.027 | 0.025 | 53.6 | 0.3646
交流220kV | 2009-05-26 | 2012-10-18 | 3.4 | 23.33 | 418.27 | 711.97 | 3.97 | 0.43 | 0.47 | 0 | 4.87 | 0.009 | 0.002 | 60 | 1.7022
交流220kV | 2009-05-26 | 2012-10-18 | 3.4 | 17.05 | 306.89 | 669.36 | 3.64 | 0.38 | 0.49 | 0 | 4.51 | 0.01 | 0.003 | 61 | 2.1811
交流220kV | 2010-10-13 | 2014-03-07 | 3.4 | 14 | 239 | 1100 | 3.12 | 0.68 | 0.37 | 0 | 4.17 | 0.022 | 0.365 | 49 | 4.6025
交流220kV | 2010-10-13 | 2014-03-07 | 3.4 | 27 | 342 | 915 | 3.08 | 0.71 | 0.34 | 0 | 4.13 | 0.022 | 0.412 | 57 | 2.6754
交流220kV | 2008-04-25 | 2011-09-20 | 3.4055 | 3.97 | 71.77 | 489.1 | 4.04 | 0.58 | 0.42 | 0 | 5.04 | 0.005 | 0.001 | 58 | 6.8148
交流220kV | 2009-07-10 | 2012-12-05 | 3.4082 | 8.8 | 55.5 | 574.4 | 2.9 | 0.5 | 0.6 | 0 | 4 | 0 | 0 | 0 | 10.3495
交流220kV | 2009-08-04 | 2012-12-31 | 3.411 | 15 | 158 | 1772 | 4.58 | 0.83 | 0.88 | 0 | 6.29 | 0.048 | 0.113 | 69.3 | 11.2152
交流220kV | 2010-10-27 | 2014-03-27 | 3.4164 | 28.35 | 1033.5 | 1967.05 | 10.29 | 1.12 | 3.45 | 0 | 14.86 | 0.005 | 0.03 | 46 | 1.9033
交流220kV | 2010-04-28 | 2013-09-29 | 3.4247 | 14.6 | 643.24 | 2075.74 | 4.46 | 0.66 | 0.55 | 0 | 5.67 | 0.013 | 0.001 | 57.5 | 3.227
交流220kV | 2009-06-15 | 2012-11-16 | 3.4247 | 38.13 | 306.72 | 640.9 | 6.31 | 0.52 | 1.01 | 0 | 7.84 | 0.002 | 0.005 | 60.3 | 2.0895
交流220kV | 2008-10-26 | 2012-03-30 | 3.4274 | 27.1 | 320.6 | 794.7 | 5.3 | 0.5 | 0.6 | 0 | 6.4 | 0.007 | 0 | 56 | 2.4788
交流220kV | 2008-12-19 | 2012-05-23 | 3.4274 | 75.68 | 458.67 | 672.34 | 13.31 | 0.81 | 0.88 | 0 | 15 | 0.006 | 0.001 | 60 | 1.4658
交流220kV | 2009-07-17 | 2012-12-19 | 3.4274 | 9 | 55 | 254 | 0.2 | 0.2 | 0.1 | 0 | 0.5 | 0.025 | 0.21 | 56 | 4.6182
交流220kV | 2008-10-31 | 2012-04-06 | 3.4329 | 18 | 188 | 667 | 4 | 0.7 | 0.9 | 0.1 | 5.7 | 0.003 | 0.092 | 56 | 3.5479
220 | 2008-10-31 | 2012-04-10 | 3.4438 | 10 | 117 | 38 | 0.8 | 0.1 | 0 | 0 | 0.9 | 0.007 | 0.067 | 54 | 0.32479
交流220kV | 2010-10-15 | 2014-03-25 | 3.4438 | 9 | 311 | 1646 | 4.89 | 0.64 | 0.67 | 0.08 | 6.28 | 0.001 | 0.07 | 50 | 5.2926
交流220kV | 2007-10-31 | 2011-04-12 | 3.4493 | 20.42 | 238.96 | 946.33 | 3.84 | 0.51 | 0.53 | 0 | 4.88 | 0.022 | 0.002 | 53.8 | 3.9602
交流220kV | 2010-06-23 | 2013-12-05 | 3.4548 | 6.3 | 105 | 409.9 | 4.2 | 0.3 | 0.4 | 0 | 4.9 | 0 | 0 | 0 | 3.9038
交流220kV | 2010-06-22 | 2013-12-05 | 3.4575 | 4.9 | 164.5 | 527.7 | 5.4 | 0.4 | 0.6 | 0 | 6.4 | 0 | 0 | 0 | 3.2079
交流220kV | 2009-06-15 | 2012-11-28 | 3.4575 | 31.06 | 305.98 | 700.94 | 5.81 | 0.58 | 1.12 | 0 | 7.51 | 0.007 | 0.005 | 55.8 | 2.2908
交流220kV | 2009-06-21 | 2012-12-05 | 3.4603 | 8.2 | 278.1 | 841.1 | 4.3 | 0.4 | 0.4 | 0 | 5.1 | 0 | 0 | 0 | 3.0245
交流220kV | 2009-09-19 | 2013-03-05 | 3.4603 | 11.8 | 201.7 | 989.6 | 4 | 0.6 | 0.9 | 0 | 5.5 | 0.019 | 0.345 | 56.3 | 4.9063
交流220kV | 2008-06-30 | 2011-12-16 | 3.463 | 27.7 | 335.9 | 1007.5 | 5 | 0.4 | 0.7 | 0 | 6.1 | 0 | 0 | 0 | 2.9994
交流220kV | 2008-06-30 | 2011-12-16 | 3.463 | 26.4 | 312.8 | 729.4 | 4.3 | 0.3 | 0.6 | 0 | 5.2 | 0 | 0 | 0 | 2.3318
交流220kV | 2009-09-18 | 2013-03-05 | 3.463 | 17 | 220.9 | 1405.8 | 16.3 | 0.6 | 2.2 | 0 | 19.1 | 0.025 | 0.658 | 56.8 | 6.364
交流220kV | 2009-09-18 | 2013-03-05 | 3.463 | 7.9 | 181.7 | 789.2 | 10.5 | 0.6 | 0.9 | 0 | 12 | 0.018 | 0.272 | 62.1 | 4.3434
交流220kV | 2008-06-26 | 2011-12-13 | 3.4658 | 5.59 | 408.85 | 938.02 | 7.22 | 2.57 | 0 | 0 | 9.79 | 0.01 | 0 | 0 | 2.2943
交流220kV | 2007-12-25 | 2011-06-13 | 3.4685 | 76.68 | 484.55 | 2930.94 | 8.5 | 4.85 | 1.59 | 0 | 14.94 | 0.003 | 0.02 | 51 | 6.0488
交流220kV | 2009-11-28 | 2013-05-17 | 3.4685 | 12 | 402 | 668 | 5.2 | 1.1 | 5.2 | 0 | 11.5 | 0.002 | 0.167 | 58 | 1.6617
交流220kV | 2007-12-27 | 2011-06-16 | 3.4712 | 17.9 | 144.3 | 802.1 | 2.6 | 0 | 0 | 0 | 2.6 | 0.01 | 0 | 53.2 | 5.5586
交流220kV | 2008-06-28 | 2011-12-17 | 3.4712 | 22.97 | 488.32 | 3076.42 | 12.13 | 1.83 | 1 | 0 | 14.96 | 0 | 0 | 0 | 6.3
交流220kV | 2008-12-21 | 2012-06-13 | 3.4795 | 17.7 | 168 | 202.9 | 2.6 | 0.1 | 0.3 | 0.1 | 3.1 | 0.012 | 0.095 | 56.4 | 1.2077
交流220kV | 2008-12-21 | 2012-06-13 | 3.4795 | 15 | 170.4 | 197.2 | 2.4 | 0.1 | 0.2 | 0.1 | 2.8 | 0.012 | 0.106 | 56.3 | 1.1573
交流220kV | 2008-03-28 | 2011-09-20 | 3.4822 | 3.21 | 75.85 | 463.09 | 3.44 | 0.65 | 0.36 | 0 | 4.45 | 0.003 | 0.001 | 60 | 6.1053
交流220kV | 2006-09-22 | 2010-03-18 | 3.4877 | 9.74 | 169.49 | 593.99 | 1.86 | 0.28 | 0.21 | 0 | 2.35 | 0.01 | 0.12 | 48 | 3.5046
交流220kV | 2006-09-22 | 2010-03-18 | 3.4877 | 8.82 | 141.24 | 440.7 | 2.02 | 0.22 | 1.06 | 0 | 3.3 | 0.013 | 0.207 | 52 | 3.1202
交流220kV | 2009-06-29 | 2012-12-24 | 3.4904 | 11.68 | 157.07 | 651.01 | 2.98 | 0.37 | 0.31 | 0 | 3.66 | 0.011 | 0.003 | 60 | 4.1447
交流220kV | 2009-06-29 | 2012-12-24 | 3.4904 | 12.82 | 122.26 | 640.61 | 2.59 | 0.31 | 0.27 | 0 | 3.17 | 0.012 | 0.002 | 61 | 5.2397
交流220kV | 2009-06-22 | 2012-12-19 | 3.4959 | 5 | 54 | 298 | 0.1 | 0.2 | 0.1 | 0 | 0.4 | 0.031 | 0.21 | 55 | 5.5185
交流220kV | 2009-04-19 | 2012-10-17 | 3.4986 | 13.49 | 270.28 | 842.48 | 4.32 | 0.82 | 0.73 | 0 | 5.87 | 0.008 | 0.004 | 60 | 3.1171
交流220kV | 2008-09-27 | 2012-03-28 | 3.5014 | 14.3 | 238.5 | 1115 | 4.3 | 0.7 | 0.6 | 0 | 5.6 | 0.016 | 0 | 63.9 | 4.6751
交流220kV | 2008-09-27 | 2012-03-28 | 3.5014 | 13.2 | 240.5 | 1098.7 | 4.3 | 0.9 | 0.6 | 0 | 5.8 | 0.016 | 0 | 70.9 | 4.5684
交流220kV | 2008-12-19 | 2012-06-21 | 3.5068 | 18.45 | 642.72 | 2889.22 | 9.2 | 1.4 | 0.23 | 0 | 10.83 | 0 | 0 | 0 | 4.4953
交流220kV | 2010-06-30 | 2013-12-31 | 3.5068 | 4.31 | 118.66 | 640.99 | 2.19 | 0.29 | 0 | 0 | 2.48 | 0 | 0 | 0 | 5.4019
交流220kV | 2009-08-06 | 2013-02-06 | 3.5068 | 5.2 | 162 | 559.2 | 2.3 | 0.5 | 0.4 | 0 | 3.2 | 0.009 | 0.134 | 62 | 3.4519
交流220kV | 2007-09-11 | 2011-03-15 | 3.5096 | 33 | 85 | 544 | 7.5 | 2.1 | 3.7 | 0.2 | 13.5 | 0.005 | 0.001 | 53 | 6.4
交流220kV | 2009-09-13 | 2013-03-21 | 3.5205 | 58.08 | 700.85 | 1485.25 | 47.97 | 16.47 | 12.49 | 0.08 | 77.01 | 0.018 | 0.196 | 50.4 | 2.1192
交流220kV | 2010-08-26 | 2014-03-04 | 3.5233 | 20.1 | 165.5 | 2325.5 | 6.5 | 0.6 | 1.9 | 0 | 9 | 0.006 | 0.001 | 47.6 | 14.0514
交流220kV | 2010-06-15 | 2013-12-23 | 3.526 | 8.23 | 413.27 | 329.86 | 4.81 | 0.62 | 0.73 | 0 | 6.16 | 0.012 | 0.087 | 60.1 | 0.79817
交流220kV | 2008-05-31 | 2011-12-13 | 3.537 | 9.07 | 386.75 | 613.86 | 4.98 | 0.38 | 1.31 | 0 | 6.67 | 0.002 | 0.02 | 49 | 1.5872
交流220kV | 2008-05-31 | 2011-12-13 | 3.537 | 5.55 | 471.98 | 846.44 | 6.21 | 0.56 | 2.01 | 0 | 8.78 | 0.003 | 0.02 | 48 | 1.7934
交流220kV | 2008-06-27 | 2012-01-09 | 3.537 | 175.25 | 672.72 | 1122.49 | 5.59 | 1.16 | 1.97 | 0 | 8.72 | 0.007 | 0.008 | 52 | 1.6686
交流220kV | 2010-03-29 | 2013-10-12 | 3.5425 | 4.38 | 129.33 | 633.98 | 2.62 | 0.26 | 0.23 | 0 | 3.11 | 0.006 | 0.031 | 63.2 | 4.902
交流220kV | 2010-03-29 | 2013-10-12 | 3.5425 | 3.62 | 142.77 | 669.64 | 3 | 0.24 | 0.26 | 0 | 3.5 | 0.007 | 0.034 | 69.2 | 4.6903
交流220kV | 2008-06-05 | 2011-12-22 | 3.5479 | 9.89 | 401.33 | 1857.47 | 4.74 | 1.16 | 0.64 | 0 | 6.54 | 0 | 0 | 0 | 4.6283
交流220kV | 2008-06-02 | 2011-12-20 | 3.5507 | 47.5 | 226.4 | 1042.6 | 3.9 | 1 | 0.7 | 0 | 5.6 | 0 | 0 | 0 | 4.6051
交流220kV | 2009-08-17 | 2013-03-05 | 3.5507 | 9.2 | 232.5 | 1048.3 | 3.2 | 0.3 | 0.6 | 0 | 4.1 | 0.019 | 0.363 | 60.2 | 4.5088
交流220kV | 2009-08-17 | 2013-03-05 | 3.5507 | 9.9 | 330 | 1739 | 4.5 | 0.5 | 0.9 | 0 | 5.9 | 0.02 | 0.166 | 60.2 | 5.2697
交流220kV | 2009-08-18 | 2013-03-06 | 3.5507 | 27 | 407 | 573 | 11.6 | 0.72 | 1.86 | 0 | 14.18 | 0.011 | 0.093 | 52.8 | 1.4079
交流220kV | 2008-05-31 | 2011-12-20 | 3.5562 | 58.1 | 233.9 | 1014.6 | 3.8 | 0.7 | 0.6 | 0 | 5.1 | 0 | 0 | 0 | 4.3378
交流220kV | 2010-06-04 | 2013-12-23 | 3.5562 | 7.03 | 308.09 | 587.39 | 4.02 | 0.31 | 0.36 | 0 | 4.69 | 0.012 | 0.087 | 61.2 | 1.9066
交流220kV | 2007-12-21 | 2011-07-12 | 3.5589 | 143.2 | 960.6 | 4076.8 | 11.8 | 2.9 | 1.8 | 0 | 16.5 | 0 | 0 | 0 | 4.244
交流220kV | 2008-06-26 | 2012-01-16 | 3.5589 | 11.67 | 402.57 | 271.16 | 26.7 | 0.89 | 1.98 | 0 | 29.57 | 0.01 | 0.005 | 50.8 | 0.67357
交流220kV | 2009-12-17 | 2013-07-12 | 3.5699 | 5.2 | 83.2 | 627.3 | 2.7 | 0 | 0 | 0 | 2.7 | 0.034 | 1.9 | 52 | 7.5397
交流220kV | 2010-05-30 | 2013-12-23 | 3.5699 | 6.31 | 268.13 | 1034.28 | 3.89 | 0.52 | 0 | 0 | 4.41 | 0.011 | 0.067 | 59.3 | 3.8574
交流220kV | 2006-06-23 | 2010-01-18 | 3.5753 | 30 | 254 | 2013 | 11.8 | 0.8 | 1.3 | 0 | 13.9 | 0.01 | 0.001 | 49 | 7.9252
交流220kV | 2008-05-23 | 2011-12-20 | 3.5781 | 13.7 | 330.3 | 1017.7 | 5.9 | 0.6 | 1.6 | 0 | 8.1 | 0 | 0 | 0 | 3.0811
交流220kV | 2008-05-08 | 2011-12-13 | 3.6 | 3992.9 | 624.71 | 2094.58 | 139.6 | 1.57 | 14.61 | 0 | 155.78 | 0.021 | 0.001 | 64 | 3.3529
交流220kV | 2009-11-18 | 2013-06-26 | 3.6055 | 5.48 | 50.62 | 168.59 | 0.88 | 0 | 0 | 0 | 0.88 | 0.025 | 0.06 | 60.4 | 3.3305
交流220kV | 2008-08-04 | 2012-03-16 | 3.6164 | 25.15 | 186.45 | 635.87 | 3.8 | 0.85 | 1.21 | 0 | 5.86 | 0.005 | 0.001 | 55 | 3.4104
交流220kV | 2008-04-30 | 2011-12-16 | 3.6301 | 24.6 | 220.1 | 1055.5 | 3.5 | 0.4 | 0.7 | 0 | 4.6 | 0 | 0 | 0 | 4.7955
交流220kV | 2008-04-30 | 2011-12-16 | 3.6301 | 34.1 | 221.6 | 1305.9 | 3.8 | 0.4 | 1.1 | 0 | 5.3 | 0 | 0 | 0 | 5.8931
交流220kV | 2009-07-03 | 2013-02-18 | 3.6329 | 9 | 160 | 972.4 | 2.9 | 0.5 | 0.8 | 0 | 4.2 | 0.009 | 0.53 | 65.5 | 6.0775
交流220kV | 2008-10-20 | 2012-06-08 | 3.6356 | 18.55 | 488.41 | 1208.89 | 7.13 | 0.41 | 1.86 | 0 | 9.4 | 0.001 | 0.038 | 0 | 2.4752
220 | 2009-05-06 | 2012-12-24 | 3.6384 | 27.84 | 230.17 | 770.74 | 3.85 | 0.26 | 0.46 | 0 | 4.57 | 0.01 | 0.216 | 52 | 3.3486
220 | 2009-05-06 | 2012-12-24 | 3.6384 | 33.74 | 191.64 | 647.5 | 4.22 | 0.87 | 0.54 | 0 | 5.63 | 0.011 | 0.179 | 53 | 3.3787
交流220kV | 2009-10-20 | 2013-06-09 | 3.6384 | 10 | 26.2 | 422 | 1.8 | 0.2 | 0.5 | 0 | 2.5 | 0 | 0 | 0 | 16.1069
交流220kV | 2007-10-27 | 2011-06-17 | 3.6411 | 19.4 | 202.9 | 334.9 | 3.5 | 0.4 | 0.5 | 0 | 4.4 | 0 | 0 | 0 | 1.6506
交流220kV | 2007-10-30 | 2011-06-20 | 3.6411 | 6 | 163 | 527 | 6.6 | 0 | 0 | 0 | 6.6 | 0.01 | 0 | 0 | 3.2331
交流220kV | 2008-05-08 | 2011-12-30 | 3.6466 | 4802.78 | 753.05 | 2472.04 | 154.2 | 1.74 | 16.27 | 0 | 172.21 | 0.021 | 0.001 | 52.6 | 3.2827
交流220kV | 2008-01-28 | 2011-09-22 | 3.6521 | 33.9 | 825.9 | 2980.4 | 6.4 | 1.1 | 1.1 | 0 | 8.6 | 0.006 | 0.05 | 56.5 | 3.6087
交流220kV | 2008-01-28 | 2011-09-22 | 3.6521 | 18.7 | 580.1 | 1467 | 5.5 | 1 | 1 | 0 | 7.5 | 0.006 | 0.02 | 55.8 | 2.5289
交流220kV | 2008-01-28 | 2011-09-22 | 3.6521 | 3.4 | 825.9 | 2980.4 | 6.4 | 1.1 | 1.2 | 0 | 8.7 | 0.006 | 0.05 | 56.5 | 3.6087
交流220kV | 2008-01-28 | 2011-09-22 | 3.6521 | 18.6 | 580.1 | 1467 | 5.4 | 1 | 1 | 0 | 7.4 | 0.006 | 0.02 | 55.8 | 2.5289
交流220kV | 2009-07-05 | 2013-02-28 | 3.6548 | 4.4 | 138.1 | 455.3 | 2 | 0.1 | 0.2 | 0 | 2.3 | 0.017 | 0.107 | 59.2 | 3.2969
交流220kV | 2006-07-05 | 2010-03-03 | 3.663 | 9.09 | 332.87 | 694.58 | 8.47 | 1.88 | 6.16 | 0 | 16.51 | 0.016 | 0.629 | 44 | 2.0866
交流220kV | 2008-05-08 | 2012-01-06 | 3.6658 | 4710 | 753.8 | 2349.75 | 150.7 | 1.72 | 16.24 | 0 | 168.66 | 0.021 | 0.001 | 66.7 | 3.1172
交流220kV | 2009-07-02 | 2013-03-02 | 3.6685 | 21.56 | 266.29 | 2200.11 | 10.88 | 7.13 | 6.59 | 0 | 24.6 | 0.003 | 0.09 | 56.8 | 8.2621
交流220kV | 2008-07-15 | 2012-03-15 | 3.6685 | 27.55 | 321.83 | 559.98 | 4.18 | 0.42 | 0.52 | 0 | 5.12 | 0.008 | 0.074 | 51.5 | 1.74
交流220kV | 2008-07-15 | 2012-03-15 | 3.6685 | 40.82 | 413.64 | 581.85 | 5.37 | 0.74 | 0.77 | 0 | 6.88 | 0.008 | 0.116 | 52.2 | 1.4067
交流220kV | 2008-09-22 | 2012-05-24 | 3.6712 | 8.36 | 1090.13 | 1939.27 | 10.9 | 0.75 | 0 | 0 | 11.65 | 0.007 | 0.13 | 53 | 1.7789
交流220kV | 2010-07-23 | 2014-03-24 | 3.6712 | 146 | 206 | 709 | 20.13 | 2.73 | 6.89 | 0.09 | 29.84 | 0.001 | 0.07 | 50 | 3.4417
交流220kV | 2009-01-19 | 2012-09-20 | 3.6712 | 13.44 | 535.79 | 1959.7 | 8.15 | 0.51 | 1.4 | 0 | 10.06 | 0.011 | 0.003 | 59 | 3.6576
交流220kV | 2009-01-19 | 2012-09-20 | 3.6712 | 7.61 | 410.86 | 1659.59 | 19.66 | 1.05 | 1.87 | 0 | 22.58 | 0.008 | 0.002 | 60 | 4.0393
交流220kV | 2008-05-08 | 2012-01-10 | 3.6767 | 4393.75 | 721.79 | 2308.65 | 146.39 | 1.72 | 15.82 | 0 | 163.93 | 0.021 | 0.001 | 57.6 | 3.1985
220 | 2009-07-17 | 2013-03-21 | 3.6795 | 67.65 | 180.39 | 811.77 | 6.2 | 0.9 | 1.34 | 0 | 8.44 | 0.01 | 0.138 | 58 | 4.5001
220 | 2008-12-19 | 2012-08-28 | 3.6932 | 24.49 | 348.46 | 1827.39 | 21.62 | 14.74 | 5.97 | 0 | 42.33 | 0.013 | 0.389 | 60 | 5.2442
交流220kV | 2007-12-30 | 2011-09-10 | 3.6986 | 26.3 | 625.1 | 5250.8 | 6.8 | 2 | 0 | 0 | 8.8 | 0 | 0 | 0 | 8.3999
交流220kV | 2008-07-03 | 2012-03-14 | 3.6986 | 16 | 203 | 713 | 6.48 | 1.46 | 1.11 | 0 | 9.05 | 0.02 | 0.062 | 53.6 | 3.5123
交流220kV | 2008-07-09 | 2012-03-21 | 3.7014 | 73.12 | 297.47 | 709.5 | 6.08 | 0.68 | 1.07 | 0 | 7.83 | 0.004 | 0.001 | 55.3 | 2.3851
交流220kV | 2008-07-09 | 2012-03-22 | 3.7041 | 73.12 | 297.47 | 709.05 | 6.08 | 0.68 | 1.07 | 0 | 7.83 | 0.004 | 0.001 | 55.3 | 2.3836
交流220kV | 2009-09-20 | 2013-06-06 | 3.7123 | 15.94 | 319.49 | 730.13 | 4.79 | 0.7 | 0.49 | 0 | 5.98 | 0 | 0 | 0 | 2.2853
交流220kV | 2008-09-12 | 2012-05-31 | 3.7178 | 56 | 86 | 394 | 4.2 | 0 | 0.49 | 0 | 4.69 | 0.05 | 0.292 | 52 | 4.5814
交流220kV | 2009-06-14 | 2013-03-02 | 3.7178 | 9.83 | 184.14 | 1099.38 | 11.19 | 3.05 | 3.14 | 0 | 17.38 | 0.007 | 0.1 | 46.4 | 5.9703
交流220kV | 2009-06-14 | 2013-03-02 | 3.7178 | 15.31 | 255.16 | 770.37 | 8.27 | 4.23 | 4.19 | 0 | 16.69 | 0.008 | 0.13 | 47.2 | 3.0192
交流220kV | 2008-06-30 | 2012-03-20 | 3.7233 | 62.78 | 352.84 | 705.48 | 4.64 | 0.38 | 0.66 | 0 | 5.68 | 0.007 | 0.068 | 62.7 | 1.9994
交流220kV | 2009-04-10 | 2012-12-31 | 3.7288 | 12 | 498 | 1853 | 10.1 | 0.9 | 1.5 | 0 | 12.5 | 0.039 | 0.097 | 54 | 3.7209
220 | 2009-07-15 | 2013-04-07 | 3.7315 | 18.05 | 339.31 | 918.64 | 3.99 | 0.55 | 0.49 | 0 | 5.03 | 0.006 | 0.06 | 62.5 | 2.7074
220 | 2009-07-15 | 2013-04-07 | 3.7315 | 27.48 | 318.35 | 591.69 | 4.74 | 0.33 | 0.49 | 0 | 5.56 | 0.009 | 0.054 | 61.2 | 1.8586
交流220kV | 2008-05-30 | 2012-02-22 | 3.7342 | 20 | 229 | 302 | 32.71 | 1.21 | 3.61 | 0 | 37.53 | 0.001 | 0.001 | 55.3 | 1.3188
交流220kV | 2008-06-21 | 2012-03-15 | 3.7342 | 24.5 | 276.6 | 1266.8 | 4.7 | 0.6 | 1.1 | 0.1 | 6.5 | 0.02 | 0.13 | 56 | 4.5799
交流220kV | 2008-06-21 | 2012-03-16 | 3.737 | 13.4 | 321.3 | 1613.4 | 4.3 | 0.4 | 0.9 | 0 | 5.6 | 0.01 | 0.1 | 55.2 | 5.0215
交流220kV | 2009-09-05 | 2013-06-03 | 3.7452 | 10.9 | 514.6 | 1284.1 | 5.7 | 0 | 0 | 0 | 5.7 | 0.017 | 0.227 | 0 | 2.4953
交流220kV | 2008-06-30 | 2012-03-28 | 3.7452 | 27.7 | 364 | 779.7 | 6.2 | 0.5 | 0.8 | 0 | 7.5 | 0.011 | 0 | 63.3 | 2.142
交流220kV | 2008-06-30 | 2012-03-28 | 3.7452 | 25.2 | 383 | 1073.8 | 6.4 | 0.5 | 0.8 | 0 | 7.7 | 0.011 | 0 | 62.3 | 2.8037
交流220kV | 2009-06-05 | 2013-03-05 | 3.7507 | 5.1 | 166.3 | 497 | 3.4 | 0.4 | 0.9 | 0 | 4.7 | 0.018 | 0.062 | 59.8 | 2.9886
交流220kV | 2008-12-24 | 2012-09-24 | 3.7534 | 7.7 | 166.2 | 1200.77 | 3.89 | 0.52 | 0.32 | 0 | 4.73 | 0.009 | 0.002 | 60 | 7.2248
交流220kV | 2008-12-24 | 2012-09-24 | 3.7534 | 4.74 | 160.84 | 1271.82 | 3.87 | 0.41 | 0.32 | 0 | 4.6 | 0.011 | 0.003 | 62 | 7.9074
交流220kV | 2010-03-26 | 2013-12-30 | 3.7671 | 16.16 | 227.36 | 455.91 | 2.77 | 0.17 | 0.29 | 0 | 3.23 | 0 | 0 | 0 | 2.0052
交流220kV | 2009-01-23 | 2012-10-31 | 3.7726 | 96.1 | 182.2 | 225.2 | 5.3 | 0.2 | 0.8 | 0 | 6.3 | 0.012 | 0.084 | 55.4 | 1.236
交流220kV | 2009-01-23 | 2012-10-31 | 3.7726 | 270.7 | 137.5 | 180.4 | 12.2 | 0 | 1.7 | 0 | 13.9 | 0.012 | 0.107 | 58.3 | 1.312
交流220kV | 2007-09-22 | 2011-07-01 | 3.7753 | 41.05 | 389.25 | 553.9 | 4.32 | 0.32 | 0.4 | 0 | 5.04 | 0 | 0 | 0 | 1.423
交流220kV | 2007-09-22 | 2011-07-01 | 3.7753 | 44.45 | 590.35 | 896.81 | 8.5 | 0.66 | 5.19 | 0 | 14.35 | 0 | 0 | 0 | 1.5191
交流220kV | 2007-11-28 | 2011-09-08 | 3.7808 | 13.73 | 175.09 | 750.47 | 7.1 | 1.33 | 0.52 | 0 | 8.95 | 0.008 | 0.006 | 60 | 4.2862
交流220kV | 2007-11-28 | 2011-09-08 | 3.7808 | 7.46 | 94.71 | 525.48 | 4.45 | 0.96 | 0.31 | 0.08 | 5.8 | 0.009 | 0.005 | 56 | 5.5483
交流220kV | 2007-09-13 | 2011-06-27 | 3.789 | 6.1 | 519.4 | 2973.9 | 5.6 | 13.6 | 0 | 0 | 19.2 | 0 | 0 | 0 | 5.7256
交流220kV | 2009-05-20 | 2013-03-07 | 3.8 | 17.8 | 201.8 | 749.2 | 4.8 | 0.5 | 0.9 | 0 | 6.2 | 0.007 | 0.05 | 58.2 | 3.7126
交流220kV | 2007-12-25 | 2011-10-12 | 3.8 | 28 | 345 | 3381 | 8 | 1.6 | 1.9 | 0 | 11.5 | 0.003 | 0.001 | 48 | 9.8
交流220kV | 2008-02-27 | 2011-12-16 | 3.8027 | 10 | 666 | 2475 | 19.8 | 3.2 | 1.4 | 0 | 24.4 | 0.003 | 0.002 | 40 | 3.7162
交流220kV | 2008-03-19 | 2012-01-09 | 3.811 | 77.39 | 712.7 | 1313.73 | 6.18 | 0.86 | 2.02 | 0 | 9.06 | 0.006 | 0.003 | 52 | 1.8433
交流220kV | 2008-06-05 | 2012-03-28 | 3.8137 | 5.71 | 325.55 | 1853.21 | 4.36 | 1.2 | 0.76 | 0 | 6.32 | 0 | 0 | 0 | 5.6926
交流220kV | 2007-06-14 | 2011-04-06 | 3.8137 | 11.06 | 208.62 | 395.52 | 2.9 | 0.93 | 0.47 | 0 | 4.3 | 0.001 | 0.007 | 60 | 1.8959
交流220kV | 2008-04-30 | 2012-02-22 | 3.8164 | 18 | 369 | 277 | 41.49 | 0.99 | 3.75 | 0 | 46.23 | 0.001 | 0.001 | 55.2 | 0.75068
交流220kV | 2008-05-31 | 2012-03-26 | 3.8219 | 7.38 | 423.21 | 819.27 | 6.2 | 1.1 | 2.6 | 0 | 9.9 | 0.002 | 0.2 | 49 | 1.9358
交流220kV | 2008-06-02 | 2012-03-28 | 3.8219 | 54 | 256.6 | 1015.4 | 4.9 | 1.2 | 0.7 | 0 | 6.8 | 0.02 | 0 | 61.4 | 3.9571
交流220kV | 2008-05-31 | 2012-03-26 | 3.8219 | 12.28 | 364.98 | 594.09 | 5.06 | 0.98 | 1.56 | 0 | 7.6 | 0.002 | 0.2 | 49 | 1.6277
交流220kV | 2010-04-20 | 2014-02-13 | 3.8219 | 25.08 | 996.88 | 2871.96 | 26.21 | 0.86 | 2.93 | 0 | 30 | 0.008 | 0.046 | 57.2 | 2.8809
交流220kV | 2008-11-28 | 2012-09-24 | 3.8247 | 9.63 | 162.63 | 474.91 | 3.08 | 0.41 | 0.49 | 0 | 3.98 | 0.011 | 0.003 | 60 | 2.9202
交流220kV | 2008-11-28 | 2012-09-24 | 3.8247 | 11.46 | 184.24 | 507.22 | 2.77 | 0.32 | 0.37 | 0 | 3.46 | 0.01 | 0.002 | 60 | 2.753
交流220kV | 2007-12-16 | 2011-10-12 | 3.8247 | 10 | 192 | 1345 | 15 | 0.9 | 1.9 | 0 | 17.8 | 0.003 | 0.001 | 50 | 7.0052
交流220kV | 2007-12-14 | 2011-10-10 | 3.8247 | 62 | 371 | 1674 | 5.9 | 0.7 | 2.1 | 0 | 8.7 | 0.047 | 0.003 | 62 | 4.5121
交流220kV | 2007-12-16 | 2011-10-12 | 3.8247 | 9 | 138 | 827 | 9.9 | 0.3 | 0.6 | 0 | 10.8 | 0.003 | 0.003 | 48 | 5.9928
交流220kV | 2007-09-13 | 2011-07-11 | 3.8274 | 25.5 | 546.2 | 4156.7 | 8 | 31.8 | 0 | 0 | 39.8 | 0 | 0 | 0 | 7.6102
交流220kV | 2008-05-31 | 2012-03-28 | 3.8274 | 59.6 | 253.9 | 976.8 | 4.8 | 0.7 | 0.7 | 0 | 6.2 | 0.024 | 0 | 60.9 | 3.8472
交流220kV | 2009-12-28 | 2013-10-25 | 3.8274 | 4.14 | 373.54 | 1037.3 | 4.72 | 0.41 | 0.64 | 0 | 5.77 | 0.008 | 0.016 | 61.1 | 2.7769
交流220kV | 2009-12-28 | 2013-10-25 | 3.8274 | 8.36 | 474.98 | 1725.47 | 6.1 | 0.42 | 0.93 | 0 | 7.45 | 0.007 | 0.012 | 60.2 | 3.6327
交流220kV | 2007-08-10 | 2011-06-09 | 3.8329 | 41 | 165 | 1317 | 4 | 1 | 1 | 0 | 6 | 0.005 | 41 | 38 | 7.9818
交流220kV | 2009-02-26 | 2012-12-27 | 3.8356 | 8.27 | 459.49 | 2157.5 | 4.53 | 0.84 | 0.88 | 0 | 6.25 | 0.011 | 0.004 | 61 | 4.6954
交流220kV | 2008-12-30 | 2012-10-31 | 3.8384 | 22.7 | 667.3 | 1162.2 | 9 | 0 | 0.7 | 0 | 9.7 | 0.012 | 0.084 | 56.4 | 1.7416
交流220kV | 2008-12-30 | 2012-10-31 | 3.8384 | 17 | 684.7 | 1397.7 | 9.6 | 0 | 0.7 | 0 | 10.3 | 0.012 | 0.075 | 57.3 | 2.0413
交流220kV | 2007-08-25 10:00 | 2011-06-30 | 3.8482 | 5 | 98 | 1641 | 4.64 | 1.64 | 1.43 | 0 | 7.71 | 0.005 | 0.042 | 48 | 16.7449
交流220kV | 2007-12-21 | 2011-10-26 | 3.8493 | 149.2 | 958.8 | 3978.1 | 10.7 | 0.3 | 1.4 | 0 | 12.4 | 0 | 0 | 0 | 4.149
交流220kV | 2009-07-15 | 2013-05-20 | 3.8493 | 47.15 | 200.22 | 783.97 | 12.49 | 3.46 | 1.5 | 0 | 17.45 | 0.06 | 0.001 | 55 | 3.9155
220 | 2009-05-06 | 2013-03-12 | 3.8521 | 26.87 | 232.32 | 806.87 | 3.75 | 0.31 | 0.49 | 0 | 4.55 | 0.008 | 0.06 | 58 | 3.4731
220 | 2009-05-06 | 2013-03-12 | 3.8521 | 31.81 | 187.23 | 706.36 | 4.08 | 0.68 | 0.57 | 0 | 5.33 | 0.009 | 0.084 | 59 | 3.7727
交流220kV | 2008-06-30 | 2012-05-08 | 3.8575 | 13.3 | 837.8 | 4433.3 | 8 | 0.6 | 1.1 | 0 | 9.7 | 0.016 | 0.033 | 58 | 5.2916
交流220kV | 2008-01-08 | 2011-11-16 | 3.8575 | 2 | 147 | 565 | 25 | 12.3 | 0.9 | 0 | 38.2 | 0.009 | 0.004 | 65 | 3.8435
交流220kV | 2004-04-23 | 2008-03-03 | 3.863 | 6.5 | 109.3 | 1229.8 | 3.8 | 1.1 | 0.9 | 0 | 5.8 | 0.003 | 0.358 | 53.6 | 11.2516
交流220kV | 2010-05-11 | 2014-03-21 | 3.863 | 18 | 193 | 533 | 3.62 | 0.33 | 0.49 | 0 | 4.44 | 0.019 | 0.377 | 55 | 2.7617
交流220kV | 2008-02-04 | 2011-12-16 | 3.8658 | 8.3 | 463 | 5848 | 10.8 | 1.1 | 4.1 | 0 | 16 | 0 | 0 | 0 | 12.6307
交流220kV | 2007-12-01 | 2011-10-12 | 3.8658 | 45 | 223 | 2476 | 8 | 2.9 | 1.6 | 0 | 12.5 | 0.003 | 0.002 | 50 | 11.1031
交流220kV | 2009-07-09 | 2013-05-21 | 3.8685 | 36.67 | 721 | 1344.76 | 10.55 | 4.31 | 2.33 | 0 | 17.19 | 0.04 | 0.001 | 59 | 1.8651
交流220kV | 2009-12-30 | 2013-11-11 | 3.8685 | 26.44 | 564.47 | 4187.78 | 6.9 | 1.48 | 1.6 | 0.13 | 10.11 | 0.01 | 0.001 | 54.9 | 7.419
交流220kV | 2008-06-26 | 2012-05-11 | 3.8767 | 3.41 | 360.02 | 852.34 | 6.62 | 2.63 | 0 | 0 | 9.25 | 0 | 0 | 0 | 2.3675
交流220kV | 2001-05-23 | 2005-04-07 | 3.8767 | 9.9 | 664.2 | 3605.7 | 42.5 | 28.1 | 10 | 1.6 | 82.2 | 0.016 | 0.055 | 56 | 5.4286
交流220kV | 2007-08-21 | 2011-07-07 | 3.8795 | 23.1 | 134.9 | 792.8 | 2.1 | 0.6 | 0.4 | 0 | 3.1 | 0.01 | 0.08 | 60 | 5.8769
交流220kV | 2009-06-09 | 2013-04-25 | 3.8795 | 13.6 | 467 | 1578.9 | 4.9 | 0.6 | 0.6 | 0 | 6.1 | 0.003 | 0.04 | 54.8 | 3.3809
交流220kV | 2009-12-28 | 2013-11-15 | 3.8849 | 25 | 207 | 908 | 3.14 | 1.81 | 1.33 | 0 | 6.28 | 0.02 | 0.028 | 71 | 4.3865
交流220kV | 2009-12-28 | 2013-11-15 | 3.8849 | 21 | 135 | 838 | 4.3 | 0.97 | 2.56 | 0 | 7.83 | 0.03 | 0.03 | 55 | 6.2074
交流220kV | 2009-07-10 | 2013-05-29 | 3.8877 | 17.4 | 70 | 666.6 | 3.5 | 0.7 | 1.2 | 0 | 5.4 | 0.007 | 0 | 59.3 | 9.5229
交流220kV | 2009-01-15 | 2012-12-10 | 3.9041 | 15.77 | 243.15 | 1171.11 | 3.4 | 0 | 0 | 0 | 3.4 | 0 | 0 | 0 | 4.8164
交流220kV | 2008-12-12 | 2012-11-06 | 3.9041 | 58.9 | 287.9 | 405.4 | 6.1 | 0 | 1.2 | 0 | 7.3 | 0.012 | 0.068 | 56.8 | 1.4081
交流220kV | 2008-12-12 | 2012-11-06 | 3.9041 | 32.9 | 263.5 | 410.6 | 4.3 | 0 | 0.6 | 0 | 4.9 | 0.012 | 0.061 | 53.6 | 1.5583
交流220kV | 2009-04-14 | 2013-03-11 | 3.9096 | 12.53 | 197.5 | 330.72 | 2.71 | 0.25 | 0.37 | 0 | 3.33 | 0.009 | 0.061 | 64 | 1.6745
交流220kV | 2009-04-14 | 2013-03-11 | 3.9096 | 9.48 | 389.8 | 666.67 | 4.86 | 0.27 | 0.51 | 0 | 5.64 | 0.01 | 0.05 | 61.2 | 1.7103
220 | 2009-04-22 | 2013-03-20 | 3.9123 | 13.49 | 147.72 | 997.42 | 3.81 | 0.52 | 0.49 | 0 | 4.82 | 0.07 | 0.023 | 56 | 6.7521
交流220kV | 2009-04-10 | 2013-03-08 | 3.9123 | 13.7 | 122.7 | 659.2 | 3.6 | 1.9 | 1.2 | 0 | 6.7 | 0.006 | 0.052 | 59.6 | 5.3725
交流220kV | 2009-04-10 | 2013-03-08 | 3.9123 | 15.6 | 106.6 | 461.1 | 13.5 | 15.8 | 2.5 | 0.2 | 32 | 0.007 | 0.03 | 54.4 | 4.3255
220 | 2010-04-14 | 2014-03-13 | 3.9151 | 14.02 | 94.5 | 1005.98 | 3.4 | 0.36 | 0.68 | 0 | 4.44 | 0.012 | 0.089 | 40 | 10.6453
220 | 2008-05-09 | 2012-04-10 | 3.9233 | 29.65 | 115.81 | 552.86 | 5.82 | 0.77 | 3.4 | 0 | 9.99 | 0.005 | 0.055 | 59 | 4.7739
220 | 2008-05-09 | 2012-04-12 | 3.9288 | 29.65 | 115.81 | 552.86 | 5.82 | 0.77 | 3.4 | 0 | 9.99 | 0.005 | 0.055 | 59 | 4.7739
220 | 2008-05-09 | 2012-04-12 | 3.9288 | 25.65 | 122.72 | 639.76 | 5.77 | 0.66 | 3.91 | 0 | 10.34 | 0.005 | 0.051 | 58 | 5.2132
220 | 2008-04-26 | 2012-03-31 | 3.9315 | 48.53 | 459.6 | 1712.54 | 9.97 | 1.51 | 1.48 | 0 | 12.96 | 0.011 | 0.001 | 54 | 3.7262
交流220kV | 2010-04-19 | 2014-03-25 | 3.9342 | 13.6 | 118 | 240 | 2 | 0.4 | 0.4 | 0.1 | 2.9 | 0.002 | 0.08 | 64.2 | 2.0339
交流220kV | 2010-04-19 | 2014-03-25 | 3.9342 | 14.4 | 203.8 | 422.8 | 2.3 | 0.5 | 0.5 | 0 | 3.3 | 0.002 | 0.17 | 68.8 | 2.0746
交流220kV | 2008-12-30 | 2012-12-05 | 3.9342 | 17.23 | 734.54 | 2686.59 | 9.97 | 1.34 | 0.95 | 0 | 12.26 | 0.011 | 0.004 | 43 | 3.6575
220 | 2008-03-31 | 2012-03-07 | 3.937 | 12.84 | 914.12 | 1978.14 | 8.17 | 1.06 | 0.69 | 0 | 9.92 | 0.01 | 0.079 | 53 | 2.164
交流220kV | 2010-03-16 | 2014-02-20 | 3.937 | 17 | 122 | 438 | 2.33 | 0.19 | 0.36 | 0 | 2.88 | 0.001 | 0.029 | 63 | 3.5902
交流220kV | 2009-06-21 | 2013-05-29 | 3.9397 | 8.2 | 329.3 | 1072.9 | 5.5 | 0.5 | 1 | 0 | 7 | 0.005 | 0 | 64.9 | 3.2581
交流220kV | 2008-03-31 | 2012-03-09 | 3.9425 | 30.66 | 373.42 | 695.17 | 4.68 | 0.7 | 1.45 | 0.14 | 6.97 | 0.007 | 0.122 | 48.8 | 1.8616
交流220kV | 2008-03-31 | 2012-03-09 | 3.9425 | 25.18 | 362.25 | 745.52 | 4.41 | 0.48 | 0.76 | 0 | 5.65 | 0.007 | 0.119 | 50.4 | 2.058
220 | 2009-03-31 | 2013-03-11 | 3.9479 | 115.77 | 340.08 | 846.4 | 4.81 | 0.44 | 0.89 | 0 | 6.14 | 0.009 | 0.064 | 57 | 2.4888
220 | 2009-12-17 | 2013-11-27 | 3.9479 | 6.46 | 346.91 | 1199.12 | 7.08 | 0.36 | 0.92 | 0 | 8.36 | 0.009 | 0.045 | 62 | 3.4566
交流220kV | 2009-03-15 | 2013-02-24 | 3.9507 | 120.41 | 94.43 | 846.55 | 43.68 | 46.38 | 11.79 | 0 | 101.85 | 0.021 | 0.01 | 56.8 | 8.9648
交流220kV | 2008-06-05 | 2012-05-21 | 3.9616 | 7.67 | 347.39 | 2144.58 | 4.98 | 1.43 | 1 | 0 | 7.41 | 0 | 0.001 | 56.5 | 6.1734
交流220kV | 2008-05-23 | 2012-05-08 | 3.9616 | 12.4 | 324.8 | 991.2 | 5.7 | 0.6 | 1.6 | 0 | 7.9 | 0.004 | 0 | 68.4 | 3.0517
交流220kV | 2008-12-26 | 2012-12-13 | 3.9671 | 18.1 | 385.3 | 1049.8 | 6.5 | 0.5 | 0.6 | 0 | 7.6 | 0 | 0 | 0 | 2.7246
交流220kV | 2008-12-26 | 2012-12-13 | 3.9671 | 18.1 | 280.3 | 809.3 | 4.2 | 0.7 | 0.6 | 0 | 5.5 | 0 | 0 | 0 | 2.8873
交流220kV | 2007-12-25 | 2011-12-13 | 3.9699 | 71.33 | 458.84 | 2884.2 | 8.29 | 4.82 | 1.85 | 0 | 14.96 | 0.003 | 0.002 | 49 | 6.2859
交流220kV | 2009-02-12 | 2013-01-31 | 3.9699 | 4.4 | 121 | 841.7 | 9.2 | 0.5 | 1.3 | 0 | 11 | 0.004 | 0.049 | 63.8 | 6.9562
交流220kV | 2007-12-27 | 2011-12-16 | 3.9726 | 39.2 | 106.6 | 470.3 | 3.3 | 0.3 | 0.9 | 0 | 4.5 | 0 | 0 | 0 | 4.4118
交流220kV | 2009-03-01 | 2013-02-18 | 3.9726 | 6.2 | 180.2 | 768.3 | 2.5 | 0.4 | 0.8 | 0 | 3.7 | 0.005 | 0.163 | 62.2 | 4.2636
交流220kV | 2010-04-01 | 2014-03-21 | 3.9726 | 17 | 189 | 548 | 3.44 | 0.53 | 0.51 | 0 | 4.48 | 0.019 | 0.41 | 60 | 2.8995
交流220kV | 2007-06-18 | 2011-06-08 | 3.9753 | 8 | 391 | 1013 | 9 | 1 | 1 | 0 | 11 | 0.015 | 0.074 | 52 | 2.5908
交流220kV | 2009-05-26 | 2013-05-16 | 3.9753 | 16.68 | 238.79 | 591.42 | 4.99 | 0.98 | 0.88 | 0 | 6.85 | 0.012 | 0.036 | 58.2 | 2.4767
交流220kV | 2008-12-22 | 2012-12-13 | 3.9781 | 83 | 306 | 723 | 3.02 | 0.28 | 0.48 | 0 | 3.78 | 0.043 | 0.375 | 70.5 | 2.3627
交流220kV | 2010-03-16 | 2014-03-07 | 3.9781 | 4 | 33 | 178 | 1.61 | 0.22 | 2.31 | 0 | 4.14 | 0.022 | 0.182 | 58 | 5.3939
交流220kV | 2009-11-12 | 2013-11-04 | 3.9808 | 9.25 | 180.66 | 663.98 | 5.28 | 6.61 | 3.25 | 0 | 15.14 | 0.012 | 0.033 | 71 | 3.6753
交流220kV | 2009-11-12 | 2013-11-04 | 3.9808 | 11.51 | 124.47 | 603.79 | 4.43 | 0.59 | 0.61 | 0 | 5.63 | 0.008 | 0.036 | 70 | 4.8509
交流220kV | 2006-06-30 | 2010-06-23 | 3.9836 | 7.14 | 308.09 | 1250.42 | 4.3 | 2.97 | 3.97 | 0 | 11.24 | 0.023 | 0.224 | 67.7 | 4.0586
交流220kV | 2006-06-30 | 2010-06-23 | 3.9836 | 8.06 | 333.98 | 1255.7 | 6.64 | 2.08 | 0.83 | 0 | 9.55 | 0.026 | 0.24 | 65.3 | 3.7598
交流220kV | 2008-12-06 | 2012-11-30 | 3.9863 | 11.3 | 96 | 635 | 1.43 | 0.12 | 0.1 | 0 | 1.65 | 0.009 | 0.001 | 41.3 | 6.6146
交流220kV | 2007-12-21 | 2011-12-16 | 3.989 | 121 | 920.5 | 3599.6 | 10.7 | 0.7 | 1.8 | 0 | 13.2 | 0 | 0 | 0 | 3.9105
交流220kV | 2009-08-31 | 2013-08-27 | 3.9918 | 115.8 | 44.02 | 403.83 | 18.6 | 3.44 | 5.39 | 0 | 27.43 | 0.003 | 0.001 | 56 | 9.1738
交流220kV | 2009-08-31 | 2013-08-27 | 3.9918 | 73.97 | 113.43 | 445.47 | 14.51 | 4.09 | 2.85 | 0 | 21.45 | 0.004 | 0.001 | 56 | 3.9273
交流220kV | 2008-12-31 | 2012-12-28 | 3.9945 | 11.9 | 101.74 | 763.13 | 2.03 | 0.3 | 0.23 | 0 | 2.56 | 0.008 | 0.002 | 60 | 7.5008
交流220kV | 2008-12-31 | 2012-12-28 | 3.9945 | 12.03 | 103.35 | 765.3 | 2.04 | 0.29 | 0.23 | 0 | 2.56 | 0.009 | 0.001 | 61 | 7.4049
交流220kV | 2009-12-17 | 2013-12-17 | 4.0027 | 4.3 | 74.2 | 554.2 | 2.8 | 0 | 0 | 0 | 2.8 | 0.06 | 1.06 | 47 | 7.469
交流220kV | 2008-12-19 | 2012-12-21 | 4.0082 | 17.71 | 695.77 | 2845.8 | 7.29 | 2.14 | 1.46 | 0 | 10.89 | 0 | 0.03 | 50 | 4.0901
交流220kV | 2007-12-14 | 2011-12-19 | 4.0164 | 9.5 | 388.39 | 1967.14 | 3.94 | 0.65 | 0.75 | 0 | 5.34 | 0.002 | 0.03 | 42 | 5.0649
交流220kV | 2008-06-28 | 2012-07-06 | 4.0247 | 8.51 | 381.2 | 4428.9 | 8.73 | 0.16 | 1.35 | 0 | 10.24 | 0 | 0.402 | 61.3 | 11.6183
交流220kV | 2007-03-30 | 2011-04-12 | 4.0384 | 6.29 | 296.57 | 850.87 | 14.69 | 3.25 | 3.26 | 0 | 21.2 | 0.005 | 0.156 | 54.2 | 2.869
交流220kV | 2009-04-24 | 2013-05-09 | 4.0438 | 15 | 218 | 1654 | 10.9 | 0 | 0 | 0 | 10.9 | 0.006 | 0.013 | 54 | 7.5872
220 | 2009-04-28 | 2013-05-15 | 4.0493 | 11.64 | 663.79 | 2362.1 | 6.26 | 0.96 | 0.88 | 0 | 8.1 | 0.007 | 0.003 | 44 | 3.5585
交流220kV | 2009-03-22 | 2013-04-08 | 4.0493 | 29.4 | 1.14 | 13.68 | 1.72 | 0.3 | 0.49 | 0 | 2.51 | 0.015 | 0.003 | 58.6 | 12
交流220kV | 2007-01-30 | 2011-02-25 | 4.074 | 15 | 480 | 490 | 19.25 | 1.94 | 2.34 | 0 | 23.53 | 0.001 | 0.001 | 50 | 1.0208
交流220kV | 2009-04-27 | 2013-05-24 | 4.0767 | 12.55 | 708.49 | 1865.85 | 11.68 | 1.48 | 7.98 | 0 | 21.14 | 0.008 | 0.103 | 50.6 | 2.6336
交流220kV | 2009-04-19 | 2013-05-16 | 4.0767 | 12 | 279 | 795.85 | 5 | 0.94 | 0.95 | 0 | 6.89 | 0.012 | 0.043 | 57.6 | 2.8525
交流220kV | 2006-03-15 | 2010-04-12 | 4.0795 | 10.4 | 768.28 | 1852.95 | 9.57 | 1.63 | 1.75 | 0 | 12.95 | 0.005 | 0.002 | 56.2 | 2.4118
交流220kV | 2009-01-19 | 2013-02-18 | 4.0849 | 3.5 | 178.9 | 780.5 | 3.1 | 0.3 | 0.6 | 0 | 4 | 0.007 | 0.157 | 58.7 | 4.3628
交流220kV | 2010-01-25 | 2014-02-26 | 4.0904 | 5.1 | 151.2 | 556.8 | 2.2 | 0.3 | 0.6 | 0 | 3.1 | 0.002 | 0.22 | 68 | 3.6825
交流220kV | 2010-01-25 | 2014-02-26 | 4.0904 | 13.6 | 183 | 274.4 | 2.4 | 0.5 | 0.7 | 0 | 3.6 | 0.003 | 0.15 | 51.6 | 1.4995
交流220kV | 2007-11-10 | 2011-12-16 | 4.1014 | 73.6 | 598.6 | 3343.6 | 8.4 | 0.6 | 1.5 | 0 | 10.5 | 0 | 0 | 0 | 5.5857
交流220kV | 2010-01-23 | 2014-03-04 | 4.1123 | 3.73 | 245.68 | 687.12 | 4.79 | 0.64 | 0.63 | 0 | 6.06 | 0.008 | 0.281 | 60 | 2.7968
交流220kV | 2009-01-10 | 2013-02-21 | 4.1178 | 71.15 | 260.78 | 968.71 | 20.76 | 1.95 | 5.13 | 0.27 | 28.11 | 0.021 | 0.11 | 58.8 | 3.7147
交流220kV | 2007-04-28 | 2011-06-10 | 4.1205 | 10.93 | 384.7 | 4421.93 | 8.32 | 0.79 | 1.15 | 0 | 10.26 | 0 | 0 | 0 | 11.4945
交流220kV | 2007-10-30 | 2011-12-13 | 4.1233 | 5.47 | 240.08 | 710.42 | 9.49 | 0 | 0 | 0 | 9.49 | 0.01 | 0 | 0 | 2.9591
交流220kV | 2008-02-01 | 2012-03-16 | 4.1233 | 118.52 | 516.01 | 1103.24 | 13.77 | 5.47 | 2.69 | 0.66 | 22.59 | 0.005 | 0.001 | 54 | 2.138
交流220kV | 2009-10-20 | 2013-12-04 | 4.126 | 12.3 | 30.3 | 437 | 1.9 | 0.1 | 0.6 | 0 | 2.6 | 0.04 | 0.5 | 52 | 14.4224
交流220kV | 2008-10-26 | 2012-12-11 | 4.1288 | 39.3 | 421.2 | 1015.5 | 5.5 | 0.5 | 0.8 | 0 | 6.8 | 0 | 0 | 0 | 2.411
交流220kV | 2007-12-25 | 2012-02-09 | 4.1288 | 58.15 | 443.29 | 2801.35 | 8.94 | 20.37 | 0 | 0 | 29.31 | 0.002 | 0.25 | 48 | 6.3195
交流220kV | 2007-04-30 | 2011-06-16 | 4.1315 | 3.4 | 609.1 | 4254.6 | 17.9 | 7.8 | 2.6 | 0 | 28.3 | 0.01 | 0 | 49.4 | 6.9851
交流220kV | 2008-12-20 | 2013-02-06 | 4.1342 | 4 | 148.7 | 435.5 | 11.5 | 0.6 | 1 | 0 | 13.1 | 0.008 | 0.073 | 63.2 | 2.9287
交流220kV | 2007-11-29 | 2012-01-18 | 4.1397 | 14 | 140 | 292 | 5.8 | 1 | 0 | 0 | 6.8 | 0.034 | 0.46 | 46 | 2.0857
交流220kV | 2007-10-27 | 2011-12-17 | 4.1425 | 23.43 | 231.29 | 390.78 | 3.11 | 0.5 | 0.69 | 0 | 4.3 | 0 | 0 | 0 | 1.6896
交流220kV | 2008-10-20 | 2012-12-10 | 4.1425 | 11.23 | 534.32 | 1222.28 | 7.7 | 0.37 | 0.68 | 0 | 8.75 | 0 | 0 | 0 | 2.2875
交流220kV | 2007-09-11 | 2011-11-01 | 4.1425 | 29 | 107 | 1246 | 9.5 | 2.3 | 4.1 | 0 | 15.9 | 0.005 | 0.002 | 52 | 11.6449
交流220kV | 2008-02-04 | 2012-03-29 | 4.1507 | 24.1 | 399.9 | 1654.3 | 8.3 | 1 | 1.3 | 0 | 10.6 | 0.028 | 0 | 62.5 | 4.1368
交流220kV | 2009-03-21 | 2013-05-21 | 4.1699 | 9 | 219 | 893 | 3.8 | 2.6 | 0 | 0 | 6.4 | 0.027 | 0.096 | 47 | 4.0776
交流220kV | 2006-01-06 11:08 | 2010-03-11 | 4.1768 | 34 | 188 | 392 | 22.03 | 12.07 | 44.54 | 0 | 78.64 | 0.001 | 0.001 | 50 | 2.0851
220 | 2008-12-19 | 2013-02-21 | 4.1781 | 24.64 | 410.98 | 2249.39 | 20.17 | 11.12 | 6.92 | 0 | 38.21 | 0.012 | 0.122 | 60 | 5.4732
交流220kV | 2007-04-30 | 2011-07-07 | 4.189 | 90.8 | 186 | 3438.1 | 19.7 | 15.9 | 8.6 | 0.6 | 44.8 | 0 | 0 | 0 | 18.4844
交流220kV | 1998-06-30 | 2002-09-06 | 4.189 | 25.4 | 434.2 | 1366 | 52.4 | 1.3 | 2.3 | 0 | 56 | 0.01 | 0.12 | 48 | 3.146
交流220kV | 2008-11-17 | 2013-01-24 | 4.189 | 149 | 128 | 706 | 5.54 | 0.47 | 1.18 | 0 | 7.19 | 0.044 | 0.02 | 73 | 5.5156
交流220kV | 2008-09-27 | 2012-12-05 | 4.1918 | 17 | 294.8 | 1425.8 | 4.9 | 1.1 | 0.9 | 0 | 6.9 | 0 | 0 | 0 | 4.8365
交流220kV | 2008-09-27 | 2012-12-05 | 4.1918 | 14.2 | 290.6 | 1390.2 | 4.9 | 1.1 | 0.7 | 0 | 6.7 | 0 | 0 | 0 | 4.7839
交流220kV | 2003-05-01 | 2007-07-12 | 4.2 | 17.32 | 409.4 | 3982.5 | 7.06 | 1.06 | 1.87 | 0 | 9.99 | 0.021 | 0.09 | 45 | 9.7277
交流220kV | 2006-11-30 | 2011-02-11 | 4.2027 | 4.7 | 111 | 516 | 3.85 | 0.56 | 0.86 | 0.44 | 5.71 | 0.031 | 0.102 | 48.8 | 4.6486
交流220kV | 2007-10-28 | 2012-01-09 | 4.2027 | 16 | 525 | 1397 | 7.6 | 0.7 | 1.1 | 0 | 9.4 | 0.047 | 0.032 | 61 | 2.661
交流220kV | 2009-06-15 | 2013-08-30 | 4.211 | 40.8 | 287.92 | 782.41 | 4.59 | 0.61 | 0.79 | 0 | 5.99 | 0.002 | 0.001 | 58 | 2.7175
交流220kV | 2000-02-26 | 2004-05-14 | 4.2164 | 25.1 | 791.1 | 1423.8 | 9.8 | 4.7 | 18.6 | 0.4 | 33.5 | 0.006 | 0.708 | 50 | 1.7998
交流220kV | 2008-12-25 | 2013-03-14 | 4.2192 | 7.4 | 449.13 | 546.98 | 7.42 | 1.48 | 0.83 | 0.16 | 9.89 | 0.007 | 0.14 | 60.4 | 1.2179
交流220kV | 2007-07-23 | 2011-10-10 | 4.2192 | 39 | 474 | 2581 | 6.9 | 1.2 | 3.2 | 0.1 | 11.4 | 0.048 | 0.002 | 62 | 5.4451
交流220kV | 2008-12-13 | 2013-03-03 | 4.2219 | 13.34 | 267.11 | 1285.42 | 4.21 | 3.24 | 3.89 | 0 | 11.34 | 0.006 | 0.06 | 47.6 | 4.8123
交流220kV | 2007-11-26 | 2012-02-14 | 4.2219 | 29.19 | 588.62 | 813.08 | 13.98 | 3.47 | 2.75 | 0 | 20.2 | 0.009 | 0.019 | 62.8 | 1.3813
交流220kV | 2008-04-29 | 2012-07-18 | 4.2219 | 13.56 | 472.93 | 4558.7 | 10.66 | 1.58 | 1.29 | 0.3 | 13.83 | 0.009 | 0.001 | 60 | 9.6393
220 | 2008-04-11 | 2012-07-02 | 4.2274 | 7.23 | 546.96 | 1342 | 5.82 | 0.7 | 1.55 | 0 | 8.07 | 0.012 | 0.018 | 59.5 | 2.4536
交流220kV | 2007-12-25 | 2012-03-16 | 4.2274 | 54.89 | 446.46 | 3046.53 | 8.23 | 4.92 | 2.06 | 0 | 15.21 | 0.002 | 0.2 | 51 | 6.8237
交流220kV | 2008-09-12 | 2012-12-05 | 4.2329 | 56 | 90 | 516 | 3 | 0 | 1 | 0 | 4 | 0 | 0 | 0 | 5.7333
交流220kV | 2008-12-31 | 2013-03-25 | 4.2329 | 58 | 337 | 1450 | 8.54 | 0.7 | 1.13 | 0 | 10.37 | 0.006 | 0.1 | 59 | 4.3027
交流220kV | 2008-12-31 | 2013-03-25 | 4.2329 | 54 | 319 | 1137 | 8.25 | 0.73 | 0.9 | 0 | 9.88 | 0.009 | 0.3 | 61 | 3.5643
交流220kV | 2007-09-22 | 2011-12-17 | 4.2384 | 32.5 | 524.75 | 857.71 | 7.35 | 1.21 | 0.51 | 0 | 9.07 | 0 | 0 | 0 | 1.6345
交流220kV | 2007-09-22 | 2011-12-17 | 4.2384 | 20.54 | 206.31 | 367.68 | 2.99 | 0.31 | 0.3 | 0 | 3.6 | 0 | 0 | 0 | 1.7822
交流220kV | 2008-07-21 | 2012-10-18 | 4.2466 | 7.81 | 559.45 | 1300.88 | 7.52 | 0.76 | 1.08 | 0 | 9.36 | 0.013 | 0.23 | 62 | 2.3253
交流220kV | 2007-12-30 | 2012-03-29 | 4.2493 | 4.91 | 532.97 | 2730.73 | 4.44 | 0.85 | 0 | 0 | 5.29 | 0 | 0 | 0 | 5.1236
交流220kV | 2009-09-20 | 2013-12-20 | 4.2521 | 18.04 | 150.23 | 241.18 | 5.29 | 0.63 | 0.77 | 0 | 6.69 | 0 | 0 | 61 | 1.6054
220 | 2008-12-19 | 2013-03-21 | 4.2548 | 19.7 | 345.18 | 1384.62 | 20.92 | 12.93 | 6.1 | 0 | 39.95 | 0.012 | 0.13 | 58.4 | 4.0113
交流220kV | 2007-09-13 | 2011-12-15 | 4.2575 | 9 | 616 | 2770.1 | 6.3 | 13.7 | 0 | 0 | 20 | 0.02 | 0 | 50 | 4.4969
交流220kV | 2007-09-13 | 2011-12-15 | 4.2575 | 25.2 | 549.2 | 4170.3 | 5.2 | 23.7 | 0 | 0 | 28.9 | 0.02 | 0 | 50 | 7.5934
交流220kV | 2007-12-20 | 2012-03-22 | 4.2575 | 2.4 | 182.2 | 370 | 4.5 | 0.5 | 0.5 | 0 | 5.5 | 0.007 | 0.098 | 57.8 | 2.0307
交流220kV | 2008-12-06 | 2013-03-11 | 4.263 | 17.5 | 96 | 864 | 1.4 | 0.22 | 0 | 0 | 1.62 | 0.006 | 0.001 | 45.7 | 9
220 | 2008-12-18 | 2013-03-26 | 4.2712 | 14.35 | 511.95 | 1215.12 | 5.99 | 0.59 | 0.93 | 0 | 7.51 | 0.005 | 0.001 | 60 | 2.3735
220 | 2008-12-18 | 2013-03-26 | 4.2712 | 18.16 | 353.34 | 992.65 | 4.94 | 0.5 | 0.69 | 0 | 6.13 | 0.005 | 0.001 | 58 | 2.8093
交流220kV | 2009-01-18 | 2013-04-27 | 4.274 | 3.5 | 174.5 | 536.2 | 2.7 | 0.3 | 0.4 | 0 | 3.4 | 0.011 | 0.155 | 49.6 | 3.0728
交流220kV | 2008-06-12 | 2012-09-20 | 4.2767 | 12.53 | 394.55 | 1170.03 | 6.24 | 1.02 | 0.57 | 0 | 7.83 | 0.011 | 0.001 | 60 | 2.9655
交流220kV | 2009-11-04 | 2014-02-13 | 4.2795 | 18.58 | 986.02 | 2637.68 | 17.56 | 0.67 | 2.4 | 0 | 20.63 | 0.012 | 0.046 | 55.6 | 2.6751
交流220kV | 2008-07-08 | 2012-10-18 | 4.2822 | 3.34 | 251.19 | 1074.25 | 5.92 | 1.42 | 2.88 | 0 | 10.22 | 0.006 | 0.001 | 62 | 4.2766
交流220kV | 2008-11-21 | 2013-03-04 | 4.2849 | 10.31 | 602.42 | 677.62 | 25.53 | 0.94 | 3 | 0 | 29.47 | 0.008 | 0.285 | 53.6 | 1.1248
交流220kV | 2007-11-25 | 2012-03-07 | 4.2849 | 25.21 | 340.77 | 830.02 | 5.71 | 1.15 | 0.53 | 0 | 7.39 | 0.008 | 0.093 | 51.3 | 2.4357
交流220kV | 2007-11-25 | 2012-03-07 | 4.2849 | 26.11 | 359.05 | 875.52 | 5.23 | 0.75 | 0.37 | 0 | 6.35 | 0.009 | 0.103 | 51.7 | 2.4384
交流220kV | 2008-07-07 | 2012-10-18 | 4.2849 | 12.03 | 241.66 | 851.94 | 4.12 | 0.8 | 0.87 | 0 | 5.79 | 0.008 | 0.001 | 60 | 3.5254
220 | 2008-11-30 | 2013-03-20 | 4.3041 | 9 | 70 | 293 | 1.2 | 0 | 0 | 0 | 1.2 | 0.007 | 0.001 | 52 | 4.1857
交流220kV | 2008-07-15 | 2012-11-02 | 4.3041 | 18.7 | 424 | 629.9 | 5.1 | 0 | 0 | 0 | 5.1 | 0.012 | 0.064 | 58.8 | 1.4856
交流220kV | 2008-07-15 | 2012-11-02 | 4.3041 | 25.2 | 489 | 630.4 | 5.9 | 0 | 0.6 | 0 | 6.5 | 0.012 | 0.084 | 54.3 | 1.2892
交流220kV | 2006-12-16 | 2011-04-06 | 4.3068 | 11.04 | 277 | 677 | 3.39 | 0.73 | 0.27 | 0 | 4.39 | 0.026 | 0.751 | 52.8 | 2.444
交流220kV | 2007-07-27 | 2011-11-17 | 4.3123 | 9 | 528 | 2503 | 9.9 | 1.2 | 2.1 | 0.1 | 13.3 | 0.002 | 0.001 | 45 | 4.7405
交流220kV | 2007-05-04 | 2011-08-26 | 4.3151 | 9.63 | 173.24 | 816.02 | 9.04 | 3.1 | 1.16 | 0 | 13.3 | 0.005 | 0.002 | 60 | 4.7103
交流220kV | 2009-01-15 | 2013-05-14 | 4.3288 | 12.7 | 256.8 | 1275.9 | 4.6 | 0 | 0 | 0 | 4.6 | 0.013 | 0.065 | 0 | 4.9685
交流220kV | 2008-11-04 | 2013-03-03 | 4.3288 | 16.49 | 285.85 | 1268.34 | 18.47 | 7.03 | 6.29 | 0 | 31.79 | 0.007 | 0.04 | 50.6 | 4.4371
交流220kV | 2007-04-29 | 2011-08-26 | 4.3288 | 11.87 | 215.48 | 662.5 | 8.23 | 0.94 | 0.82 | 0 | 9.99 | 0.003 | 0.001 | 60 | 3.0745
交流220kV | 2008-11-18 | 2013-03-18 | 4.3315 | 13.21 | 103.97 | 570.78 | 8.23 | 4.66 | 4.21 | 0 | 17.1 | 0.008 | 0.15 | 51.6 | 5.4899
交流220kV | 2008-11-18 | 2013-03-18 | 4.3315 | 15.64 | 179.46 | 421.95 | 12.17 | 5.27 | 5.51 | 0 | 22.95 | 0.008 | 0.12 | 52.8 | 2.3512
交流220kV | 2005-09-19 | 2010-01-18 | 4.3342 | 8 | 562 | 2246 | 11.4 | 1.7 | 3.7 | 0 | 16.8 | 0.01 | 0.02 | 56 | 3.9964
交流220kV | 2008-11-29 | 2013-04-01 | 4.3397 | 88.83 | 348.56 | 948.85 | 6.6 | 1.27 | 1.15 | 0 | 9.02 | 0.014 | 0.15 | 61.7 | 2.7222
交流220kV | 2009-11-18 | 2014-03-21 | 4.3397 | 16.34 | 41.65 | 56.3 | 0.15 | 0.4 | 0.3 | 0 | 0.85 | 0.004 | 0.04 | 70 | 1.3517
交流220kV | 2007-11-29 | 2012-04-01 | 4.3425 | 7.9 | 69.11 | 157.17 | 2.43 | 0.37 | 0.23 | 0 | 3.03 | 0.027 | 0.055 | 56 | 2.2742
交流220kV | 2008-10-31 | 2013-03-05 | 4.3452 | 23.2 | 592.8 | 1081.1 | 5 | 0.5 | 1 | 0 | 6.5 | 0.017 | 0.059 | 61.2 | 1.8237
交流220kV | 2006-01-18 | 2010-05-25 | 4.3507 | 17.08 | 192.59 | 254.03 | 6.64 | 0 | 0 | 0 | 6.64 | 0.003 | 2.97 | 38.1 | 1.319
交流220kV | 2008-06-28 | 2012-11-02 | 4.3507 | 17 | 552.1 | 960.6 | 6.3 | 0 | 1.1 | 0 | 7.4 | 0.012 | 0.082 | 53.3 | 1.7399
交流220kV | 2006-01-17 | 2010-05-25 | 4.3534 | 18.25 | 231.21 | 179.18 | 11.66 | 1.18 | 2.3 | 0 | 15.14 | 0.003 | 0.147 | 39.4 | 0.77497
交流220kV | 2002-03-01 | 2006-07-07 | 4.3534 | 65.02 | 562.38 | 1925.64 | 6.27 | 3.1 | 0 | 0 | 9.37 | 0.008 | 0.6 | 51.5 | 3.4241
交流220kV | 2006-01-23 | 2010-06-02 | 4.3589 | 18.77 | 353.99 | 809.36 | 8.2 | 1.86 | 2.36 | 0 | 12.42 | 0.002 | 0.375 | 67.1 | 2.2864
交流220kV | 2007-12-14 | 2012-04-23 | 4.3616 | 10.63 | 338.89 | 1774.75 | 3.82 | 1.05 | 1.29 | 0 | 6.16 | 0.002 | 0.2 | 49 | 5.237
交流220kV | 2009-06-29 | 2013-11-08 | 4.3644 | 17.12 | 167.39 | 634.19 | 3.41 | 0.5 | 0.4 | 0 | 4.31 | 0.011 | 0.036 | 67 | 3.7887
交流220kV | 2009-06-29 | 2013-11-08 | 4.3644 | 12.66 | 166.56 | 573.34 | 3.6 | 0.44 | 0.3 | 0 | 4.34 | 0.008 | 0.046 | 67 | 3.4422
交流220kV | 2008-11-09 | 2013-03-22 | 4.3671 | 5 | 285 | 278 | 15.01 | 1.42 | 3.2 | 0 | 19.63 | 0.001 | 0.04 | 51.5 | 0.97544
交流220kV | 2008-11-25 | 2013-04-10 | 4.3753 | 3 | 17 | 268 | 1 | 0 | 0 | 0 | 1 | 0.008 | 0.093 | 57 | 15.7647
交流220kV | 2008-10-20 | 2013-03-06 | 4.3781 | 14 | 699 | 289 | 12.53 | 0.92 | 1.83 | 0 | 15.28 | 0.026 | 0.11 | 53.6 | 0.41345
交流220kV | 2007-12-21 | 2012-05-07 | 4.3808 | 123.4 | 987.4 | 3705.2 | 11 | 0.7 | 2.1 | 0 | 13.8 | 0 | 0.03 | 64 | 3.7525
220 | 2009-10-15 | 2014-03-04 | 4.3863 | 17.92 | 220.64 | 947.56 | 3.96 | 0.47 | 0.46 | 0 | 4.89 | 0.012 | 0.064 | 59 | 4.2946
220 | 2009-10-15 | 2014-03-04 | 4.3863 | 12.43 | 224.72 | 1009.96 | 4.33 | 0.63 | 0.52 | 0 | 5.48 | 0.01 | 0.062 | 57 | 4.4943
交流220kV | 2007-11-03 | 2012-03-22 | 4.3863 | 32.7 | 393.42 | 583.8 | 5.19 | 0.5 | 0.55 | 0 | 6.24 | 0.005 | 0.001 | 54.5 | 1.4839
交流220kV | 2007-11-03 | 2012-03-22 | 4.3863 | 13.12 | 94.36 | 302.54 | 4.62 | 0.43 | 1 | 0 | 6.05 | 0.007 | 0.001 | 55 | 3.2062
220 | 2008-10-31 | 2013-03-22 | 4.3918 | 13 | 281 | 414 | 4.9 | 1.1 | 0 | 0 | 6 | 0.007 | 0.001 | 52 | 1.4733
交流220kV | 2009-07-10 | 2013-12-03 | 4.4027 | 29.7 | 105.4 | 831.7 | 4.4 | 0.8 | 1.1 | 0 | 6.3 | 0 | 0 | 0 | 7.8909
交流220kV | 2008-06-19 | 2012-11-12 | 4.4027 | 10.83 | 280.4 | 842.6 | 4.41 | 0.55 | 0.37 | 0 | 5.33 | 0.011 | 0.003 | 60 | 3.005
交流220kV | 2008-06-19 | 2012-11-12 | 4.4027 | 7.05 | 287.74 | 751.32 | 4.01 | 0.49 | 0.34 | 0 | 4.84 | 0.008 | 0.002 | 60 | 2.6111
交流220kV | 2009-04-23 | 2013-09-16 | 4.4027 | 2.8 | 2 | 56 | 3.11 | 0.22 | 0.54 | 0 | 3.87 | 0.013 | 0.002 | 67 | 28
交流220kV | 2008-06-22 | 2012-11-15 | 4.4027 | 16 | 116 | 895 | 5.11 | 0.9 | 1.53 | 0 | 7.54 | 0.026 | 0.121 | 70 | 7.7155
交流220kV | 2009-04-23 | 2013-09-16 | 4.4027 | 24 | 66 | 814 | 3.8 | 0.96 | 0.56 | 0 | 5.32 | 0.012 | 0.002 | 73.4 | 12.3333
交流220kV | 2007-01-25 | 2011-06-21 | 4.4055 | 20.66 | 1123.12 | 6335.12 | 21.01 | 5.39 | 3.89 | 0.21 | 30.5 | 0.003 | 0.02 | 49 | 5.6406
交流220kV | 2007-10-30 | 2012-03-26 | 4.4082 | 4 | 206 | 567 | 8.6 | 0 | 0 | 0 | 8.6 | 0 | 0 | 0 | 2.7524
交流220kV | 2006-10-18 | 2011-03-16 | 4.411 | 21.08 | 872.05 | 1139.46 | 17.35 | 1.63 | 2.87 | 0 | 21.85 | 0.011 | 0.007 | 53 | 1.3066
交流220kV | 2006-02-21 | 2010-07-22 | 4.4164 | 103.3 | 495.2 | 2612.9 | 5.2 | 0.8 | 0.9 | 0 | 6.9 | 0.011 | 0.001 | 40.6 | 5.2765
交流220kV | 2008-12-19 | 2013-05-20 | 4.4192 | 82.66 | 464.19 | 901.87 | 14.5 | 1.04 | 1.05 | 0 | 16.59 | 0.07 | 0.001 | 58 | 1.9429
交流220kV | 2008-12-21 | 2013-05-27 | 4.4329 | 15 | 170.4 | 197.2 | 2.4 | 0.1 | 0.2 | 0.1 | 2.8 | 0.012 | 0.111 | 56.8 | 1.1573
交流220kV | 2008-12-21 | 2013-05-27 | 4.4329 | 11.9 | 117.5 | 168.2 | 1.7 | 0 | 0 | 0 | 1.7 | 0.012 | 0.102 | 56.4 | 1.4315
交流220kV | 2008-06-30 | 2012-12-05 | 4.4356 | 20.5 | 379.2 | 1302.7 | 6.6 | 0.5 | 0.9 | 0 | 8 | 0 | 0 | 0 | 3.4354
交流220kV | 2008-06-30 | 2012-12-05 | 4.4356 | 20.6 | 362.9 | 865.6 | 6.1 | 0.4 | 0.8 | 0 | 7.3 | 0 | 0 | 0 | 2.3852
交流220kV | 2008-09-12 | 2013-02-20 | 4.4438 | 58 | 84 | 349 | 3 | 1 | 1 | 0 | 5 | 0 | 0 | 0 | 4.1548
交流220kV | 2007-02-14 | 2011-07-25 | 4.4438 | 12.85 | 228.47 | 771.58 | 8.92 | 0.74 | 0.65 | 0 | 10.31 | 0.003 | 0.002 | 60 | 3.3772
交流220kV | 2008-12-26 | 2013-06-06 | 4.4466 | 13.8 | 269.6 | 1432.9 | 4.4 | 0.7 | 0.6 | 0 | 5.7 | 0.016 | 0 | 68.3 | 5.3149
交流220kV | 2008-12-26 | 2013-06-06 | 4.4466 | 13.5 | 380.9 | 1600.8 | 6.3 | 0.6 | 0.7 | 0 | 7.6 | 0.021 | 0 | 70.1 | 4.2027
交流220kV | 2009-06-21 | 2013-12-04 | 4.4575 | 8.1 | 389.5 | 1307.6 | 5.9 | 1 | 0.9 | 0 | 7.8 | 0 | 0 | 0 | 3.3571
交流220kV | 2007-06-18 | 2011-12-02 | 4.4603 | 12 | 338 | 715 | 7 | 0 | 1 | 0 | 8 | 0 | 0 | 0 | 2.1154
交流220kV | 2008-06-26 | 2012-12-10 | 4.4603 | 1.67 | 338.86 | 824.97 | 6.69 | 0 | 0 | 0 | 6.69 | 0.011 | 0 | 0 | 2.4345
220 | 2008-10-01 | 2013-03-20 | 4.4685 | 3.1 | 75.7 | 772.2 | 1.94 | 0.45 | 1.6 | 0 | 3.99 | 0.108 | 0.12 | 57 | 10.2008
交流220kV | 2009-04-30 | 2013-10-17 | 4.4685 | 31 | 118 | 1495 | 121 | 97 | 41 | 0.1 | 259.1 | 0.026 | 0.004 | 66 | 12.6695
交流220kV | 2008-03-31 | 2012-09-25 | 4.4904 | 16.7 | 472.2 | 561.6 | 6.5 | 0 | 1.2 | 0.1 | 7.8 | 0.012 | 0.065 | 58.2 | 1.1893
交流220kV | 2008-03-31 | 2012-09-25 | 4.4904 | 19.7 | 449.2 | 501.6 | 5.8 | 0 | 0 | 0.1 | 5.9 | 0.012 | 0.067 | 54.2 | 1.1167
交流220kV | 2008-03-31 | 2012-09-25 | 4.4904 | 23.1 | 557.4 | 554.1 | 6.5 | 0 | 0.8 | 0.1 | 7.4 | 0.012 | 0.062 | 54.8 | 0.99408
交流220kV | 2008-06-28 | 2012-12-26 | 4.4986 | 16.56 | 412.69 | 2602.01 | 7.42 | 0.95 | 1.66 | 0 | 10.03 | 0 | 0 | 0 | 6.305
交流220kV | 2008-12-19 | 2013-06-20 | 4.5041 | 15.6 | 667 | 3244 | 7.9 | 2.4 | 1.6 | 0 | 11.9 | 0 | 0 | 0 | 4.8636
交流220kV | 2008-10-09 | 2013-04-10 | 4.5041 | 6 | 68 | 284 | 1 | 0 | 0 | 0 | 1 | 0.016 | 0.098 | 58 | 4.1765
交流220kV | 2007-09-20 | 2012-03-22 | 4.5068 | 4.85 | 222.24 | 937.43 | 6.62 | 1.33 | 1.57 | 0 | 9.52 | 0.018 | 0.034 | 58 | 4.2181
交流220kV | 2008-06-02 | 2012-12-05 | 4.5123 | 53.9 | 324 | 1400.4 | 5.6 | 1.5 | 1 | 0 | 8.1 | 0 | 0 | 0 | 4.3222
交流220kV | 2008-01-08 | 2012-07-12 | 4.5123 | 22.7 | 274.71 | 1211.97 | 139.38 | 201.3 | 46.59 | 0.2 | 387.47 | 0.013 | 0.089 | 54 | 4.4118
交流220kV | 2008-05-31 | 2012-12-04 | 4.5151 | 50.7 | 309.9 | 1373.2 | 5.2 | 1 | 1.1 | 0 | 7.3 | 0 | 0 | 0 | 4.4311
交流220kV | 2007-11-10 | 2012-05-16 | 4.5178 | 112.5 | 808.3 | 4404.7 | 8.9 | 1.7 | 1.6 | 0 | 12.2 | 0.008 | 0.03 | 54.6 | 5.4493
交流220kV | 2007-06-15 | 2011-12-22 | 4.5233 | 18.76 | 813.93 | 1609.34 | 8.66 | 1.46 | 1.24 | 0 | 11.36 | 0 | 0 | 0 | 1.9772
交流220kV | 2007-10-31 | 2012-05-10 | 4.5288 | 17.21 | 202.73 | 1233.22 | 4.49 | 0.65 | 0.63 | 0 | 5.77 | 0.018 | 0.001 | 56.4 | 6.0831
交流220kV | 2007-06-18 | 2011-12-28 | 4.5315 | 9 | 409 | 860 | 8 | 3 | 5 | 0 | 16 | 0 | 0 | 0 | 2.1027
交流220kV | 2007-10-30 | 2012-05-11 | 4.5342 | 4.18 | 230.88 | 657.46 | 10.1 | 0 | 1.53 | 0 | 11.63 | 0.012 | 0 | 0 | 2.8476
交流220kV | 2008-05-31 | 2012-12-13 | 4.5397 | 6.85 | 365.17 | 600.07 | 5 | 0.43 | 1.24 | 0.07 | 6.74 | 0.002 | 0.1 | 41 | 1.6433
交流220kV | 2008-05-31 | 2012-12-13 | 4.5397 | 7.21 | 510.22 | 901.21 | 7.07 | 0.56 | 2.5 | 0 | 10.13 | 0.001 | 0.1 | 42 | 1.7663
交流220kV | 2008-05-23 | 2012-12-05 | 4.5397 | 14.1 | 385.4 | 1000.8 | 6 | 0.7 | 0.7 | 0 | 7.4 | 0 | 0 | 0 | 2.5968
交流220kV | 2008-06-27 | 2013-01-14 | 4.5534 | 167.12 | 579.93 | 1107.19 | 6.88 | 1.15 | 2.11 | 0 | 10.14 | 0.004 | 0.001 | 52 | 1.9092
220 | 2007-08-17 | 2012-03-07 | 4.5589 | 68.15 | 169.09 | 1967.52 | 7.74 | 0.65 | 1.65 | 0 | 10.04 | 0.011 | 0.142 | 60 | 11.6359
交流220kV | 2009-08-31 | 2014-03-24 | 4.5644 | 91.63 | 141.54 | 485.05 | 20.65 | 4.61 | 3.07 | 0 | 28.33 | 0.007 | 0.001 | 59.7 | 3.4269
交流220kV | 2009-08-31 | 2014-03-24 | 4.5644 | 121.22 | 45.83 | 342.64 | 11.59 | 2.04 | 3.1 | 0 | 16.73 | 0.007 | 0.001 | 59.7 | 7.4763
交流220kV | 2008-10-26 | 2013-05-24 | 4.5781 | 30.4 | 456 | 1290.4 | 7.1 | 0.3 | 0.5 | 0 | 7.9 | 0.04 | 0.08 | 54.2 | 2.8298
交流220kV | 2007-07-28 | 2012-02-23 | 4.5781 | 145.06 | 817.12 | 2853.85 | 12.5 | 0.83 | 2.03 | 0 | 15.36 | 0.021 | 0.002 | 65.6 | 3.4926
220 | 2007-08-06 | 2012-03-07 | 4.589 | 48.59 | 201.15 | 1272.32 | 7.06 | 0.63 | 1.46 | 0 | 9.15 | 0.009 | 0.085 | 59 | 6.3252
220 | 2008-12-27 | 2013-07-31 | 4.5945 | 33.36 | 271.64 | 658.08 | 5.29 | 0.82 | 1.4 | 0.11 | 7.62 | 0.007 | 0.001 | 58 | 2.4226
220 | 2008-12-27 | 2013-08-01 | 4.5973 | 33.36 | 272 | 658 | 5.29 | 0.82 | 1.4 | 0.11 | 7.62 | 0.007 | 0.001 | 58 | 2.4191
交流220kV | 2007-07-11 | 2012-02-14 | 4.6 | 45.64 | 464.82 | 459.42 | 36.77 | 0.73 | 5.03 | 0 | 42.53 | 0.009 | 0.03 | 55.6 | 0.98838
交流220kV | 2007-07-28 | 2012-03-02 | 4.6 | 39.39 | 240.27 | 749.96 | 4.62 | 0.54 | 0.88 | 0 | 6.04 | 0.018 | 0.005 | 62.9 | 3.1213
交流220kV | 2008-12-05 | 2013-07-11 | 4.6 | 35 | 46 | 241 | 4.85 | 0.56 | 1.33 | 0 | 6.74 | 0.002 | 0.001 | 74 | 5.2391
交流220kV | 2008-12-05 | 2013-07-11 | 4.6 | 42 | 31 | 246 | 4.28 | 0.72 | 1.1 | 0 | 6.1 | 0.002 | 0.001 | 74 | 7.9355
交流220kV | 2008-04-25 | 2012-12-04 | 4.6137 | 5.4 | 209.55 | 1058.92 | 5.29 | 0.71 | 0.58 | 0 | 6.58 | 0.008 | 0.003 | 60 | 5.0533
交流220kV | 2007-09-13 | 2012-04-24 | 4.6164 | 7.5 | 762.2 | 3347.9 | 5.5 | 13.4 | 0 | 0 | 18.9 | 0.029 | 0 | 50 | 4.3924
交流220kV | 2007-09-13 | 2012-04-24 | 4.6164 | 15.4 | 694.1 | 4455.4 | 8.7 | 28.9 | 1.8 | 0 | 39.4 | 0.027 | 0 | 50 | 6.419
交流220kV | 2009-07-03 | 2014-02-13 | 4.6192 | 5.2 | 139.7 | 1322.4 | 3.9 | 0.7 | 1 | 0 | 5.6 | 0.011 | 0.076 | 64.9 | 9.466
交流220kV | 2007-09-07 | 2012-04-20 | 4.6219 | 20.12 | 898.72 | 1658.69 | 23.7 | 3.6 | 3.45 | 0 | 30.75 | 0.007 | 0.001 | 55 | 1.8456
交流220kV | 2008-04-30 | 2012-12-13 | 4.6247 | 27.7 | 256.3 | 1814.4 | 5.1 | 0.5 | 1.1 | 0 | 6.7 | 4.5 | 0 | 0 | 7.0792
交流220kV | 2008-04-30 | 2012-12-13 | 4.6247 | 21.2 | 270.7 | 1722.3 | 5.5 | 0.6 | 1.4 | 0 | 7.5 | 0 | 0 | 0 | 6.3624
交流220kV | 2007-07-24 | 2012-03-07 | 4.6247 | 22.75 | 397.36 | 930.21 | 6.91 | 1.17 | 0.67 | 0 | 8.75 | 0.007 | 0.126 | 50.4 | 2.341
交流220kV | 2007-10-23 | 2012-06-08 | 4.6301 | 6.77 | 1055.67 | 2902.47 | 11.83 | 2.81 | 1.46 | 0.12 | 16.22 | 0.007 | 0.257 | 0 | 2.7494
交流220kV | 2008-10-20 | 2013-06-06 | 4.6301 | 9.56 | 551.59 | 1723.79 | 7.71 | 0.35 | 0.71 | 0 | 8.77 | 0.001 | 0.012 | 71.2 | 3.1251
交流220kV | 2007-09-04 | 2012-04-20 | 4.6301 | 15.81 | 732.01 | 1016.23 | 18.54 | 1.39 | 3.21 | 0 | 23.14 | 0.006 | 0.001 | 55 | 1.3883
交流220kV | 2007-04-30 | 2011-12-16 | 4.6329 | 10.7 | 583.4 | 2287 | 7 | 2.8 | 1.9 | 0 | 11.7 | 0 | 0 | 0 | 3.9201
交流220kV | 2007-09-02 | 2012-04-20 | 4.6356 | 31.58 | 545.89 | 870.49 | 12.49 | 0.82 | 2.15 | 0 | 15.46 | 0.005 | 0.001 | 54 | 1.5946
交流220kV | 2008-07-26 | 2013-03-14 | 4.6356 | 4 | 60.9 | 508.5 | 1.6 | 0.3 | 0.3 | 0 | 2.2 | 0.006 | 0.065 | 57.2 | 8.3498
交流220kV | 2008-07-26 | 2013-03-14 | 4.6356 | 6.5 | 178.7 | 814.2 | 4.7 | 2 | 1 | 0 | 7.7 | 0.007 | 0.055 | 54.7 | 4.5562
交流220kV | 2007-04-28 | 2011-12-17 | 4.6411 | 9.23 | 404.95 | 4574.12 | 10.27 | 2.05 | 1.56 | 0 | 13.88 | 0 | 0 | 0 | 11.2955
交流220kV | 2007-04-29 | 2011-12-19 | 4.6438 | 6.63 | 467.37 | 855.82 | 6.7 | 1.53 | 1.47 | 0.07 | 9.77 | 0.003 | 0.02 | 44 | 1.8311
交流220kV | 2008-11-09 | 2013-07-01 | 4.6438 | 19.44 | 917.64 | 4472.04 | 20.98 | 1.97 | 2.69 | 0 | 25.64 | 0.01 | 0.167 | 52.8 | 4.8734
交流220kV | 2007-04-30 | 2011-12-22 | 4.6493 | 114.36 | 169.51 | 1796.66 | 17.72 | 5.42 | 11.05 | 0.28 | 34.47 | 0 | 0 | 44.3 | 10.5991
交流220kV | 2009-07-05 | 2014-02-26 | 4.6493 | 8.5 | 365.2 | 1303.5 | 5.4 | 0.5 | 0.6 | 0 | 6.5 | 0.01 | 0.052 | 56 | 3.5693
交流220kV | 2009-07-03 | 2014-02-26 | 4.6548 | 11.7 | 414.3 | 1443.4 | 4.9 | 0.9 | 0.8 | 0 | 6.6 | 0.011 | 0.05 | 54 | 3.4839
交流220kV | 2009-07-02 | 2014-03-02 | 4.6685 | 17.31 | 304.68 | 2396.14 | 16.21 | 5.49 | 6.35 | 0 | 28.05 | 0.003 | 0.05 | 49.6 | 7.8644
交流220kV | 2007-01-25 | 2011-09-29 | 4.6795 | 108.91 | 113.06 | 941.39 | 4.26 | 0.69 | 1.03 | 0 | 5.98 | 0.003 | 0.02 | 51 | 8.3265
交流220kV | 2008-01-07 | 2012-09-10 | 4.6795 | 16.32 | 368.29 | 1425.61 | 6.12 | 0.88 | 0.61 | 0 | 7.61 | 0.012 | 0.062 | 58.3 | 3.8709
交流220kV | 2008-01-07 | 2012-09-10 | 4.6795 | 16.32 | 442.03 | 1283.05 | 6.31 | 1.83 | 1.59 | 0 | 9.73 | 0.012 | 0.074 | 57.3 | 2.9026
交流220kV | 2008-07-03 | 2013-03-08 | 4.6822 | 12 | 237 | 906 | 7.71 | 1.54 | 1.58 | 0 | 10.83 | 0.021 | 0.052 | 51.4 | 3.8228
交流220kV | 2008-07-03 | 2013-03-08 | 4.6822 | 10 | 163 | 208 | 31.06 | 1.27 | 1.11 | 0 | 33.44 | 0.02 | 0.072 | 51.2 | 1.2761
交流220kV | 2009-02-26 | 2013-11-01 | 4.6822 | 12.29 | 510.53 | 2020.93 | 5.01 | 1.12 | 0.98 | 0 | 7.11 | 0.011 | 0.015 | 62 | 3.9585
交流220kV | 2007-04-09 | 2011-12-16 | 4.6904 | 20.4 | 526.5 | 1124.5 | 11.8 | 0.5 | 0.8 | 0 | 13.1 | 0 | 0 | 0 | 2.1358
交流220kV | 2008-03-28 | 2012-12-04 | 4.6904 | 4.03 | 218.22 | 1110.04 | 4.35 | 0.76 | 0.41 | 0 | 5.52 | 0.009 | 0.002 | 61 | 5.0868
交流220kV | 2007-10-27 | 2012-07-06 | 4.6959 | 21.69 | 231.59 | 391.78 | 3.1 | 0.46 | 0.77 | 0 | 4.33 | 0 | 0 | 47.7 | 1.6917
交流220kV | 2007-06-29 | 2012-03-09 | 4.6986 | 26.92 | 581.4 | 3415.6 | 9.5 | 0.56 | 1.32 | 0 | 11.38 | 0.008 | 0.062 | 53 | 5.8748
交流220kV | 2007-06-29 | 2012-03-09 | 4.6986 | 19.27 | 755.02 | 3830.98 | 10.79 | 0.73 | 1.59 | 0 | 13.11 | 0.012 | 0.981 | 51.9 | 5.074
交流220kV | 2009-06-25 | 2014-03-07 | 4.7014 | 7 | 482 | 2240 | 5.08 | 1.05 | 0.88 | 0 | 7.01 | 0.025 | 0.382 | 50 | 4.6473
交流220kV | 2006-12-27 | 2011-09-16 | 4.7233 | 9 | 131 | 383 | 6.6 | 0.9 | 3.6 | 0 | 11.1 | 0.061 | 0.385 | 65 | 2.9237
交流220kV | 2009-01-19 | 2013-10-11 | 4.7288 | 15.54 | 762.47 | 1602.8 | 24.44 | 1.21 | 2.26 | 0 | 27.91 | 0.006 | 0.326 | 57.7 | 2.1021
交流220kV | 2009-01-19 | 2013-10-11 | 4.7288 | 9.03 | 482.62 | 2117.06 | 7.63 | 0.52 | 2.01 | 0 | 10.16 | 0.009 | 0.059 | 60.4 | 4.3866
交流220kV | 2007-11-28 | 2012-08-21 | 4.7342 | 22.8 | 606.7 | 1068 | 8.2 | 3 | 0.6 | 0 | 11.8 | 0.012 | 0.075 | 56.9 | 1.7603
交流220kV | 2007-11-28 | 2012-08-24 | 4.7425 | 17.3 | 315.4 | 681.2 | 5.2 | 0.4 | 0.3 | 0.1 | 6 | 0.012 | 0.074 | 58.6 | 2.1598
交流220kV | 2008-09-27 | 2013-06-25 | 4.7452 | 8.5 | 239.9 | 1709.1 | 4.2 | 1.1 | 0.8 | 0 | 6.1 | 0.02 | 0 | 62.3 | 7.1242
交流220kV | 2008-09-27 | 2013-06-25 | 4.7452 | 10.9 | 255.5 | 1705.9 | 4.3 | 1 | 1.1 | 0 | 6.4 | 0.021 | 0 | 62.3 | 6.6767
220 | 2009-03-06 | 2013-12-05 | 4.7534 | 17.26 | 267.98 | 1399.48 | 5.33 | 0.55 | 0.59 | 0 | 6.47 | 0.009 | 0.074 | 62.4 | 5.2223
交流220kV | 2008-06-30 | 2013-04-01 | 4.7562 | 15.9 | 918.5 | 4000.8 | 9.2 | 0.7 | 1.4 | 0 | 11.3 | 0.014 | 0.053 | 57.3 | 4.3558
交流220kV | 2008-05-21 | 2013-02-23 | 4.7644 | 6.21 | 201.51 | 871.46 | 3.45 | 0.66 | 1.39 | 0 | 5.5 | 0.02 | 0.19 | 55 | 4.3246
交流220kV | 2007-07-10 | 2012-04-16 | 4.7726 | 2 | 580 | 1637 | 7.77 | 2.05 | 2.85 | 0 | 12.67 | 0.004 | 0.06 | 60 | 2.8224
交流220kV | 2006-12-21 | 2011-09-29 | 4.7753 | 16 | 577 | 4108 | 8.8 | 4 | 3.4 | 0.2 | 16.4 | 0.064 | 0.034 | 61 | 7.1196
交流220kV | 2009-06-15 | 2014-03-26 | 4.7808 | 35.76 | 410.48 | 628.91 | 5.33 | 0.67 | 0.93 | 0 | 6.93 | 0.011 | 0.001 | 59.2 | 1.5321
交流220kV | 2006-12-06 | 2011-09-16 | 4.7808 | 13 | 175 | 476 | 10 | 0.7 | 1.2 | 0 | 11.9 | 0.056 | 1.285 | 72 | 2.72
交流220kV | 2009-01-23 | 2013-11-05 | 4.7863 | 92.44 | 175.51 | 397.29 | 6.25 | 0.51 | 0.93 | 0 | 7.69 | 0.025 | 0.024 | 61 | 2.2636
交流220kV | 2009-01-23 | 2013-11-05 | 4.7863 | 263.58 | 134.36 | 319.37 | 15.15 | 0.36 | 2.14 | 0 | 17.65 | 0.014 | 0.051 | 50 | 2.377
交流220kV | 2006-12-03 | 2011-09-15 | 4.7863 | 15 | 576 | 2786 | 6.7 | 1.3 | 2.1 | 0.2 | 10.3 | 0.004 | 0.005 | 72.7 | 4.8368
交流220kV | 2007-06-15 | 2012-03-28 | 4.789 | 12.94 | 754.04 | 1594.21 | 9.03 | 2.31 | 1.39 | 0 | 12.73 | 0 | 0.003 | 65.6 | 2.1142
交流220kV | 2006-06-28 | 2011-04-12 | 4.7918 | 11 | 419 | 1885 | 7.7 | 0.4 | 1.5 | 0 | 9.6 | 0.009 | 0.002 | 52 | 4.4988
交流220kV | 2007-07-20 | 2012-05-03 | 4.7918 | 17.55 | 1097.86 | 4937.47 | 8.34 | 2.97 | 1.29 | 0 | 12.6 | 0.008 | 0.11 | 55 | 4.4974
220 | 2009-05-11 | 2014-02-26 | 4.8 | 1.07 | 24.76 | 542.33 | 1.09 | 0.32 | 0.24 | 1.83 | 3.48 | 0.012 | 0.179 | 48.8 | 21.9035
交流220kV | 2008-06-30 | 2013-04-18 | 4.8027 | 24.9 | 557.9 | 1762.4 | 9.3 | 0.7 | 1.1 | 0 | 11.1 | 0.012 | 0 | 65.5 | 3.159
交流220kV | 2008-06-30 | 2013-04-18 | 4.8027 | 19.7 | 399.4 | 880.5 | 6.5 | 0.4 | 0.8 | 0 | 7.7 | 0.009 | 0 | 63.3 | 2.2046
交流220kV | 2008-02-15 | 2012-12-03 | 4.8027 | 73.4 | 175.84 | 925.01 | 6.15 | 0.53 | 1.13 | 0 | 7.81 | 0.02 | 0.45 | 53 | 5.2605
交流220kV | 2006-12-10 | 2011-09-29 | 4.8055 | 36 | 527 | 4567 | 9.9 | 0.8 | 1.4 | 0.1 | 12.2 | 0.051 | 0.001 | 54.4 | 8.666
交流220kV | 2007-08-25 10:00 | 2012-06-14 | 4.8071 | 8 | 126 | 1810 | 5.75 | 1.67 | 1.76 | 0 | 9.18 | 0.005 | 0.07 | 60 | 14.3651
交流220kV | 2008-09-12 | 2013-07-03 | 4.8082 | 10 | 58 | 470 | 2 | 0 | 0 | 0 | 2 | 0.051 | 0.084 | 53 | 8.1034
交流220kV | 2008-05-30 | 2013-03-22 | 4.8137 | 17 | 239 | 462 | 35.82 | 0.76 | 2.87 | 0 | 39.45 | 0.001 | 0.3 | 44.8 | 1.9331
交流220kV | 2008-05-20 | 2013-03-12 | 4.8137 | 59.39 | 371.42 | 775.78 | 5.58 | 0.52 | 2.09 | 0 | 8.19 | 0.008 | 0.01 | 52 | 2.0887
220 | 2008-05-09 | 2013-03-04 | 4.8219 | 21.76 | 135.71 | 639.3 | 4.98 | 0.46 | 1.5 | 0 | 6.94 | 0.006 | 0.07 | 60 | 4.7108
220 | 2008-05-09 | 2013-03-04 | 4.8219 | 27.35 | 108.74 | 496.94 | 4.51 | 0.46 | 1.27 | 0.08 | 6.32 | 0.007 | 0.127 | 57 | 4.57
交流220kV | 2007-09-22 | 2012-07-17 | 4.8219 | 35.78 | 361.83 | 687.32 | 3.1 | 0.49 | 0.49 | 0 | 4.08 | 0 | 0 | 56.2 | 1.8996
交流220kV | 2007-09-22 | 2012-07-17 | 4.8219 | 33.83 | 425.83 | 798.3 | 3.74 | 0.59 | 1.09 | 0 | 5.42 | 0 | 0 | 52.8 | 1.8747
交流220kV | 2006-12-28 | 2011-10-24 | 4.8247 | 69.42 | 181.63 | 2551.34 | 5.76 | 1.88 | 1.89 | 0 | 9.53 | 0 | 0 | 0 | 14.0469
交流220kV | 2008-10-26 | 2013-08-23 | 4.8274 | 41.4 | 457.2 | 1425.2 | 6.6 | 0.4 | 0.8 | 0 | 7.8 | 0 | 0 | 0 | 3.1172
交流220kV | 2008-03-19 | 2013-01-14 | 4.8274 | 63.99 | 462.57 | 1116.27 | 6.84 | 0.69 | 2.33 | 0 | 9.86 | 0.003 | 0.003 | 52 | 2.4132
交流220kV | 2006-11-30 | 2011-09-28 | 4.8301 | 8.1 | 152 | 672 | 4.92 | 0.84 | 1.69 | 0 | 7.45 | 0.03 | 0.071 | 50.2 | 4.4211
220 | 2008-06-30 | 2013-05-03 | 4.8438 | 37.17 | 292.72 | 1509.2 | 5.48 | 4.43 | 5.48 | 0.27 | 15.66 | 0.014 | 0.081 | 61.5 | 5.1558
交流220kV | 2004-04-23 | 2009-02-27 | 4.8521 | 2 | 193 | 1429.7 | 4.4 | 0.6 | 0.8 | 0 | 5.8 | 0.003 | 0.176 | 53.2 | 7.4078
交流220kV | 2008-02-04 | 2012-12-11 | 4.8548 | 18.4 | 456.8 | 2016.1 | 8.9 | 1.1 | 1.5 | 0 | 11.5 | 0 | 0 | 0 | 4.4135
交流220kV | 2007-06-15 | 2012-04-25 | 4.8658 | 15.69 | 788.25 | 1593.21 | 9.06 | 2.31 | 2.4 | 0 | 13.77 | 0 | 0 | 51 | 2.0212
交流220kV | 2008-12-21 | 2013-11-05 | 4.8767 | 13.13 | 181.69 | 354.82 | 3.23 | 0.38 | 0.37 | 0 | 3.98 | 0.011 | 0.047 | 56 | 1.9529
交流220kV | 2008-12-21 | 2013-11-05 | 4.8767 | 13.07 | 195.35 | 342.2 | 3 | 0.36 | 0.1 | 0 | 3.46 | 0.009 | 0.033 | 63 | 1.7517
交流220kV | 2009-04-14 | 2014-02-28 | 4.8795 | 10.81 | 324.58 | 766.72 | 1.76 | 0.29 | 1.07 | 0 | 3.12 | 0.004 | 0.03 | 62.4 | 2.3622
交流220kV | 2009-04-14 | 2014-02-28 | 4.8795 | 8.5 | 251.94 | 541.75 | 4.85 | 0.44 | 0.48 | 0 | 5.77 | 0.004 | 0.034 | 57.6 | 2.1503
220 | 2008-06-15 | 2013-05-03 | 4.8849 | 35.22 | 211.43 | 1101.51 | 4.33 | 1 | 1.85 | 0 | 7.18 | 0.012 | 0.102 | 60.7 | 5.2098
220 | 2009-04-22 | 2014-03-12 | 4.8904 | 11.98 | 173.11 | 1125.48 | 4.45 | 0.59 | 0.57 | 0 | 5.61 | 0.014 | 0.18 | 52.8 | 6.5015
交流220kV | 2008-04-30 | 2013-03-21 | 4.8932 | 15.2 | 229.4 | 1472.9 | 5 | 0.5 | 1.2 | 0 | 6.7 | 0.012 | 0 | 72.7 | 6.4207
交流220kV | 2008-04-30 | 2013-03-21 | 4.8932 | 13.7 | 253.5 | 1318.6 | 5.2 | 0.6 | 1.2 | 0 | 7 | 0.01 | 0 | 64 | 5.2016
交流220kV | 2005-04-27 | 2010-03-18 | 4.8932 | 30 | 282 | 203 | 14.5 | 1.02 | 2.97 | 0.05 | 18.54 | 0.001 | 0.11 | 50 | 0.71986
交流220kV | 2008-04-30 | 2013-03-21 | 4.8932 | 20 | 367 | 676 | 44.93 | 0.98 | 4.38 | 0 | 50.29 | 0.003 | 0.05 | 50 | 1.842
交流220kV | 2007-01-25 | 2011-12-19 | 4.9014 | 100.18 | 153.85 | 1332.79 | 4.82 | 0.8 | 1.15 | 0.07 | 6.84 | 0.003 | 0.02 | 44 | 8.6629
交流220kV | 2005-04-03 | 2010-02-26 | 4.9041 | 20 | 338 | 363 | 19.93 | 4.79 | 4.93 | 0 | 29.65 | 0.021 | 0.003 | 50 | 1.074
交流220kV | 2008-06-19 | 2013-05-14 | 4.9041 | 15.1 | 411.5 | 1491.9 | 26.2 | 3.8 | 16.4 | 0 | 46.4 | 0.003 | 0.19 | 54 | 3.6255
交流220kV | 2009-01-15 | 2013-12-12 | 4.9096 | 6.4 | 264 | 1247.7 | 4.1 | 0 | 0 | 0 | 4.1 | 0 | 0 | 0 | 4.7261
交流220kV | 2006-11-01 | 2011-09-30 | 4.9151 | 12 | 312 | 1303 | 4.2 | 0.7 | 0.6 | 0 | 5.5 | 0.003 | 0.03 | 67.5 | 4.1763
交流220kV | 2007-04-29 | 2012-03-28 | 4.9178 | 8.24 | 424.57 | 765.35 | 6.74 | 3.24 | 3.03 | 0 | 13.01 | 0.002 | 0.2 | 48 | 1.8026
交流220kV | 2005-07-28 | 2010-06-28 | 4.9205 | 20 | 151 | 2224 | 7.8 | 0.5 | 1.5 | 0 | 9.8 | 0.05 | 0 | 45 | 14.7285
交流220kV | 2008-12-12 | 2013-11-12 | 4.9205 | 26.29 | 286.43 | 669.13 | 4.92 | 0.55 | 0.94 | 0 | 6.41 | 0.006 | 0.046 | 65 | 2.3361
交流220kV | 2008-12-12 | 2013-11-12 | 4.9205 | 74.29 | 334.98 | 684.96 | 8.42 | 0.53 | 1.67 | 0 | 10.62 | 0.009 | 0.074 | 67 | 2.0448
交流220kV | 2006-12-16 | 2011-11-18 | 4.926 | 10.03 | 312 | 757 | 3.64 | 0.75 | 0.23 | 0 | 4.62 | 0.031 | 0.075 | 52.6 | 2.4263
交流220kV | 2008-01-01 | 2012-12-04 | 4.9288 | 7.03 | 258.97 | 1117.3 | 5.02 | 0.65 | 0.61 | 0 | 6.28 | 0.009 | 0.004 | 60 | 4.3144
交流220kV | 2008-01-08 | 2012-12-12 | 4.9315 | 22.7 | 274.71 | 1211.97 | 139.38 | 201.3 | 46.59 | 0.2 | 387.47 | 0.013 | 0.089 | 54 | 4.4118
交流220kV | 2007-01-13 | 2011-12-19 | 4.9342 | 10.06 | 567.35 | 880.42 | 12.64 | 3.37 | 2.95 | 0 | 18.96 | 0.003 | 0.02 | 43 | 1.5518
交流220kV | 2009-03-15 | 2014-02-20 | 4.9397 | 46.9 | 45.76 | 370.63 | 37.29 | 40.57 | 10.68 | 0 | 88.54 | 0.006 | 0.06 | 64.4 | 8.0994
交流220kV | 2007-12-27 | 2012-12-05 | 4.9452 | 51.3 | 129.1 | 550.5 | 4 | 0.8 | 1.1 | 0 | 5.9 | 0 | 0 | 0 | 4.2641
交流220kV | 2008-12-26 | 2013-12-05 | 4.9452 | 14.2 | 328.3 | 803.3 | 4.8 | 0.7 | 0.6 | 0 | 6.1 | 0 | 0 | 0 | 2.4468
交流220kV | 2008-12-26 | 2013-12-05 | 4.9452 | 13.2 | 425.4 | 1208.3 | 7.2 | 0.8 | 0.9 | 0 | 8.9 | 0 | 0 | 0 | 2.8404
220 | 2008-04-11 | 2013-03-22 | 4.9479 | 1.52 | 509.56 | 1091.88 | 6.46 | 0.68 | 1.55 | 0 | 8.69 | 0.01 | 0.02 | 60 | 2.1428
交流220kV | 2008-06-26 | 2013-06-06 | 4.9479 | 4.5 | 451.2 | 1073.6 | 8.7 | 2.7 | 0 | 0 | 11.4 | 0.015 | 0.123 | 0 | 2.3794
交流220kV | 2008-06-28 | 2013-06-08 | 4.9479 | 14.06 | 541.65 | 3169.3 | 11.81 | 1.31 | 5 | 0 | 18.12 | 0 | 0 | 0 | 5.8512
交流220kV | 2007-01-07 | 2011-12-19 | 4.9507 | 9.93 | 482.24 | 3989.33 | 6.33 | 7.41 | 0 | 0.19 | 13.93 | 0.002 | 0.02 | 46 | 8.2725
交流220kV | 2007-04-30 | 2012-04-10 | 4.9507 | 60.73 | 203.43 | 1995.19 | 17.69 | 11.56 | 4.92 | 0 | 34.17 | 0 | 0 | 0 | 9.8077
交流220kV | 1999-04-13 | 2004-03-25 | 4.9534 | 10.1 | 1224.9 | 3052.3 | 7.6 | 31.8 | 5.8 | 0 | 45.2 | 0.006 | 0.709 | 50 | 2.4919
交流220kV | 2007-09-16 | 2012-08-28 | 4.9534 | 7.63 | 807.01 | 4458.76 | 10.25 | 3.35 | 1.87 | 0 | 15.47 | 0.011 | 0.003 | 62 | 5.525
220 | 2008-03-31 | 2013-03-14 | 4.9562 | 7.3 | 860.05 | 2389.71 | 9.15 | 1.04 | 0.96 | 0 | 11.15 | 0.013 | 0.072 | 57 | 2.7786
交流220kV | 2007-11-25 | 2012-11-07 | 4.9562 | 12.1 | 431 | 513.8 | 6.4 | 0.1 | 0.2 | 0 | 6.7 | 0.012 | 0.086 | 53.4 | 1.1921
交流220kV | 2007-11-25 | 2012-11-07 | 4.9562 | 12.5 | 377 | 452.5 | 6.4 | 0.2 | 0.4 | 0 | 7 | 0.012 | 0.078 | 55.1 | 1.2003
交流220kV | 2008-12-19 | 2013-12-03 | 4.9589 | 15.6 | 818 | 4232 | 9 | 3.1 | 1.9 | 0 | 14 | 0.04 | 0.66 | 49 | 5.1736
交流220kV | 2008-10-31 | 2013-10-17 | 4.9644 | 18 | 192 | 703 | 4.9 | 0.6 | 0.7 | 0.1 | 6.3 | 0.033 | 0.003 | 62 | 3.6615
交流220kV | 2006-12-24 | 2011-12-12 | 4.9699 | 19 | 166.3 | 742 | 6.7 | 0.53 | 0.63 | 0 | 7.86 | 0 | 0 | 0 | 4.4618
交流220kV | 2007-12-25 | 2012-12-13 | 4.9726 | 35 | 76 | 829 | 4.17 | 7.11 | 1.61 | 0 | 12.89 | 0.042 | 0.77 | 70.7 | 10.9079
交流220kV | 2007-06-18 | 2012-06-08 | 4.9781 | 8 | 391 | 1013 | 9 | 1 | 1 | 0 | 11 | 0.015 | 0.074 | 52 | 2.5908
交流220kV | 2006-03-11 | 2011-03-02 | 4.9781 | 7 | 592 | 841 | 6.9 | 1 | 0.9 | 0 | 8.8 | 0.004 | 0.004 | 48 | 1.4206
交流220kV | 2007-12-21 | 2012-12-13 | 4.9836 | 136.9 | 934.1 | 2900.5 | 10.2 | 0.6 | 1.4 | 0 | 12.2 | 0 | 0 | 0 | 3.1051
交流220kV | 2006-12-28 | 2011-12-22 | 4.9863 | 67.02 | 171.66 | 2334.84 | 5.67 | 2.02 | 1.07 | 0 | 8.76 | 0 | 0 | 0 | 13.6015
交流220kV | 2007-12-14 | 2012-12-07 | 4.9863 | 14.21 | 447.31 | 2576.22 | 4.62 | 0.76 | 0.89 | 0 | 6.27 | 0.002 | 0.1 | 40 | 5.7594
交流220kV | 2009-02-12 | 2014-02-11 | 5 | 8.6 | 164.3 | 1192.7 | 11.6 | 0.7 | 1.9 | 0 | 14.2 | 0.004 | 0.073 | 59.6 | 7.2593
交流220kV | 2007-09-25 | 2012-09-24 | 5.0027 | 12.11 | 332.81 | 1097.04 | 5.05 | 0.56 | 0.57 | 0 | 6.18 | 0.008 | 0.002 | 62 | 3.2963
交流220kV | 2007-09-25 | 2012-09-24 | 5.0027 | 17.15 | 466.04 | 1525.45 | 7.48 | 1.8 | 1.03 | 0 | 10.31 | 0.011 | 0.001 | 62 | 3.2732
交流220kV | 2006-12-13 | 2011-12-15 | 5.0082 | 40.2 | 137.9 | 1981.7 | 4.4 | 1 | 0.7 | 0 | 6.1 | 0 | 0 | 0 | 14.3706
交流220kV | 2007-09-13 | 2012-09-16 | 5.0137 | 9.7 | 650.5 | 3294.8 | 7 | 13.4 | 0 | 0 | 20.4 | 0.026 | 2.7 | 44 | 5.065
交流220kV | 2008-05-31 | 2013-06-05 | 5.0164 | 4 | 590 | 1125 | 8 | 1 | 3 | 0 | 12 | 0.001 | 0.1 | 45 | 1.9068
交流220kV | 2008-05-31 | 2013-06-05 | 5.0164 | 6 | 455 | 766 | 6 | 0 | 2 | 0 | 8 | 0.001 | 0.1 | 45 | 1.6835
交流220kV | 2005-08-12 | 2010-08-17 | 5.0164 | 17.21 | 582.34 | 1704.26 | 7.22 | 12.11 | 2.09 | 0 | 21.42 | 0.014 | 0.397 | 58 | 2.9266
交流220kV | 2008-04-02 | 2013-04-07 | 5.0164 | 26 | 426 | 1110 | 6.47 | 0.7 | 1.1 | 0 | 8.27 | 0.009 | 0.1 | 57 | 2.6056
交流220kV | 2006-09-10 | 2011-09-19 | 5.0274 | 63.62 | 72.9 | 2982.71 | 8.24 | 4.73 | 2.67 | 0 | 15.64 | 0 | 0 | 0 | 40.9151
交流220kV | 2006-12-09 | 2011-12-21 | 5.0356 | 5.61 | 629.44 | 990.71 | 6.48 | 4.29 | 1.48 | 0 | 12.25 | 0 | 0 | 0 | 1.574
交流220kV | 2008-03-01 | 2013-03-14 | 5.0384 | 3.8 | 346.8 | 2048.5 | 10.7 | 1 | 2.3 | 0 | 14 | 0.017 | 0.062 | 59.2 | 5.9069
交流220kV | 2009-03-22 | 2014-04-04 | 5.0384 | 122.44 | 416.24 | 935.08 | 8.22 | 1.29 | 2.46 | 0 | 11.97 | 0.062 | 0.104 | 48 | 2.2465
交流220kV | 2008-08-04 | 2013-08-19 | 5.0438 | 16.5 | 161.8 | 779.1 | 6.18 | 0.93 | 1.35 | 0 | 8.46 | 0.004 | 0.001 | 54 | 4.8152
交流220kV | 2008-06-02 | 2013-06-19 | 5.0493 | 38.7 | 275.4 | 2415.4 | 5.5 | 1.6 | 1.1 | 0 | 8.2 | 0.03 | 0 | 63.3 | 8.7705
交流220kV | 2006-10-10 | 2011-10-28 | 5.0521 | 10 | 813 | 2332 | 9.2 | 1.5 | 0.9 | 0 | 11.6 | 0.045 | 0.034 | 62 | 2.8684
交流220kV | 2006-10-10 | 2011-10-28 | 5.0521 | 56 | 228 | 892 | 13.1 | 1.7 | 0.8 | 0 | 15.6 | 0.048 | 0.034 | 65 | 3.9123
交流220kV | 2008-05-31 | 2013-06-19 | 5.0548 | 31.8 | 229.3 | 2149.6 | 4.6 | 1.2 | 1.1 | 0 | 6.9 | 0.023 | 0 | 62.6 | 9.3746
交流220kV | 2006-11-23 | 2011-12-13 | 5.0575 | 7.64 | 484.56 | 1909.75 | 8.1 | 7.71 | 1.66 | 0 | 17.47 | 0.012 | 0 | 0 | 3.9412
交流220kV | 2009-01-19 | 2014-02-13 | 5.0712 | 2.9 | 192.1 | 965.3 | 3.6 | 0.5 | 0.7 | 0 | 4.8 | 0.008 | 0.05 | 66 | 5.025
交流220kV | 2006-02-21 | 2011-03-19 | 5.074 | 18.28 | 1142.55 | 4414.62 | 8.04 | 1.16 | 1.43 | 0 | 10.63 | 0.014 | 0.002 | 55.4 | 3.8638
交流220kV | 2008-04-29 | 2013-05-27 | 5.0795 | 6.43 | 332.58 | 3893.65 | 9.68 | 1.58 | 1.32 | 0.3 | 12.88 | 0.006 | 0.001 | 60 | 11.7074
220 | 2008-06-29 | 2013-07-31 | 5.0904 | 8.66 | 317.47 | 1358.32 | 5.13 | 0.89 | 0.77 | 0 | 6.79 | 0.008 | 0.001 | 58 | 4.2786
交流220kV | 2007-11-10 | 2012-12-11 | 5.0904 | 111.8 | 883.8 | 4420.2 | 10.1 | 2.7 | 1.6 | 0 | 14.4 | 0 | 0 | 0 | 5.0014
交流220kV | 2006-04-08 | 2011-05-11 | 5.0932 | 11.44 | 347.69 | 2089.27 | 8.86 | 1 | 0.94 | 0.22 | 11.02 | 0.01 | 0.001 | 60 | 6.009
220 | 2008-06-25 | 2013-07-31 | 5.1014 | 12.08 | 627.58 | 1942.12 | 10.9 | 5.97 | 1.19 | 0 | 18.06 | 0.01 | 0.001 | 48 | 3.0946
220 | 2008-06-25 | 2013-08-01 | 5.1041 | 12.08 | 628 | 1942 | 10.9 | 5.97 | 1.19 | 0 | 18.06 | 0.01 | 0.001 | 48 | 3.0924
交流220kV | 2006-01-18 | 2011-02-28 | 5.1151 | 2.54 | 176.36 | 529.44 | 12.34 | 0 | 2.04 | 0 | 14.38 | 0.005 | 0.189 | 54.6 | 3.002
交流220kV | 2009-01-10 | 2014-02-20 | 5.1151 | 17.07 | 82.38 | 428.51 | 15.07 | 1.47 | 4.96 | 0 | 21.05 | 0.004 | 0.05 | 68 | 5.2016
交流220kV | 2007-10-19 | 2012-11-28 | 5.1151 | 34.9 | 544.05 | 1148.3 | 5.84 | 0.56 | 0.79 | 0 | 7.19 | 0.009 | 0.008 | 61.5 | 2.1107
交流220kV | 2007-10-30 | 2012-12-10 | 5.1178 | 2.66 | 209.41 | 623.77 | 8.82 | 0 | 0 | 0 | 8.82 | 0 | 0 | 0 | 2.9787
交流220kV | 2006-01-17 | 2011-02-28 | 5.1178 | 5.14 | 248.34 | 248.45 | 10.34 | 2.26 | 3.32 | 0 | 15.92 | 0.005 | 0.156 | 51.6 | 1.0004
交流220kV | 2007-10-23 | 2012-12-10 | 5.137 | 8.89 | 1330.83 | 2875.85 | 14.3 | 2.75 | 1.34 | 0.21 | 18.6 | 0 | 0 | 0 | 2.1609
交流220kV | 2008-10-20 | 2013-12-10 | 5.1425 | 10.67 | 643.35 | 1665.34 | 8.41 | 0.27 | 0.97 | 0 | 9.65 | 0 | 0 | 0 | 2.5885
交流220kV | 2008-07-21 | 2013-09-10 | 5.1425 | 12.34 | 785.7 | 1616.98 | 12.01 | 0.98 | 3.17 | 0 | 16.16 | 0.014 | 0.11 | 53 | 2.058
交流220kV | 2006-03-15 | 2011-05-06 | 5.1452 | 5.54 | 655.35 | 2063.88 | 8.48 | 2.06 | 2.1 | 0 | 12.64 | 0.009 | 0.001 | 56 | 3.1493
交流220kV | 2008-12-20 | 2014-02-11 | 5.1479 | 5.6 | 153.2 | 527.6 | 11.4 | 0.8 | 1 | 0 | 13.2 | 0.008 | 0.06 | 58.8 | 3.4439
交流220kV | 2009-01-18 | 2014-03-12 | 5.1479 | 3.9 | 107.4 | 370.8 | 2.3 | 0.3 | 0.4 | 0 | 3 | 0.009 | 0.068 | 52.4 | 3.4525
交流220kV | 2009-01-18 | 2014-03-12 | 5.1479 | 6.2 | 101 | 417.6 | 5.4 | 0.6 | 0.8 | 0 | 6.8 | 0.01 | 0.077 | 56.8 | 4.1347
交流220kV | 2006-06-02 | 2011-07-25 | 5.1479 | 4.49 | 117.33 | 561.22 | 5.06 | 0.45 | 0.54 | 0 | 6.05 | 0.005 | 0.001 | 60 | 4.7833
交流220kV | 2004-12-11 | 2010-02-04 | 5.1534 | 10 | 337.23 | 734.43 | 6.6 | 1.71 | 4.01 | 0 | 12.32 | 0.005 | 0.062 | 53 | 2.1778
220 | 2006-12-28 | 2012-02-22 | 5.1562 | 65.02 | 249.55 | 1839.52 | 6.85 | 0.8 | 1.32 | 0 | 8.97 | 0.016 | 0.158 | 54 | 7.3713
交流220kV | 2006-10-24 | 2011-12-19 | 5.1562 | 28.61 | 111.91 | 1892.4 | 4.09 | 0.61 | 0.89 | 0 | 5.59 | 0.003 | 0.02 | 44 | 16.91
交流220kV | 2007-01-30 | 2012-03-26 | 5.1562 | 6 | 417 | 2688 | 24.97 | 1.85 | 3.82 | 0 | 30.64 | 0.001 | 0.001 | 50 | 6.446
交流220kV | 2008-12-25 | 2014-02-20 | 5.1589 | 3.09 | 392 | 737.86 | 8.7 | 1.86 | 1.21 | 0 | 11.77 | 0.005 | 0.045 | 62.4 | 1.8823
交流220kV | 2007-10-27 | 2012-12-26 | 5.1699 | 19 | 241.04 | 360.6 | 2.56 | 0.38 | 0.57 | 0 | 3.51 | 0 | 0 | 0 | 1.496
交流220kV | 2007-04-30 | 2012-07-02 | 5.1781 | 94.4 | 205.2 | 2119.24 | 20.15 | 11.83 | 6.77 | 0 | 38.75 | 0 | 0 | 0 | 10.3277
交流220kV | 2007-04-28 | 2012-07-06 | 5.1945 | 15.65 | 359.41 | 2254.8 | 8.4 | 0.71 | 1.06 | 0 | 10.17 | 0 | 0.122 | 57.7 | 6.2736
交流220kV | 2008-09-27 | 2013-12-06 | 5.1945 | 10.4 | 272.4 | 1723.6 | 4.8 | 1.4 | 0.8 | 0 | 7 | 0 | 0 | 0 | 6.3275
交流220kV | 2008-09-27 | 2013-12-06 | 5.1945 | 11.1 | 288.6 | 1730.1 | 4.9 | 1 | 0.8 | 0 | 6.7 | 0 | 0 | 0 | 5.9948
220 | 2008-12-19 | 2014-03-03 | 5.2055 | 24.59 | 371.09 | 1968.33 | 27.95 | 17.05 | 7.53 | 0 | 52.53 | 0.039 | 0.099 | 58.5 | 5.3042
交流220kV | 2007-09-22 | 2012-12-04 | 5.2055 | 40.66 | 482.58 | 880.66 | 4.31 | 0.61 | 0.71 | 0 | 5.63 | 0 | 0 | 0 | 1.8249
交流220kV | 2007-09-22 | 2012-12-04 | 5.2055 | 32.61 | 464.38 | 804.57 | 4.19 | 0.64 | 0.89 | 0 | 5.72 | 0 | 0 | 0 | 1.7326
交流220kV | 2008-12-13 | 2014-03-03 | 5.2219 | 13.38 | 308.64 | 1300.57 | 4.54 | 3.22 | 3.87 | 0 | 11.63 | 0.006 | 0.03 | 41.6 | 4.2139
220 | 2007-01-08 | 2012-03-30 | 5.2274 | 53.76 | 94.05 | 576.38 | 6.93 | 6.47 | 1.64 | 0 | 15.04 | 0.008 | 0.001 | 60 | 6.1284
交流220kV | 2006-06-26 | 2011-09-16 | 5.2274 | 102.8 | 167.3 | 2756.8 | 53 | 52.9 | 18.3 | 0 | 124.2 | 0 | 0 | 0 | 16.4782
交流220kV | 2006-06-26 | 2011-09-16 | 5.2274 | 106.9 | 171.2 | 2796.5 | 54 | 53.4 | 18.7 | 0 | 126.1 | 0 | 0 | 0 | 16.3347
交流220kV | 2007-01-25 | 2012-04-16 | 5.2274 | 98.54 | 149.04 | 1274.63 | 5.37 | 1.63 | 2.14 | 0 | 9.14 | 0.002 | 0.2 | 49 | 8.5523
交流220kV | 2008-11-21 | 2014-02-13 | 5.2329 | 5.55 | 566.36 | 431.13 | 23.61 | 0.82 | 3.1 | 0 | 27.53 | 0.004 | 0.213 | 49.6 | 0.76123
220 | 2007-12-24 | 2013-03-21 | 5.2438 | 21.52 | 369.21 | 1665.04 | 7.92 | 0.99 | 5.73 | 0 | 14.64 | 0.014 | 0.038 | 58.2 | 4.5097
交流220kV | 2007-10-28 | 2013-01-24 | 5.2466 | 40 | 95 | 1288 | 3.76 | 1.56 | 0.99 | 0 | 6.31 | 0.039 | 0.022 | 70.5 | 13.5579
交流220kV | 2006-11-30 | 2012-02-28 | 5.2493 | 19.01 | 202.51 | 714.45 | 5.43 | 0.84 | 1.03 | 0.34 | 7.64 | 0.012 | 0.07 | 57.5 | 3.528
交流220kV | 2006-11-30 | 2012-02-28 | 5.2493 | 42.44 | 166.54 | 585.21 | 6 | 0.75 | 1.28 | 0.2 | 8.23 | 0.015 | 0.06 | 57 | 3.5139
交流220kV | 2006-12-28 | 2012-03-28 | 5.2521 | 63.32 | 163.58 | 2297.51 | 5.91 | 1.95 | 1.09 | 0 | 8.95 | 0 | 0 | 0 | 14.0452
交流220kV | 2006-07-21 | 2011-10-20 | 5.2521 | 24 | 178 | 1327 | 6 | 0.6 | 1.1 | 0 | 7.7 | 0.044 | 0.005 | 40.8 | 7.4551
交流220kV | 2006-09-04 | 2011-12-06 | 5.2575 | 7.5 | 307.4 | 1254 | 3.6 | 1 | 0.6 | 0 | 5.2 | 0 | 0 | 0 | 4.0794
交流220kV | 2006-09-10 | 2011-12-14 | 5.263 | 61.9 | 53.5 | 2534.46 | 7.64 | 4.13 | 2.69 | 0 | 14.46 | 0 | 0 | 0 | 47.3731
交流220kV | 2008-09-12 | 2013-12-17 | 5.2658 | 68 | 97 | 477 | 3 | 1 | 1 | 0 | 5 | 0 | 0 | 0 | 4.9175
交流220kV | 2006-01-06 11:08 | 2011-04-14 | 5.27 | 34 | 164 | 879 | 26.07 | 12.32 | 54.03 | 0 | 92.42 | 0.001 | 0.002 | 50 | 5.3598
交流220kV | 2008-11-29 | 2014-03-07 | 5.2712 | 71.15 | 337.34 | 952.82 | 6.1 | 1.1 | 1.19 | 0 | 8.39 | 0.011 | 0.096 | 67.5 | 2.8245
交流220kV | 2008-05-08 | 2013-08-16 | 5.2767 | 3998.68 | 477.81 | 3214.34 | 234.6 | 2.12 | 27.93 | 0 | 264.65 | 0.021 | 0.03 | 60 | 6.7272
交流220kV | 2007-04-19 | 2012-07-28 | 5.2795 | 1.73 | 6.3 | 209.3 | 0.38 | 0.04 | 0.14 | 0 | 0.56 | 0.01 | 0.19 | 52 | 33.2222
交流220kV | 2007-01-13 | 2012-04-25 | 5.2849 | 20.86 | 1092.68 | 1247.22 | 20.42 | 5.06 | 13.68 | 0 | 39.16 | 0.002 | 0.2 | 43 | 1.1414
交流220kV | 2008-12-07 | 2014-03-21 | 5.2877 | 4.8 | 299.84 | 539.5 | 5.46 | 0.91 | 0.48 | 0 | 6.85 | 0.005 | 0.056 | 58 | 1.7993
交流220kV | 2006-06-30 | 2011-10-14 | 5.2932 | 89 | 534 | 7231 | 9.8 | 1.1 | 2.7 | 0 | 13.6 | 0.015 | 0.001 | 72 | 13.5412
220 | 2008-11-30 | 2014-03-18 | 5.2986 | 13.09 | 202.18 | 691.55 | 3.81 | 0.43 | 1.17 | 0 | 5.41 | 0.044 | 0.001 | 60.1 | 3.4205
交流220kV | 2007-11-26 | 2013-03-13 | 5.2986 | 15.46 | 670.07 | 932.44 | 16.01 | 4.79 | 3.3 | 0 | 24.1 | 0.009 | 0.014 | 53.2 | 1.3916
交流220kV | 2007-01-07 | 2012-04-25 | 5.3014 | 36.57 | 4171.99 | 19985 | 36.05 | 10.16 | 8.3 | 0.54 | 55.05 | 0.003 | 0.2 | 43 | 4.7903
交流220kV | 2007-06-08 | 2012-09-24 | 5.3014 | 5.91 | 248.11 | 847.1 | 4.91 | 0.62 | 0.54 | 0 | 6.07 | 0.006 | 0.002 | 62 | 3.4142
交流220kV | 2007-06-08 | 2012-09-24 | 5.3014 | 8.92 | 437.66 | 1064.9 | 7.05 | 1.37 | 0.85 | 0 | 9.27 | 0.008 | 0.001 | 62 | 2.4332
交流220kV | 2008-06-05 | 2013-09-25 | 5.3096 | 11.97 | 505.59 | 2991.89 | 5.81 | 2.33 | 0.81 | 2.5 | 11.45 | 0 | 0.001 | 48 | 5.9176
交流220kV | 2008-07-15 | 2013-11-04 | 5.3096 | 17.08 | 349.01 | 619.89 | 5.61 | 0.33 | 0.63 | 0 | 6.57 | 0.012 | 0.024 | 70 | 1.7761
交流220kV | 2008-07-15 | 2013-11-04 | 5.3096 | 13.92 | 315.12 | 578.63 | 4.63 | 0.4 | 0.5 | 0 | 5.53 | 0.011 | 0.059 | 67 | 1.8362
交流220kV | 2007-09-20 | 2013-01-11 | 5.3151 | 4.58 | 235.6 | 1062.98 | 9.18 | 1.4 | 1.82 | 0 | 12.4 | 0.025 | 0.061 | 59 | 4.5118
220 | 2008-11-30 | 2014-03-28 | 5.326 | 11.3 | 215.66 | 750.76 | 3.27 | 0.6 | 0.39 | 0.04 | 4.3 | 0.036 | 0.001 | 47.6 | 3.4812
交流220kV | 2006-12-20 | 2012-04-16 | 5.326 | 5 | 97 | 431 | 2.05 | 1.35 | 0 | 0 | 3.4 | 0.003 | 0.16 | 58 | 4.4433
交流220kV | 2007-02-05 | 2012-06-02 | 5.326 | 2.9 | 97.1 | 1193.6 | 8.2 | 1.5 | 0.3 | 0 | 10 | 0.012 | 0.169 | 56 | 12.2925
交流220kV | 2007-12-20 | 2013-04-16 | 5.326 | 5.4 | 224.1 | 341.8 | 4.3 | 0.2 | 0.2 | 0 | 4.7 | 0.022 | 0.279 | 49.2 | 1.5252
交流220kV | 2008-11-04 | 2014-03-03 | 5.3288 | 16.69 | 282.47 | 1396.28 | 17.83 | 6.11 | 5.67 | 0 | 29.61 | 0.007 | 0.05 | 40.8 | 4.9431
交流220kV | 2006-06-28 | 2011-10-25 | 5.3288 | 9 | 482 | 2762 | 8.8 | 0.4 | 2.2 | 0 | 11.4 | 0.009 | 0.002 | 54 | 5.7303
交流220kV | 2005-09-19 | 2011-01-17 | 5.3315 | 4.15 | 970.3 | 2732.98 | 14.81 | 1.48 | 4.32 | 0 | 20.61 | 0.011 | 0.005 | 52.5 | 2.8166
交流220kV | 2008-06-12 | 2013-10-10 | 5.3315 | 3.74 | 351.09 | 1066.09 | 5.25 | 1.12 | 0.62 | 0 | 6.99 | 0.012 | 0.071 | 63.1 | 3.0365
交流220kV | 2008-05-08 | 2013-09-06 | 5.3342 | 2700.11 | 375.62 | 2811.92 | 180.53 | 1.71 | 24.44 | 0 | 206.68 | 0.004 | 0.19 | 69 | 7.4861
交流220kV | 2007-12-27 | 2013-04-28 | 5.3397 | 18.8 | 1427.5 | 3918.5 | 13 | 1.9 | 2.4 | 0 | 17.3 | 0.003 | 0.06 | 54.5 | 2.745
交流220kV | 2007-05-04 | 2012-09-03 | 5.3397 | 14.1 | 588.31 | 2224.26 | 10.84 | 3.5 | 1.38 | 0 | 15.72 | 0.008 | 0.003 | 62 | 3.7808
交流220kV | 2008-06-30 | 2013-11-01 | 5.3425 | 79 | 62 | 467 | 9.23 | 0.92 | 2.04 | 0.12 | 12.31 | 0.004 | 0.002 | 68 | 7.5323
交流220kV | 2007-04-29 | 2012-09-03 | 5.3534 | 12.3 | 654.25 | 1839.96 | 9.7 | 1.17 | 0.89 | 0 | 11.76 | 0.006 | 0.002 | 62 | 2.8123
交流220kV | 2008-06-28 | 2013-11-04 | 5.3562 | 9.8 | 405.19 | 974.61 | 6.27 | 0.46 | 1.1 | 0 | 7.83 | 0.011 | 0.017 | 71 | 2.4053
交流220kV | 2008-11-12 | 2014-03-21 | 5.3562 | 31 | 130 | 971 | 3.41 | 0.59 | 0.58 | 0 | 4.58 | 0.023 | 0.645 | 51 | 7.4692
交流220kV | 2008-11-12 | 2014-03-21 | 5.3562 | 33 | 148 | 850 | 3.28 | 0.81 | 0.55 | 0 | 4.64 | 0.023 | 0.602 | 50 | 5.7432
交流220kV | 2008-11-09 | 2014-03-20 | 5.3616 | 3 | 321 | 226 | 17.33 | 1.76 | 3.61 | 0 | 22.7 | 0.001 | 0.06 | 47.5 | 0.70405
交流220kV | 2007-06-29 | 2012-11-06 | 5.3616 | 20.1 | 692.1 | 2103.3 | 11.7 | 0 | 1.5 | 0 | 13.2 | 0.012 | 0.074 | 56.2 | 3.039
交流220kV | 2007-06-29 | 2012-11-06 | 5.3616 | 13.4 | 880.9 | 2294.7 | 13.7 | 0 | 3.4 | 0 | 17.1 | 0.012 | 0.073 | 54.6 | 2.6049
交流220kV | 2006-12-28 | 2012-05-08 | 5.3644 | 58.65 | 164.29 | 2338.29 | 5.87 | 1.79 | 0.97 | 0 | 8.63 | 0 | 0.089 | 56.7 | 14.2327
交流220kV | 2007-11-03 | 2013-03-14 | 5.3644 | 4 | 244.5 | 1220.5 | 11.2 | 1.1 | 1.8 | 0 | 14.1 | 0.018 | 0.051 | 58.6 | 4.9918
交流220kV | 2007-10-14 | 2013-02-23 | 5.3671 | 19.79 | 165.14 | 707.21 | 2.65 | 1 | 1.36 | 0 | 5.01 | 0.024 | 0.23 | 50 | 4.2825
交流220kV | 2008-02-04 | 2013-06-20 | 5.3781 | 20.2 | 504.6 | 3865.9 | 11.9 | 3.2 | 2.4 | 0 | 17.5 | 0.022 | 0 | 55.3 | 7.6613
交流220kV | 2007-08-06 | 2012-12-24 | 5.389 | 8.53 | 424.72 | 1248.77 | 6.94 | 1.64 | 0.55 | 0 | 9.13 | 0.006 | 0.002 | 62 | 2.9402
交流220kV | 2007-08-06 | 2012-12-24 | 5.389 | 11.82 | 398.66 | 1506.95 | 6.71 | 1.66 | 0.54 | 0.24 | 9.15 | 0.008 | 0.001 | 62 | 3.78
交流220kV | 2006-07-26 | 2011-12-15 | 5.3918 | 49.9 | 97.9 | 711.3 | 27.3 | 13.5 | 10.4 | 0 | 51.2 | 0 | 0 | 0 | 7.2656
交流220kV | 2005-12-30 | 2011-05-23 | 5.3973 | 16.09 | 270.76 | 744.05 | 4.97 | 0.69 | 0.61 | 0 | 6.27 | 0.01 | 0.001 | 60 | 2.748
交流220kV | 2006-12-28 | 2012-05-23 | 5.4055 | 20 | 129 | 1788 | 4.6 | 0.5 | 0 | 0 | 5.1 | 0.014 | 0.003 | 48 | 13.8605
交流220kV | 2007-12-25 | 2013-05-24 | 5.4164 | 101.64 | 439.23 | 4074.37 | 10.32 | 5.19 | 2.06 | 0 | 17.57 | 0.003 | 0.25 | 55 | 9.2762
交流220kV | 2006-11-23 | 2012-04-24 | 5.4219 | 7.06 | 534.63 | 2061.95 | 8.84 | 8.14 | 6.25 | 0 | 23.23 | 0.012 | 0 | 0 | 3.8568
交流220kV | 2007-12-14 | 2013-05-16 | 5.4247 | 7.31 | 359.09 | 2425.78 | 4.53 | 0.7 | 0.76 | 0 | 5.99 | 0.003 | 0.025 | 55 | 6.7554
交流220kV | 2007-01-06 | 2012-06-13 | 5.4384 | 2.73 | 145.3 | 674.95 | 12.54 | 0.86 | 11.36 | 0 | 24.76 | 0.001 | 0.321 | 62.8 | 4.6452
220 | 2008-06-20 | 2013-11-27 | 5.4411 | 5.54 | 1084.6 | 2701.16 | 12.56 | 0.98 | 2.71 | 0 | 16.25 | 0.008 | 0.054 | 58.8 | 2.4905
220 | 2008-10-01 | 2014-03-12 | 5.4466 | 2.93 | 58.82 | 748.85 | 1.51 | 0.3 | 0.13 | 0 | 1.94 | 0.018 | 0.16 | 56.6 | 12.7312
交流220kV | 2008-06-30 | 2013-12-11 | 5.4521 | 21.4 | 457.9 | 1768.6 | 7.5 | 7.5 | 1.1 | 0 | 16.1 | 0 | 0 | 0 | 3.8624
交流220kV | 2008-06-30 | 2013-12-11 | 5.4521 | 21.7 | 499.3 | 1932.2 | 8.4 | 0.7 | 1.2 | 0 | 10.3 | 0 | 0 | 0 | 3.8698
交流220kV | 2005-12-27 | 2011-06-09 | 5.4521 | 23 | 354 | 3105 | 6.8 | 1 | 2.2 | 0 | 10 | 0.007 | 0.005 | 44 | 8.7712
交流220kV | 2006-04-29 | 2011-10-10 | 5.4521 | 14 | 157 | 1099 | 6.5 | 0.7 | 3.5 | 0 | 10.7 | 0.05 | 0.002 | 61 | 7
交流220kV | 2006-07-08 | 2011-12-21 | 5.4575 | 4.9 | 58.19 | 163.07 | 4.55 | 3.73 | 0.6 | 0 | 8.88 | 0 | 0 | 0 | 2.8024
交流220kV | 2006-10-08 | 2012-03-22 | 5.4575 | 57.2 | 284.8 | 1976.6 | 6 | 0 | 0 | 0 | 6 | 0 | 0 | 0 | 6.9403
交流220kV | 2008-06-26 | 2013-12-11 | 5.463 | 2.51 | 462.36 | 981.07 | 9.22 | 2.17 | 0 | 0 | 11.39 | 0 | 0 | 0 | 2.1219
交流220kV | 2006-01-19 | 2011-07-06 | 5.463 | 8.16 | 1202.41 | 2789.01 | 13.59 | 1.64 | 2.84 | 0 | 18.07 | 0 | 0 | 0 | 2.3195
交流220kV | 2008-05-29 | 2013-11-13 | 5.463 | 5.11 | 470.55 | 1004.24 | 6.85 | 0.71 | 1.23 | 0 | 8.79 | 0.009 | 0.15 | 61 | 2.1342
交流220kV | 2007-03-20 | 2012-09-03 | 5.463 | 13.02 | 455.85 | 986.11 | 6.15 | 0.78 | 0.79 | 0 | 7.72 | 0.011 | 0.001 | 56 | 2.1632
交流220kV | 2006-06-26 | 2011-12-12 | 5.4658 | 94.5 | 162 | 2595.4 | 52.4 | 48.6 | 17.5 | 0 | 118.5 | 0 | 0 | 0 | 16.021
交流220kV | 2005-10-25 | 2011-04-12 | 5.4658 | 12.91 | 274.55 | 364.83 | 37 | 2.91 | 11.53 | 0 | 51.44 | 0.004 | 0.169 | 55.4 | 1.3288
交流220kV | 2006-06-02 | 2011-11-18 | 5.4658 | 15 | 678 | 2682 | 8.6 | 0.7 | 0.7 | 0.1 | 10.1 | 0.003 | 0.027 | 69 | 3.9558
交流220kV | 2007-06-18 | 2012-12-06 | 5.474 | 5 | 366 | 833 | 7 | 1 | 1 | 0 | 9 | 0 | 0 | 0 | 2.276
交流220kV | 2008-05-31 | 2013-11-20 | 5.4767 | 9.28 | 490.81 | 830.37 | 6.83 | 0.5 | 1.74 | 0 | 9.07 | 0.003 | 0.25 | 51 | 1.6918
交流220kV | 2006-12-24 | 2012-06-14 | 5.4767 | 16 | 159.5 | 761.9 | 6.6 | 0.6 | 1.4 | 0 | 8.6 | 0.007 | 0.1 | 50 | 4.7768
交流220kV | 2008-05-31 | 2013-11-20 | 5.4767 | 6.17 | 674.68 | 1298.1 | 9.17 | 0.75 | 3.52 | 0 | 13.44 | 0.003 | 0.25 | 51 | 1.924
交流220kV | 2005-07-28 | 2011-01-17 | 5.4767 | 24 | 138 | 2041 | 8.1 | 0.5 | 1.3 | 0 | 9.9 | 0.005 | 0 | 55 | 14.7899
交流220kV | 2008-04-02 | 2013-09-25 | 5.4849 | 22 | 392 | 1356 | 6.2 | 0.6 | 1 | 0 | 7.8 | 0.009 | 0.1 | 57 | 3.4592
交流220kV | 2007-09-11 | 2013-03-07 | 5.4904 | 30 | 133 | 1224 | 10.9 | 2.2 | 4.6 | 0 | 17.7 | 0.009 | 0.3 | 57 | 9.203
交流220kV | 2004-11-13 | 2010-05-11 | 5.4932 | 12.4 | 302.5 | 1109.3 | 4.4 | 0.6 | 1.5 | 0 | 6.5 | 0.026 | 0.257 | 45 | 3.6671
220 | 2008-06-13 | 2013-12-11 | 5.4986 | 10.5 | 516.7 | 2474.46 | 5.77 | 2.8 | 0.94 | 5.29 | 14.8 | 0.008 | 0.001 | 46 | 4.789
交流220kV | 2008-04-25 | 2013-10-23 | 5.4986 | 10.97 | 377.16 | 1210.34 | 6.72 | 0.87 | 0.72 | 0 | 8.31 | 0.008 | 0.073 | 46.9 | 3.2091
220 | 2008-06-12 | 2013-12-11 | 5.5014 | 13.79 | 297.43 | 1240.76 | 6.12 | 0.7 | 0.72 | 0 | 7.54 | 0.007 | 0.001 | 52 | 4.1716
交流220kV | 2006-06-14 | 2011-12-16 | 5.5096 | 22.7 | 592.8 | 6507 | 12.6 | 1.5 | 0 | 0 | 14.1 | 0 | 0 | 0 | 10.9767
交流220kV | 2006-09-29 | 2012-04-01 | 5.5096 | 12.75 | 922.08 | 3453.06 | 19.44 | 8.11 | 5.45 | 1.43 | 34.43 | 0.009 | 0.001 | 55 | 3.7449
交流220kV | 2008-05-15 | 2013-11-16 | 5.5096 | 33.06 | 75.1 | 1467.71 | 3.25 | 0.54 | 0.75 | 0 | 4.54 | 0.002 | 0.1 | 65 | 19.5434
220 | 2006-11-05 | 2012-05-09 | 5.5123 | 1.9 | 99.35 | 992.05 | 4.29 | 2.59 | 1.37 | 0 | 8.25 | 0.009 | 0.001 | 50 | 9.9854
交流220kV | 2008-06-28 | 2013-12-31 | 5.5123 | 11.94 | 490.23 | 2468.42 | 10.59 | 0.96 | 1.91 | 0 | 13.46 | 0 | 0 | 0 | 5.0352
交流220kV | 2007-12-30 | 2013-07-04 | 5.5151 | 9.1 | 681.8 | 4037.7 | 5 | 1.2 | 0 | 0 | 6.2 | 0.034 | 0 | 52 | 5.9221
交流220kV | 2008-06-19 | 2013-12-23 | 5.5151 | 10.88 | 315.96 | 693.45 | 5.13 | 0.76 | 0.41 | 0 | 6.3 | 0.012 | 0.05 | 69.7 | 2.1947
交流220kV | 2008-06-19 | 2013-12-23 | 5.5151 | 7.9 | 320.97 | 643.01 | 5.1 | 0.55 | 0.38 | 0 | 6.03 | 0.012 | 0.041 | 65.9 | 2.0033
交流220kV | 2007-11-29 | 2013-06-04 | 5.5178 | 31.11 | 66.3 | 752.5 | 13.35 | 1.84 | 4.3 | 0 | 19.49 | 0.003 | 0.046 | 59 | 11.3499
交流220kV | 2007-08-20 | 2013-02-23 | 5.5178 | 30.22 | 84.29 | 1166.32 | 8.78 | 2.73 | 2.06 | 0.21 | 13.78 | 0.021 | 0.26 | 50 | 13.837
交流220kV | 2008-06-02 | 2013-12-12 | 5.5315 | 35.8 | 342.5 | 1822.4 | 5.8 | 1.5 | 0.9 | 0 | 8.2 | 0 | 0 | 0 | 5.3209
交流220kV | 2008-05-31 | 2013-12-12 | 5.537 | 41.3 | 366.5 | 1957.2 | 5.9 | 1.2 | 1.2 | 0 | 8.3 | 0 | 0 | 0 | 5.3402
交流220kV | 2006-07-26 | 2012-02-06 | 5.537 | 4 | 180.7 | 577.4 | 9.5 | 0.4 | 1.3 | 0 | 11.2 | 0.008 | 0.094 | 66.5 | 3.1954
交流220kV | 2008-06-27 | 2014-01-10 | 5.5425 | 47.78 | 343.01 | 1033.13 | 7.11 | 0.81 | 2.34 | 0.06 | 10.32 | 0.005 | 0.006 | 52 | 3.012
交流220kV | 2006-12-09 | 2012-06-24 | 5.5452 | 4.42 | 689.68 | 1261.84 | 6.87 | 4.14 | 1.45 | 0 | 12.46 | 0.021 | 0.297 | 58 | 1.8296
交流220kV | 2008-07-26 | 2014-02-10 | 5.5479 | 5.2 | 120.3 | 969.8 | 2.8 | 0.5 | 0.5 | 0 | 3.8 | 0.007 | 0.104 | 60.1 | 8.0615
交流220kV | 2006-09-10 | 2012-03-28 | 5.5507 | 60.11 | 53.94 | 2648.78 | 8.02 | 4.27 | 2.46 | 0 | 14.75 | 0 | 0 | 0 | 49.106
交流220kV | 2008-05-23 | 2013-12-10 | 5.5534 | 15.8 | 504.9 | 1820.9 | 7.8 | 0.6 | 1.1 | 0 | 9.5 | 0 | 0 | 0 | 3.6065
交流220kV | 2006-06-06 | 2011-12-27 | 5.5616 | 23 | 57 | 374 | 9 | 1 | 3 | 0 | 13 | 0 | 0 | 0 | 6.5614
交流220kV | 2006-12-13 | 2012-07-05 | 5.5644 | 48.9 | 145.3 | 2373.2 | 6.1 | 1.1 | 1 | 0 | 8.2 | 0.008 | 0.05 | 58.1 | 16.3331
交流220kV | 2006-06-23 | 2012-01-16 | 5.5699 | 25.72 | 277.5 | 2448.08 | 7.12 | 0.76 | 1.89 | 0 | 9.77 | 0.011 | 0.005 | 56.2 | 8.8219
交流220kV | 2004-08-13 | 2010-03-09 | 5.5726 | 10.24 | 436.56 | 1008.01 | 11.98 | 5.45 | 11.69 | 0 | 29.12 | 0.025 | 1.537 | 47 | 2.309
交流220kV | 2004-08-13 | 2010-03-09 | 5.5726 | 20.2 | 766.56 | 1359.29 | 7.06 | 1.6 | 1.91 | 0 | 10.57 | 0.018 | 0.499 | 49 | 1.7732
交流220kV | 2005-12-18 | 2011-07-15 | 5.5753 | 8.6 | 599.3 | 1651.9 | 11.3 | 0.5 | 1.9 | 0 | 13.7 | 0.008 | 0.15 | 62 | 2.7564
交流220kV | 2008-03-28 | 2013-10-23 | 5.5753 | 4.97 | 297.04 | 1188.86 | 4.91 | 0.84 | 0.47 | 0 | 6.22 | 0.011 | 0.205 | 47 | 4.0024
220 | 2007-08-17 | 2013-03-14 | 5.5781 | 77.2 | 189.24 | 2666.52 | 9.27 | 0.82 | 2.56 | 0 | 12.65 | 0.012 | 0.097 | 51 | 14.0907
交流220kV | 2004-10-10 | 2010-05-10 | 5.5836 | 62 | 299 | 2473 | 6.2 | 0.6 | 1.6 | 0 | 8.4 | 0.007 | 0.002 | 45 | 8.2709
交流220kV | 2007-07-20 | 2013-02-16 | 5.5836 | 8.69 | 964.63 | 4044.07 | 8.32 | 3.22 | 1.61 | 0 | 13.15 | 0.008 | 0.132 | 53 | 4.1924
交流220kV | 2008-03-31 | 2013-10-29 | 5.5836 | 23.12 | 560.84 | 1223.66 | 7.15 | 0 | 1.91 | 0 | 9.06 | 0.009 | 0.006 | 64.4 | 2.1818
交流220kV | 2008-03-31 | 2013-10-29 | 5.5836 | 14.77 | 396.35 | 787.43 | 5.63 | 0.39 | 0.62 | 0 | 6.64 | 0.006 | 0.02 | 53.2 | 1.9867
交流220kV | 2008-03-31 | 2013-10-29 | 5.5836 | 14.23 | 424.66 | 794.8 | 5.58 | 0.45 | 0.66 | 0 | 6.69 | 0.008 | 0.024 | 58.4 | 1.8716
交流220kV | 2006-10-25 | 2012-05-25 | 5.5863 | 15.9 | 269 | 907.1 | 4.2 | 0.9 | 0.6 | 0 | 5.7 | 0.01 | 0.11 | 51.2 | 3.3721
交流220kV | 2006-04-19 | 2011-11-18 | 5.5863 | 16 | 928 | 3455 | 10.7 | 1 | 0.9 | 0.1 | 12.7 | 0.003 | 0.001 | 70 | 3.7231
220 | 2006-11-28 | 2012-07-02 | 5.5973 | 10.02 | 502.21 | 2368.3 | 10.44 | 2.22 | 2.8 | 0 | 15.46 | 0.041 | 0.024 | 58.5 | 4.7158
220 | 2007-12-26 | 2013-07-31 | 5.6 | 16.57 | 884.14 | 5070.97 | 38.45 | 72.68 | 18.42 | 0 | 129.55 | 0.007 | 0.003 | 47 | 5.7355
220 | 2007-12-26 | 2013-08-01 | 5.6027 | 16.57 | 884 | 5071 | 38.45 | 72.68 | 18.42 | 0 | 129.55 | 0.007 | 0.003 | 47 | 5.7364
交流220kV | 2006-10-18 | 2012-05-24 | 5.6027 | 26 | 606 | 907 | 15.4 | 1.9 | 2.5 | 0 | 19.8 | 0.011 | 0.005 | 52 | 1.4967
交流220kV | 2007-02-14 | 2012-09-20 | 5.6027 | 2.88 | 492.58 | 2001.52 | 8.76 | 0.83 | 0.75 | 0 | 10.34 | 0.011 | 0.002 | 60 | 4.0633
交流220kV | 2007-10-30 | 2013-06-06 | 5.6055 | 28.1 | 134 | 462.5 | 2.5 | 0 | 0 | 0 | 2.5 | 0.015 | 0.087 | 0 | 3.4515
交流220kV | 2007-04-30 | 2012-12-05 | 5.6055 | 9.8 | 637.9 | 2568.1 | 8.1 | 3.5 | 1.9 | 0 | 13.5 | 0 | 0 | 0 | 4.0259
交流220kV | 2006-09-10 | 2012-04-17 | 5.6055 | 2 | 136 | 1452 | 2.8 | 0.48 | 0.91 | 0 | 4.19 | 0.003 | 0.083 | 60 | 10.6765
220 | 2007-08-06 | 2013-03-14 | 5.6082 | 52.91 | 187.22 | 1674.91 | 8.13 | 0.78 | 2.08 | 0 | 10.99 | 0.012 | 0.104 | 57 | 8.9462
交流220kV | 2007-11-10 | 2013-06-20 | 5.6137 | 99.3 | 794.9 | 4899.1 | 9.9 | 3 | 1.6 | 0 | 14.5 | 0 | 0.04 | 45.8 | 6.1632
交流220kV | 2008-04-30 | 2013-12-10 | 5.6164 | 24 | 332.2 | 2534.1 | 6.9 | 0.7 | 2.8 | 0 | 10.4 | 0 | 0 | 0 | 7.6282
交流220kV | 2008-04-30 | 2013-12-10 | 5.6164 | 18.2 | 349.6 | 2161.2 | 6.9 | 0.8 | 3.2 | 0 | 10.9 | 0 | 0 | 0 | 6.1819
交流220kV | 2007-10-23 | 2013-06-05 | 5.6219 | 5.5 | 1323.62 | 4513.46 | 0 | 2.97 | 1.78 | 0.18 | 4.93 | 0.003 | 0.42 | 67.6 | 3.4099
交流220kV | 2007-10-27 | 2013-06-09 | 5.6219 | 17.69 | 252.51 | 407.44 | 3.82 | 0.44 | 0.74 | 0 | 5 | 0.031 | 0.017 | 45.6 | 1.6136
交流220kV | 2008-04-29 | 2013-12-12 | 5.6247 | 8.77 | 152.53 | 849.56 | 3.45 | 0.69 | 0.84 | 0 | 4.98 | 0.005 | 0.09 | 62 | 5.5698
交流220kV | 2006-07-09 | 2012-02-23 | 5.6301 | 11 | 40 | 490 | 3 | 1 | 0 | 0 | 4 | 0.027 | 0.001 | 50 | 12.25
交流220kV | 2007-04-29 | 2012-12-14 | 5.6329 | 5.29 | 426.5 | 783.36 | 6.71 | 1.13 | 1.33 | 0 | 9.17 | 0.001 | 0.2 | 41 | 1.8367
交流220kV | 2006-03-11 | 2011-10-28 | 5.6356 | 9 | 660 | 1066 | 8 | 0.9 | 1 | 0 | 9.9 | 0.005 | 0.004 | 50 | 1.6152
220 | 2007-12-11 | 2013-07-31 | 5.6411 | 27.7 | 769.56 | 1789.18 | 8.74 | 0.8 | 1.69 | 0 | 11.23 | 0.009 | 0.001 | 51 | 2.3249
220 | 2007-12-11 | 2013-08-01 | 5.6438 | 27.7 | 770 | 1789 | 8.78 | 0.8 | 1.69 | 0 | 11.27 | 0.009 | 0.001 | 51 | 2.3234
交流220kV | 2007-04-30 | 2012-12-20 | 5.6466 | 80.75 | 47.36 | 680.53 | 11.47 | 8.54 | 3.98 | 0.16 | 24.15 | 0 | 0 | 0 | 14.3693
交流220kV | 2007-04-09 | 2012-12-05 | 5.663 | 17.9 | 597.7 | 1186.3 | 14.2 | 0.5 | 0.8 | 0 | 15.5 | 0 | 0 | 0 | 1.9848
交流220kV | 2007-04-28 | 2012-12-26 | 5.6685 | 11.36 | 367.41 | 4156.64 | 6.82 | 0.85 | 1.46 | 0 | 9.13 | 0 | 0 | 0 | 11.3134
交流220kV | 2007-08-25 10:00 | 2013-04-26 | 5.6728 | 12 | 173 | 1559 | 7.49 | 1.6 | 1.9 | 0 | 10.99 | 0.003 | 0.027 | 54 | 9.0116
交流220kV | 2007-04-20 | 2012-12-20 | 5.674 | 11.77 | 266.86 | 653.31 | 4.93 | 0.3 | 0.41 | 0 | 5.64 | 0 | 0.2 | 46 | 2.4481
交流220kV | 2007-07-11 | 2013-03-13 | 5.6767 | 1.43 | 449.94 | 416.4 | 15.79 | 0.83 | 2.05 | 0 | 18.67 | 0.009 | 0.069 | 59.6 | 0.92546
交流220kV | 2007-07-11 | 2013-03-13 | 5.6767 | 1.43 | 449.94 | 416.4 | 15.79 | 0.83 | 2.05 | 0 | 18.67 | 0.016 | 0.069 | 59.6 | 0.92546
交流220kV | 2008-06-18 | 2014-02-19 | 5.6767 | 18.29 | 654.84 | 1258.37 | 6.88 | 0.49 | 0.9 | 0 | 8.27 | 0.008 | 0.1 | 52 | 1.9216
交流220kV | 2006-07-26 | 2012-03-29 | 5.6795 | 57.8 | 104.4 | 641.9 | 33.5 | 14.2 | 12.2 | 0.1 | 60 | 0.007 | 0.06 | 59.5 | 6.1485
交流220kV | 2006-07-26 | 2012-03-29 | 5.6795 | 56.2 | 102.7 | 605.5 | 31.7 | 13 | 10 | 0.1 | 54.8 | 0 | 0 | 0 | 5.8958
220 | 2008-07-21 | 2014-03-26 | 5.6822 | 27.64 | 222.67 | 874.97 | 5 | 0.4 | 0.99 | 0 | 6.39 | 0.033 | 0.001 | 41.6 | 3.9294
交流220kV | 2001-01-17 | 2006-09-27 | 5.6959 | 4.7 | 522.5 | 1159.6 | 12.7 | 2 | 9.6 | 0 | 24.3 | 0.018 | 1.009 | 45 | 2.2193
交流220kV | 2007-09-22 | 2013-06-09 | 5.7178 | 36.13 | 477.44 | 917.59 | 4.81 | 0.66 | 3.51 | 0 | 8.98 | 0 | 0 | 0 | 1.9219
交流220kV | 2007-09-22 | 2013-06-09 | 5.7178 | 23.12 | 421.42 | 789.4 | 6.38 | 0.81 | 6.79 | 0 | 13.98 | 0 | 0 | 0 | 1.8732
交流220kV | 2006-06-26 | 2012-03-14 | 5.7205 | 105.5 | 176 | 2418.9 | 56.3 | 52 | 19.1 | 0 | 127.4 | 0.007 | 0.06 | 57.2 | 13.7438
交流220kV | 2008-07-09 | 2014-04-01 | 5.7315 | 80.69 | 180.84 | 836.35 | 6.67 | 0.82 | 2.36 | 0 | 9.85 | 0.005 | 0.001 | 59.4 | 4.6248
交流220kV | 2006-12-27 | 2012-09-20 | 5.737 | 5 | 154 | 258 | 0.1 | 0.2 | 0.1 | 0 | 0.4 | 0.025 | 0.21 | 55 | 1.6753
交流220kV | 2006-08-28 | 2012-05-29 | 5.7562 | 5.91 | 488.6 | 2526.11 | 8.56 | 1.26 | 1.96 | 0.06 | 11.84 | 0.014 | 0.278 | 57.6 | 5.1701
交流220kV | 2006-06-19 | 2012-03-22 | 5.7616 | 107.1 | 137.3 | 2133.9 | 83.3 | 78.7 | 31.6 | 0 | 193.6 | 0 | 0 | 0 | 15.5419
交流220kV | 2008-02-15 | 2013-11-21 | 5.7699 | 59.81 | 167.15 | 1074.4 | 6.58 | 0.58 | 1.27 | 0 | 8.43 | 0.023 | 0.22 | 55 | 6.4278
交流220kV | 2006-09-04 | 2012-06-11 | 5.7726 | 7 | 309.8 | 1512.6 | 5.2 | 1.1 | 1.1 | 0 | 7.4 | 0 | 0.45 | 68 | 4.8825
交流220kV | 2006-12-21 | 2012-09-28 | 5.7753 | 20 | 571 | 5339 | 9.7 | 3.8 | 2.8 | 0 | 16.3 | 0.058 | 0.032 | 60 | 9.3503
交流220kV | 2006-09-28 | 2012-07-09 | 5.7836 | 9.24 | 972.81 | 2392.14 | 11.74 | 1.76 | 0.86 | 0 | 14.36 | 0.002 | 0.054 | 0 | 2.459
交流220kV | 2006-12-06 | 2012-09-20 | 5.7945 | 9 | 147 | 214 | 0.2 | 0.1 | 0.2 | 0 | 0.5 | 0.014 | 0.23 | 56 | 1.4558
交流220kV | 2004-05-28 | 2010-03-17 | 5.8055 | 136.32 | 237.47 | 1460.8 | 29.91 | 2.85 | 18.06 | 0 | 50.82 | 0.009 | 0.297 | 51 | 6.1515
交流220kV | 2006-12-10 | 2012-09-28 | 5.8055 | 36 | 480 | 5203 | 10.6 | 0.6 | 1.5 | 0.12 | 12.82 | 0.052 | 0.049 | 52 | 10.8396
交流220kV | 2008-05-30 | 2014-03-20 | 5.8082 | 11 | 278 | 334 | 36.75 | 0.95 | 3.83 | 0 | 41.53 | 0.001 | 0.066 | 50 | 1.2014
交流220kV | 2008-06-05 | 2014-03-27 | 5.811 | 5.04 | 283.86 | 2064.16 | 4.3 | 2.1 | 0.97 | 1.9 | 9.27 | 0 | 0.001 | 47 | 7.2718
交流220kV | 2008-01-01 | 2013-10-23 | 5.8137 | 6.74 | 295.16 | 1126.13 | 5.24 | 0.71 | 0.71 | 0 | 6.66 | 0.009 | 0.133 | 68 | 3.8153
交流220kV | 2008-03-19 | 2014-01-10 | 5.8164 | 49.18 | 182.58 | 914.24 | 3.56 | 0.64 | 1.25 | 0 | 5.45 | 0.004 | 0.005 | 52 | 5.0073
交流220kV | 2007-11-03 | 2013-08-27 | 5.8192 | 22.2 | 395.75 | 750.64 | 4.76 | 0.5 | 0.63 | 0 | 5.89 | 0.002 | 0.001 | 58 | 1.8968
交流220kV | 2007-11-03 | 2013-08-27 | 5.8192 | 8.54 | 77.12 | 379.21 | 4.01 | 0.45 | 0.98 | 0 | 5.44 | 0.002 | 0.002 | 59 | 4.9171
220 | 2006-05-29 | 2012-03-27 | 5.8329 | 4.37 | 418.77 | 714.19 | 5.08 | 0.45 | 0.66 | 0 | 6.19 | 0.004 | 0.078 | 50 | 1.7054
交流220kV | 2005-04-27 | 2011-02-24 | 5.8329 | 16 | 320 | 320 | 17.8 | 1.35 | 4.83 | 0 | 23.98 | 0.001 | 0.001 | 50 | 1
交流220kV | 2008-01-07 | 2013-11-08 | 5.8411 | 18.54 | 458.76 | 1285.54 | 7.24 | 1.37 | 0.67 | 0 | 9.28 | 0.009 | 0.043 | 67 | 2.8022
交流220kV | 2008-01-07 | 2013-11-08 | 5.8411 | 17.6 | 508.82 | 1147.13 | 8.46 | 1.38 | 0.82 | 0 | 10.66 | 0.009 | 0.042 | 65 | 2.2545
交流220kV | 2008-02-04 | 2013-12-10 | 5.8521 | 15.2 | 514.4 | 2643.2 | 11.7 | 3.1 | 2 | 0 | 16.8 | 0 | 0 | 0 | 5.1384
交流220kV | 2008-05-08 | 2014-03-15 | 5.8548 | 141.41 | 47.2 | 267.42 | 3.68 | 0.21 | 0.47 | 0 | 4.36 | 0.008 | 0.16 | 66 | 5.6657
交流220kV | 2007-10-16 | 2013-08-23 | 5.8575 | 5.3 | 699.8 | 1746.6 | 8 | 1 | 1.7 | 0.1 | 10.8 | 0.01 | 0.15 | 56.9 | 2.4959
交流220kV | 2007-01-25 | 2012-12-07 | 5.8712 | 109.97 | 159.24 | 1539.58 | 6.07 | 0.97 | 1.4 | 0 | 8.44 | 0.002 | 0.1 | 40 | 9.6683
交流220kV | 2007-10-16 | 2013-08-29 | 5.874 | 7.9 | 805.5 | 1827.7 | 7.8 | 0.8 | 1.3 | 0.1 | 10 | 0.01 | 0.09 | 60 | 2.269
220 | 2007-06-28 | 2013-05-15 | 5.8849 | 18.9 | 1056.98 | 4261.91 | 13.71 | 0 | 2.36 | 1.36 | 17.43 | 0.007 | 0.002 | 46 | 4.0322
交流220kV | 2006-03-19 | 2012-02-06 | 5.8904 | 3 | 133 | 891.2 | 31.5 | 1.8 | 21.2 | 0 | 54.5 | 0.006 | 0.045 | 64 | 6.7008
交流220kV | 2008-04-30 | 2014-03-20 | 5.8904 | 15 | 369 | 634 | 50.54 | 1.09 | 5.65 | 0 | 57.28 | 0.001 | 0.05 | 50 | 1.7182
交流220kV | 2007-01-13 | 2012-12-07 | 5.9041 | 10.31 | 564.05 | 988.43 | 15.87 | 3.63 | 4.25 | 0 | 23.75 | 0.003 | 0.2 | 41 | 1.7524
交流220kV | 2004-04-23 | 2010-03-18 | 5.9041 | 1.2 | 61.3 | 832.2 | 2.6 | 0.4 | 0.7 | 0 | 3.7 | 0.003 | 0.245 | 55.4 | 13.5759
交流220kV | 2006-09-04 | 2012-07-31 | 5.9096 | 8 | 332.6 | 1494 | 4.9 | 1 | 0.7 | 0 | 6.6 | 0 | 0 | 0 | 4.4919
交流220kV | 2006-01-19 | 2011-12-17 | 5.9123 | 8.34 | 636.81 | 1514.48 | 6.85 | 2.37 | 1.45 | 0 | 10.67 | 0 | 0 | 0 | 2.3782
交流220kV | 2007-12-25 | 2013-11-26 | 5.926 | 50.24 | 492.02 | 4031.56 | 9.58 | 4.91 | 1.75 | 0 | 16.24 | 0.003 | 0.2 | 41 | 8.1939
交流220kV | 2007-06-12 | 2013-05-14 | 5.926 | 32.9 | 285.3 | 1433.9 | 46.8 | 18.4 | 15.6 | 0 | 80.8 | 0.003 | 0.13 | 49 | 5.0259
交流220kV | 2006-07-26 | 2012-06-29 | 5.9315 | 56.2 | 103.6 | 792.3 | 31.9 | 15.6 | 12.4 | 0.1 | 60 | 0 | 0 | 0 | 7.6477
交流220kV | 2007-01-06 | 2012-12-10 | 5.9315 | 2.37 | 197.54 | 748.15 | 9.43 | 0.26 | 0.7 | 0 | 10.39 | 0 | 0 | 0 | 3.7873
交流220kV | 2007-01-07 | 2012-12-14 | 5.9397 | 12.38 | 385.17 | 3363.53 | 5.82 | 5.16 | 0 | 0.08 | 11.06 | 0.002 | 0.1 | 42 | 8.7326
交流220kV | 2006-12-30 | 2012-12-06 | 5.9397 | 13.01 | 100.91 | 632.02 | 2.91 | 0.75 | 3.43 | 0 | 7.09 | 0.012 | 0.013 | 59 | 6.2632
交流220kV | 2007-06-15 | 2013-05-23 | 5.9425 | 14.84 | 1032.32 | 2515.37 | 11.97 | 2.81 | 1.78 | 0 | 16.56 | 0 | 0.003 | 51.8 | 2.4366
交流220kV | 2007-11-28 | 2013-11-06 | 5.9452 | 8.43 | 432.64 | 1371.48 | 7.61 | 1.52 | 0.66 | 0 | 9.79 | 0.011 | 0.037 | 65 | 3.17
交流220kV | 2007-11-28 | 2013-11-06 | 5.9452 | 5.61 | 226.97 | 1103.13 | 5.05 | 1.12 | 0.36 | 0 | 6.53 | 0.017 | 0.046 | 63 | 4.8602
交流220kV | 2008-03-01 | 2014-02-10 | 5.9507 | 5 | 321.92 | 2143.4 | 11.5 | 1.3 | 2.6 | 0 | 15.4 | 0.018 | 0.409 | 51 | 6.6582
交流220kV | 1999-04-13 | 2005-03-24 | 5.9507 | 7.46 | 950.51 | 3156.65 | 5.94 | 34.68 | 4.31 | 0 | 44.93 | 0.012 | 0.723 | 53 | 3.321
交流220kV | 2007-12-14 | 2013-11-26 | 5.9562 | 8.15 | 443.2 | 2846.29 | 4.64 | 0.78 | 0.89 | 0 | 6.31 | 0.002 | 0.1 | 41 | 6.4221
交流220kV | 2007-12-27 | 2013-12-12 | 5.9644 | 60.2 | 113.2 | 701.6 | 4.4 | 0.6 | 0.8 | 0 | 5.8 | 0 | 0 | 0 | 6.1979
交流220kV | 2006-07-08 | 2012-06-24 | 5.9671 | 2.23 | 361.1 | 1004.62 | 6.72 | 3.74 | 2.92 | 0 | 13.38 | 0.031 | 0.282 | 53 | 2.7821
交流220kV | 2007-11-25 | 2013-11-11 | 5.9671 | 10.36 | 311.18 | 736.1 | 5.59 | 0.85 | 0.33 | 0 | 6.77 | 0.009 | 0.083 | 62 | 2.3655
交流220kV | 2007-11-25 | 2013-11-11 | 5.9671 | 7.56 | 360.08 | 868.92 | 7.15 | 1.37 | 0.58 | 0 | 9.1 | 0.008 | 0.077 | 68 | 2.4131
220 | 2008-03-31 | 2014-03-19 | 5.9699 | 3.84 | 765.63 | 2226.2 | 8.81 | 1.01 | 0.96 | 0 | 10.78 | 0.013 | 0.057 | 56 | 2.9077
交流220kV | 2007-12-30 | 2013-12-17 | 5.9699 | 11.2 | 634.1 | 4572.2 | 5.1 | 0 | 0 | 0 | 5.1 | 0.04 | 1.6 | 45 | 7.2105
交流220kV | 2007-04-08 | 2013-03-26 | 5.9699 | 114.27 | 979.88 | 1328.88 | 10.39 | 1.43 | 3.59 | 0 | 15.41 | 0.021 | 0.001 | 82.1 | 1.3562
交流220kV | 2006-12-24 | 2012-12-13 | 5.9753 | 12.2 | 144.4 | 741.6 | 6 | 0.6 | 0.5 | 0 | 7.1 | 0 | 0 | 0 | 5.1357
交流220kV | 2006-06-06 | 2012-05-31 | 5.989 | 23 | 59 | 475 | 10.3 | 3.2 | 0.5 | 0 | 14 | 0.047 | 0.067 | 52 | 8.0508
交流220kV | 2005-12-14 | 2011-12-13 | 6 | 7.69 | 253.72 | 616.06 | 2.92 | 0.76 | 0.35 | 0 | 4.03 | 0.003 | 0.02 | 48 | 2.4281
交流220kV | 2006-12-13 | 2012-12-13 | 6.0055 | 51.1 | 147.6 | 2152.5 | 6.4 | 1.9 | 1 | 0 | 9.3 | 0 | 0 | 0 | 14.5833
交流220kV | 2007-07-09 | 2013-07-10 | 6.0082 | 127.14 | 724.89 | 1842.47 | 93.67 | 117.88 | 20.49 | 2.75 | 234.79 | 0.004 | 0.004 | 60.7 | 2.5417
交流220kV | 2004-08-13 | 2010-08-17 | 6.0137 | 12.02 | 538.52 | 1776.39 | 20.07 | 3.36 | 8.34 | 0 | 31.77 | 0.014 | 0.456 | 60 | 3.2987
交流220kV | 2004-08-13 | 2010-08-17 | 6.0137 | 8.33 | 617.94 | 1953.47 | 12.94 | 2.8 | 4.6 | 0 | 20.34 | 0.013 | 0.806 | 56 | 3.1613
交流220kV | 2004-02-26 | 2010-03-03 | 6.0192 | 7.28 | 340.48 | 1383.15 | 7.75 | 3.05 | 1.31 | 0 | 12.11 | 0.015 | 0.248 | 50 | 4.0624
220 | 2007-03-08 | 2013-03-15 | 6.0247 | 9.28 | 634.58 | 1969.07 | 8.68 | 1.07 | 1.18 | 0 | 10.93 | 0.003 | 1.99 | 51.6 | 3.1029
交流220kV | 2007-06-18 | 2013-06-25 | 6.0247 | 6 | 415 | 978 | 9 | 1 | 2 | 0 | 12 | 0.025 | 0.064 | 53 | 2.3566
交流220kV | 2006-12-09 | 2012-12-18 | 6.0301 | 4.28 | 689.35 | 1157.66 | 5.9 | 3.36 | 0 | 0 | 9.26 | 0.006 | 0.3 | 60 | 1.6794
交流220kV | 2006-06-19 | 2012-06-29 | 6.0329 | 85.4 | 124 | 2551.2 | 89.1 | 87 | 35.2 | 0 | 211.3 | 0 | 0 | 0 | 20.5742
交流220kV | 2005-04-03 | 2011-04-14 | 6.0329 | 14 | 283 | 382 | 15.83 | 3.46 | 5.08 | 0 | 24.37 | 0.003 | 0.001 | 49.8 | 1.3498
交流220kV | 2005-06-24 | 2011-07-07 | 6.0384 | 26.2 | 290.1 | 1593.1 | 7.3 | 0.8 | 4.1 | 0 | 12.2 | 0 | 0 | 0 | 5.4916
交流220kV | 2006-04-28 | 2012-05-11 | 6.0411 | 9.11 | 256.44 | 899.57 | 6.91 | 0.77 | 1.52 | 0 | 9.2 | 0.04 | 0.001 | 59 | 3.5079
交流220kV | 2006-11-23 | 2012-12-07 | 6.0438 | 8.42 | 545.83 | 2052.49 | 8.79 | 8.99 | 1.81 | 0 | 19.59 | 0 | 0 | 0 | 3.7603
交流220kV | 2006-06-26 | 2012-07-12 | 6.0493 | 119 | 178.5 | 3045.4 | 62.6 | 58.3 | 20.6 | 0.1 | 141.6 | 0 | 0 | 0 | 17.0611
交流220kV | 2007-05-11 | 2013-05-29 | 6.0548 | 26.8 | 389.8 | 1134.6 | 8.2 | 1.6 | 1.3 | 0 | 11.1 | 0.003 | 1.11 | 54.5 | 2.9107
交流220kV | 2007-12-27 | 2014-01-16 | 6.0603 | 4.8 | 222.7 | 544.8 | 5 | 0.5 | 0.4 | 0.1 | 6 | 0.001 | 0.13 | 57.2 | 2.4463
交流220kV | 2007-12-27 | 2014-01-16 | 6.0603 | 12.9 | 190.1 | 375.4 | 5.2 | 0.4 | 0.6 | 0 | 6.2 | 0.002 | 0.14 | 53.6 | 1.9748
交流220kV | 2006-04-19 | 2012-05-09 | 6.0603 | 10 | 749 | 2763 | 9.8 | 1 | 0.9 | 0.1 | 11.8 | 0.003 | 0.01 | 37 | 3.6889
交流220kV | 2007-02-12 | 2013-03-05 | 6.063 | 4.6 | 189.8 | 1760.5 | 8.8 | 0.6 | 2 | 0 | 11.4 | 0.011 | 0.085 | 69.5 | 9.2756
交流220kV | 2007-04-29 | 2013-05-24 | 6.074 | 8.61 | 533.9 | 1164.58 | 9.29 | 1.72 | 1.94 | 0.11 | 13.06 | 0.003 | 0.25 | 56 | 2.1813
交流220kV | 2005-08-23 | 2011-09-20 | 6.0795 | 30.69 | 349.22 | 991.03 | 8.51 | 0.78 | 1.59 | 0.18 | 11.06 | 0.003 | 0.02 | 49 | 2.8378
交流220kV | 2005-06-20 | 2011-07-22 | 6.0904 | 12 | 628 | 3371 | 12 | 2 | 4 | 0 | 18 | 0 | 0 | 0 | 5.3678
交流220kV | 2005-05-10 | 2011-06-13 | 6.0959 | 49.52 | 333.98 | 2225.09 | 11.59 | 3.59 | 2.92 | 0 | 18.1 | 0.002 | 0.02 | 49 | 6.6623
交流220kV | 2007-04-30 | 2013-06-05 | 6.1041 | 11.1 | 579.2 | 4126.9 | 7.3 | 3.6 | 2.4 | 0 | 13.3 | 0 | 0 | 60.8 | 7.1252
交流220kV | 2007-04-30 | 2013-06-06 | 6.1068 | 106.19 | 148.01 | 1447.83 | 16.77 | 4.98 | 8.56 | 0 | 30.31 | 0 | 0 | 0 | 9.782
交流220kV | 2006-03-15 | 2012-04-23 | 6.1123 | 7.8 | 720.5 | 2130.4 | 8.9 | 2 | 2.4 | 0 | 13.3 | 0.011 | 0.002 | 58.8 | 2.9568
交流220kV | 2007-04-28 | 2013-06-07 | 6.1151 | 8.28 | 397.83 | 4360.7 | 9.38 | 40.9 | 4.49 | 0 | 54.77 | 0 | 0 | 0 | 10.9612
交流220kV | 2006-03-07 | 2012-04-17 | 6.1178 | 3 | 670 | 2359 | 5.74 | 0.67 | 1.91 | 0 | 8.32 | 0.004 | 0.073 | 58 | 3.5209
交流220kV | 2006-03-07 | 2012-04-17 | 6.1178 | 3 | 396 | 1820 | 5.74 | 1.67 | 1.91 | 0 | 9.32 | 0.004 | 0.073 | 58 | 4.596
交流220kV | 2006-10-24 | 2012-12-07 | 6.126 | 28.54 | 115.66 | 2164.79 | 4.96 | 0.65 | 0.97 | 0.1 | 6.68 | 0.002 | 0.2 | 41 | 18.7168
交流220kV | 2007-01-30 | 2013-03-15 | 6.126 | 8 | 406 | 1111 | 23.56 | 1.29 | 3.16 | 0 | 28.01 | 0.001 | 0.099 | 50 | 2.7365
交流220kV | 2005-05-13 | 2011-06-29 | 6.1315 | 21 | 354.39 | 663.94 | 8.34 | 0.88 | 0.73 | 0.08 | 10.03 | 0.01 | 0.02 | 48 | 1.8735
交流220kV | 2007-10-23 | 2013-12-09 | 6.1342 | 1.31 | 1291.27 | 3894.56 | 14.47 | 2.64 | 1.74 | 0.14 | 18.99 | 0 | 0 | 0 | 3.0161
交流220kV | 2007-09-25 | 2013-11-11 | 6.1342 | 11.26 | 312.81 | 879.71 | 5.98 | 1.2 | 0.7 | 0 | 7.88 | 0.011 | 0.053 | 68 | 2.8123
交流220kV | 2007-09-25 | 2013-11-11 | 6.1342 | 3.94 | 100.21 | 534.67 | 2.96 | 0.34 | 0.3 | 0 | 3.6 | 0.009 | 0.061 | 69 | 5.3355
交流220kV | 2007-04-20 | 2013-06-09 | 6.1425 | 9.4 | 281 | 804 | 5.6 | 0.4 | 0.5 | 0 | 6.5 | 0 | 0 | 0 | 2.8612
交流220kV | 2007-05-04 | 2013-06-25 | 6.1479 | 10.58 | 423.21 | 1908.21 | 10.23 | 3.25 | 1.3 | 0 | 14.78 | 0.012 | 0.004 | 60 | 4.5089
交流220kV | 2005-12-16 | 2012-02-09 | 6.1534 | 18 | 102 | 1455 | 2.3 | 0.4 | 0 | 0 | 2.7 | 0.016 | 0.001 | 49 | 14.2647
交流220kV | 2008-02-01 | 2014-03-27 | 6.1534 | 175.92 | 778.22 | 1340.1 | 21.4 | 5.36 | 3 | 0.56 | 30.32 | 0.002 | 0.001 | 59.7 | 1.722
交流220kV | 2006-09-10 | 2012-11-05 | 6.1589 | 83.22 | 58.47 | 3407.16 | 9.83 | 4.74 | 4.07 | 0 | 18.64 | 0 | 0.001 | 44.6 | 58.2719
交流220kV | 2007-04-29 | 2013-06-25 | 6.1616 | 12.12 | 652.99 | 1922.36 | 10.49 | 1.3 | 1 | 0 | 12.79 | 0.011 | 0.003 | 60 | 2.9439
交流220kV | 2007-04-09 | 2013-06-06 | 6.1644 | 18.2 | 646.8 | 2037.4 | 15.8 | 0.7 | 1.3 | 0 | 17.8 | 0.01 | 0 | 67.2 | 3.15
交流220kV | 2006-02-21 | 2012-04-21 | 6.1671 | 6 | 640.6 | 4424.1 | 4.9 | 0.8 | 1.1 | 0 | 6.8 | 0.013 | 0.002 | 56.7 | 6.9062
交流220kV | 2001-10-09 | 2007-12-11 | 6.1753 | 13.3 | 486.8 | 3403.3 | 10.1 | 1.4 | 1.9 | 0 | 13.4 | 0.007 | 0.002 | 59 | 6.9912
交流220kV | 2006-08-20 | 2012-10-22 | 6.1781 | 10.86 | 412.47 | 971.49 | 3.68 | 0.52 | 0.47 | 0 | 4.67 | 0.008 | 0.002 | 60 | 2.3553
交流220kV | 2007-10-27 | 2013-12-31 | 6.1836 | 17.41 | 268.67 | 381.73 | 4.39 | 0.54 | 0.57 | 0 | 5.5 | 0 | 0 | 0 | 1.4208
220 | 2006-12-28 | 2013-03-04 | 6.1863 | 66.6 | 259.1 | 2316.99 | 7.54 | 0.92 | 1.65 | 0 | 10.11 | 0.014 | 0.111 | 54 | 8.9425
交流220kV | 2006-07-09 | 2012-09-18 | 6.2 | 9 | 18 | 463 | 2 | 0.8 | 0.6 | 0 | 3.4 | 0.026 | 0.001 | 50 | 25.7222
交流220kV | 2005-12-30 | 2012-03-16 | 6.2137 | 21.86 | 325.07 | 711.86 | 4.32 | 0.54 | 0.7 | 0.08 | 5.64 | 0.006 | 0.001 | 54 | 2.1899
交流220kV | 2005-12-20 | 2012-03-07 | 6.2164 | 18.2 | 905.79 | 1580.8 | 13.51 | 3.38 | 3.13 | 0 | 20.02 | 0.012 | 0.299 | 53.3 | 1.7452
交流220kV | 2006-01-24 | 2012-04-12 | 6.2192 | 51 | 328 | 222 | 4.8 | 0.9 | 0 | 0 | 5.7 | 0.031 | 0.021 | 48 | 0.67683
交流220kV | 2005-12-28 | 2012-03-16 | 6.2192 | 14.3 | 130.38 | 806.46 | 6.49 | 7.12 | 2.23 | 0.21 | 16.05 | 0.008 | 0.001 | 54 | 6.1855
交流220kV | 2007-11-26 | 2014-02-13 | 6.2219 | 14.72 | 811.06 | 1119.09 | 16.49 | 4.56 | 3.54 | 0 | 24.59 | 0.005 | 0.015 | 60 | 1.3798
交流220kV | 2005-07-30 | 2011-10-18 | 6.2219 | 32.19 | 989.3 | 3902.7 | 12.59 | 1.1 | 1.57 | 0.3 | 15.56 | 0.047 | 0.105 | 61.2 | 3.9449
交流220kV | 2005-07-30 | 2011-10-20 | 6.2274 | 32 | 989 | 3901 | 12.6 | 1.1 | 1.6 | 0.3 | 15.6 | 0.047 | 0.011 | 61.2 | 3.9444
交流220kV | 2006-06-13 | 2012-09-03 | 6.2301 | 12.98 | 877.96 | 1660.05 | 9.32 | 0.63 | 1.1 | 0 | 11.05 | 0.008 | 0.003 | 56 | 1.8908
交流220kV | 2005-07-27 | 2011-10-18 | 6.2301 | 18.63 | 619.75 | 2367.72 | 7.98 | 0.65 | 1.09 | 0.2 | 9.92 | 0.045 | 0.061 | 61.2 | 3.8204
交流220kV | 2005-12-25 | 2012-03-19 | 6.2356 | 14.29 | 322.35 | 1433.02 | 7.79 | 0.62 | 1.37 | 0 | 9.78 | 0.009 | 0.01 | 58 | 4.4455
交流220kV | 2005-07-27 | 2011-10-20 | 6.2356 | 18.6 | 620 | 2368 | 8 | 0.7 | 1.1 | 0.2 | 10 | 0.045 | 0.01 | 61.2 | 3.8194
交流220kV | 2006-09-28 | 2012-12-24 | 6.2438 | 13.13 | 1153.86 | 2676.4 | 14.84 | 1.88 | 1.39 | 0 | 18.11 | 0 | 0 | 0 | 2.3195
交流220kV | 2003-12-12 | 2010-03-10 | 6.2466 | 21 | 1050 | 3524 | 22.18 | 18.69 | 8.86 | 0 | 49.73 | 0.001 | 0.001 | 50 | 3.3562
交流220kV | 2001-01-17 | 2007-04-16 | 6.2466 | 5.83 | 641.02 | 3188.17 | 18.38 | 1.15 | 4.15 | 0 | 23.68 | 0.018 | 0.1 | 52 | 4.9736
交流220kV | 2007-08-06 | 2013-11-05 | 6.2548 | 15.34 | 429.91 | 1469.35 | 8.3 | 1.83 | 0.58 | 0.56 | 11.27 | 0.022 | 0.037 | 66 | 3.4178
交流220kV | 2007-08-06 | 2013-11-05 | 6.2548 | 11.89 | 490.88 | 1139.01 | 8.23 | 1.35 | 0 | 0 | 9.58 | 0.012 | 0.031 | 68 | 2.3203
交流220kV | 2005-05-10 | 2011-08-11 | 6.2575 | 48.29 | 359.23 | 2486.11 | 10.59 | 3.69 | 2.67 | 0 | 16.95 | 0.003 | 0.02 | 49 | 6.9207
交流220kV | 2006-09-04 | 2012-12-07 | 6.263 | 7.4 | 308 | 1160 | 4.8 | 1.1 | 0.8 | 0 | 6.7 | 0 | 0 | 0 | 3.7662
交流220kV | 2007-09-13 | 2013-12-17 | 6.2658 | 16.5 | 780.9 | 6736.5 | 14.2 | 32.1 | 3.1 | 0 | 49.4 | 0.07 | 2.8 | 44 | 8.6266
交流220kV | 2007-09-13 | 2013-12-17 | 6.2658 | 8.7 | 799.4 | 4486 | 9.9 | 14 | 0.4 | 0 | 24.3 | 0.06 | 2.7 | 45 | 5.6117
交流220kV | 2007-11-03 | 2014-02-10 | 6.2767 | 6.2 | 335.1 | 1322.7 | 16.7 | 1.3 | 2.1 | 0 | 20.1 | 0.019 | 0.127 | 55.4 | 3.9472
交流220kV | 2005-06-13 | 2011-09-22 | 6.2795 | 133.72 | 188.24 | 2304.2 | 8.53 | 0 | 0 | 0 | 8.53 | 0 | 0 | 45 | 12.2408
交流220kV | 2007-09-22 | 2013-12-31 | 6.2795 | 18.83 | 389.12 | 696.21 | 4.93 | 0.39 | 0.28 | 0 | 5.6 | 0 | 0 | 0 | 1.7892
交流220kV | 2007-09-22 | 2013-12-31 | 6.2795 | 20.85 | 590.41 | 940.71 | 6.84 | 1.57 | 0.73 | 0 | 9.14 | 0 | 0 | 0 | 1.5933
交流220kV | 2006-04-08 | 2012-07-18 | 6.2822 | 15.38 | 459.46 | 1191.01 | 7.41 | 2.27 | 0.89 | 0 | 10.57 | 0.006 | 0.001 | 60 | 2.5922
交流220kV | 2005-09-04 | 2011-12-16 | 6.2849 | 34.1 | 518.1 | 2114 | 10.8 | 1.3 | 1.9 | 0 | 14 | 0 | 0 | 0 | 4.0803
交流220kV | 2007-09-12 | 2013-12-25 | 6.2904 | 47.41 | 522.6 | 3050.31 | 13.09 | 1.35 | 2.01 | 0 | 16.45 | 0.007 | 0.29 | 63 | 5.8368
220 | 2005-12-19 | 2012-04-06 | 6.3014 | 3.5 | 27.69 | 358.72 | 2.88 | 0 | 0.61 | 0 | 3.49 | 0.011 | 0.001 | 58 | 12.9549
交流220kV | 2005-12-24 | 2012-04-12 | 6.3041 | 9.5 | 427.9 | 835.2 | 4.7 | 0.4 | 0.8 | 0 | 5.9 | 0.006 | 0.043 | 53.2 | 1.9519
交流220kV | 2007-12-14 | 2014-04-03 | 6.3068 | 4.78 | 339.58 | 2538.32 | 4.14 | 0.76 | 0.94 | 0 | 5.84 | 0.001 | 0.14 | 45 | 7.4749
交流220kV | 2006-06-02 | 2012-09-20 | 6.3068 | 1.7 | 316.55 | 1555.41 | 5.88 | 0.61 | 0.61 | 0 | 7.1 | 0.01 | 0.003 | 61 | 4.9136
交流220kV | 2006-07-26 | 2012-11-14 | 6.3096 | 44.4 | 82 | 754.8 | 29.1 | 13.6 | 12.6 | 0.1 | 55.4 | 0 | 0 | 0 | 9.2049
交流220kV | 2006-07-26 | 2012-11-14 | 6.3096 | 55.9 | 92.8 | 753.5 | 31.4 | 14.5 | 11.4 | 0.1 | 57.4 | 0 | 0 | 0 | 8.1196
交流220kV | 2005-11-15 | 2012-03-07 | 6.3123 | 21.35 | 1045.31 | 2109.25 | 14.03 | 1.44 | 2.44 | 0 | 17.91 | 0.01 | 0.149 | 48.8 | 2.0178
交流220kV | 2005-08-23 | 2011-12-19 | 6.326 | 26.57 | 349.84 | 1375.81 | 8.88 | 0.79 | 1.69 | 0.22 | 11.58 | 0.003 | 0.02 | 45 | 3.9327
交流220kV | 2007-01-25 | 2013-05-24 | 6.3315 | 99.6 | 157.78 | 1657.85 | 5.85 | 0.88 | 1.4 | 0 | 8.13 | 0.003 | 0.1 | 43 | 10.5074
交流220kV | 2005-09-19 | 2012-01-17 | 6.3315 | 4.77 | 692.33 | 2526.26 | 16.83 | 1.67 | 5.16 | 0 | 23.66 | 0.007 | 0.083 | 52.5 | 3.6489
交流220kV | 2005-08-18 | 2011-12-16 | 6.3315 | 13 | 757 | 2501 | 8.6 | 4.8 | 1.4 | 0 | 14.8 | 0.002 | 0.003 | 40 | 3.3038
交流220kV | 2007-06-29 | 2013-10-28 | 6.337 | 13.46 | 1064.9 | 4134.98 | 16.09 | 0.97 | 2.28 | 0 | 19.34 | 0.008 | 0.022 | 60 | 3.883
交流220kV | 2007-06-29 | 2013-10-28 | 6.337 | 12.47 | 644.32 | 3000.82 | 11.84 | 0.66 | 1.69 | 0 | 14.19 | 0.011 | 0.02 | 58 | 4.6573
交流220kV | 2005-08-15 | 2011-12-16 | 6.3397 | 12 | 313 | 1394 | 4.2 | 0.6 | 0.5 | 0 | 5.3 | 0.003 | 0.002 | 40 | 4.4537
交流220kV | 2005-08-15 | 2011-12-16 | 6.3397 | 5 | 408 | 1481 | 4.7 | 0.6 | 0.5 | 0 | 5.8 | 0.003 | 0.003 | 42 | 3.6299
交流220kV | 2005-12-14 | 2012-04-25 | 6.3671 | 12.94 | 1223.42 | 10027.06 | 31.73 | 15.96 | 9.88 | 0 | 57.57 | 0.001 | 0.1 | 41 | 8.1959
交流220kV | 2007-01-13 | 2013-05-29 | 6.3781 | 5.81 | 568.61 | 1096.61 | 17.3 | 3.55 | 5.21 | 0 | 26.06 | 0.002 | 0.2 | 43 | 1.9286
交流220kV | 2006-07-08 | 2012-11-21 | 6.3781 | 13.1 | 45 | 376 | 4.9 | 0.2 | 1 | 0 | 6.1 | 0.008 | 0.002 | 44 | 8.3556
交流220kV | 2007-11-10 | 2014-03-28 | 6.3836 | 99.7 | 757 | 4409.9 | 8.1 | 0.6 | 1.6 | 0.2 | 10.5 | 0.007 | 0.05 | 54 | 5.8255
交流220kV | 1997-11-25 | 2004-04-12 | 6.3836 | 90.8 | 862.1 | 1260.2 | 13.8 | 4 | 4.5 | 3.4 | 25.7 | 0.006 | 0.026 | 46 | 1.4618
交流220kV | 2005-10-18 | 2012-03-05 | 6.3836 | 11.8 | 589.83 | 2553.74 | 12.24 | 0.88 | 1.97 | 0 | 15.09 | 0.004 | 0.001 | 62 | 4.3296
交流220kV | 2006-12-28 | 2013-05-16 | 6.3863 | 62.81 | 222.79 | 688.85 | 8.69 | 0.25 | 1.61 | 0 | 10.55 | 0 | 0.009 | 56.7 | 3.0919
交流220kV | 2006-07-26 | 2012-12-13 | 6.389 | 54.7 | 104.6 | 746.4 | 30.6 | 14.6 | 11.7 | 0.1 | 57 | 0 | 0 | 0 | 7.1358
交流220kV | 2007-09-30 | 2014-02-17 | 6.389 | 4.6 | 80.6 | 549 | 2 | 0.4 | 0.9 | 0 | 3.3 | 0.006 | 0.002 | 43.6 | 6.8114
交流220kV | 2005-06-27 | 2011-11-16 | 6.3918 | 5 | 145 | 747 | 6.5 | 7.5 | 2.1 | 0 | 16.1 | 0.026 | 0.003 | 55 | 5.1517
交流220kV | 2005-12-30 | 2012-05-23 | 6.4 | 22.33 | 367.7 | 789.94 | 5.48 | 0.99 | 1.41 | 0 | 7.88 | 0.003 | 0.001 | 60 | 2.1483
交流220kV | 2007-11-03 | 2014-03-28 | 6.4027 | 27.75 | 511.05 | 815.79 | 7.07 | 0.69 | 1.01 | 0 | 8.77 | 0.005 | 0.001 | 59 | 1.5963
交流220kV | 2007-11-03 | 2014-03-28 | 6.4027 | 9.21 | 88.91 | 410.63 | 5.6 | 0.57 | 1.22 | 0 | 7.39 | 0.004 | 0.001 | 59 | 4.6185
交流220kV | 2003-09-01 11:18 | 2010-01-25 | 6.4042 | 48 | 250 | 412 | 26 | 89.2 | 12.8 | 2.89 | 130.89 | 0.01 | 0.003 | 52 | 1.648
交流220kV | 2005-10-18 | 2012-03-13 | 6.4055 | 18.02 | 621.23 | 1879.07 | 10.46 | 1.16 | 1.93 | 0 | 13.55 | 0.005 | 0.001 | 76 | 3.0248
交流220kV | 2005-12-27 | 2012-05-23 | 6.4082 | 8 | 457 | 3088 | 10.5 | 0.9 | 5 | 0 | 16.4 | 0.011 | 0.001 | 40 | 6.7571
交流220kV | 2006-12-13 | 2013-05-13 | 6.4192 | 46.6 | 140.4 | 2154.5 | 5.2 | 1.9 | 1 | 0 | 8.1 | 0.006 | 0.01 | 55.4 | 15.3454
交流220kV | 2006-12-24 | 2013-05-24 | 6.4192 | 10.1 | 145.3 | 804.8 | 6.7 | 0.3 | 0.4 | 0 | 7.4 | 0.008 | 0.1 | 51.5 | 5.5389
交流220kV | 2006-10-25 | 2013-03-26 | 6.4219 | 12.3 | 271 | 888.6 | 4.4 | 0.9 | 0.6 | 0 | 5.9 | 0.003 | 0.09 | 62.8 | 3.279
交流220kV | 2007-01-06 | 2013-06-08 | 6.4247 | 1.64 | 175.08 | 929.36 | 6.79 | 0.56 | 0.9 | 0 | 8.25 | 0.001 | 0.368 | 68.3 | 5.3082
220 | 2007-09-25 | 2014-02-28 | 6.4329 | 15.12 | 60.76 | 630.33 | 3.05 | 0.8 | 0.64 | 0 | 4.49 | 0.011 | 0.095 | 41.2 | 10.3741
220 | 2007-09-25 | 2014-02-28 | 6.4329 | 15.12 | 60.76 | 630.33 | 3.05 | 0.8 | 0.64 | 0 | 4.49 | 0.097 | 0.095 | 41.2 | 10.3741
交流220kV | 2003-09-27 | 2010-03-03 | 6.4356 | 23.47 | 167.33 | 978.25 | 21.14 | 3.46 | 9 | 0 | 33.6 | 0.012 | 0.193 | 48 | 5.8462
交流220kV | 2007-01-07 | 2013-06-17 | 6.4466 | 10.56 | 453.73 | 5027.2 | 7.58 | 7.76 | 1.07 | 0.13 | 16.54 | 0.002 | 0.1 | 43 | 11.0797
交流220kV | 2006-07-08 | 2012-12-18 | 6.4521 | 0.31 | 359.94 | 1196.79 | 4.99 | 0 | 0 | 0 | 4.99 | 0.007 | 0.3 | 59 | 3.325
交流220kV | 2003-08-14 | 2010-01-27 | 6.4603 | 10 | 576 | 3418 | 25.3 | 5.6 | 4.1 | 0 | 35 | 0.011 | 0.006 | 51.5 | 5.934
交流220kV | 2001-06-04 | 2007-11-19 | 6.463 | 26.2 | 439.6 | 1440.4 | 9.4 | 1 | 2.3 | 0 | 12.7 | 0.006 | 0.005 | 49.3 | 3.2766
交流220kV | 2001-06-04 | 2007-11-20 | 6.4658 | 26.2 | 439.6 | 1440.4 | 9.4 | 1 | 2.3 | 0 | 12.7 | 0.01 | 0.005 | 49.3 | 3.2766
交流220kV | 2005-06-30 | 2011-12-21 | 6.4795 | 0.9 | 110.58 | 2794.99 | 2.11 | 19.06 | 0.31 | 0 | 21.48 | 0 | 0.001 | 55 | 25.2757
交流220kV | 2005-06-02 | 2011-11-28 | 6.4932 | 18.3 | 1399.7 | 8395.7 | 11.5 | 58.9 | 4.8 | 0 | 75.2 | 0 | 0 | 0 | 5.9982
交流220kV | 2006-12-09 | 2013-06-06 | 6.4959 | 2.83 | 688.19 | 1394.07 | 6.62 | 3.57 | 2.72 | 0 | 12.91 | 0.007 | 0.29 | 60 | 2.0257
交流220kV | 2005-06-11 | 2011-12-08 | 6.4959 | 12 | 745 | 2051 | 6.3 | 1.3 | 1.8 | 0 | 9.4 | 0.003 | 0.001 | 67 | 2.753
交流220kV | 2005-06-24 | 2011-12-22 | 6.4986 | 25.33 | 301.31 | 761.15 | 7.21 | 2.42 | 0.66 | 0 | 10.29 | 0 | 0 | 49.4 | 2.5261
交流220kV | 2006-06-14 | 2012-12-11 | 6.4986 | 13.6 | 586.7 | 3731.7 | 10.6 | 1.2 | 3.2 | 0 | 15 | 0 | 0 | 0 | 6.3605
交流220kV | 2006-12-17 | 2013-06-15 | 6.4986 | 12.35 | 669.75 | 6262.14 | 9.55 | 1.31 | 1.87 | 0 | 12.73 | 0 | 0 | 47 | 9.35
交流220kV | 2006-12-17 | 2013-06-15 | 6.4986 | 12.35 | 669.75 | 6262.14 | 9.55 | 1.31 | 1.87 | 0 | 12.73 | 0 | 0 | 55 | 9.35
交流220kV | 2004-12-29 | 2011-06-28 | 6.4986 | 19.7 | 993.7 | 2509.5 | 8.1 | 0.9 | 1.4 | 0.2 | 10.6 | 0.01 | 0.08 | 60 | 2.5254
交流220kV | 2006-01-19 | 2012-07-19 | 6.5014 | 8.18 | 699.1 | 1871.64 | 7.04 | 2.57 | 1.22 | 0 | 10.83 | 0.015 | 0.103 | 58.9 | 2.6772
交流220kV | 2005-11-28 | 2012-05-28 | 6.5014 | 7.3 | 550.4 | 1407.5 | 7.1 | 1.9 | 1 | 3.4 | 13.4 | 0.002 | 0.09 | 57.6 | 2.5572
交流220kV | 2006-06-06 | 2012-12-05 | 6.5041 | 17 | 48 | 497 | 6 | 0 | 1 | 0 | 7 | 0 | 0 | 0 | 10.3542
交流220kV | 2007-06-18 | 2013-12-18 | 6.5068 | 3 | 399 | 1101 | 9 | 1 | 1 | 0 | 11 | 0 | 0 | 0 | 2.7594
交流220kV | 2005-12-25 | 2012-06-26 | 6.5068 | 5.03 | 163.29 | 328.15 | 4.62 | 3.05 | 2.17 | 0 | 9.84 | 0.015 | 0.106 | 52.3 | 2.0096
交流220kV | 2005-12-25 | 2012-06-26 | 6.5068 | 8.13 | 268.35 | 489.26 | 4.32 | 3.69 | 1.85 | 0 | 9.86 | 0.015 | 0.095 | 54.2 | 1.8232
交流220kV | 2006-06-30 | 2012-12-31 | 6.5096 | 6 | 123 | 256 | 0.2 | 0.3 | 0.1 | 0 | 0.6 | 0.052 | 0.32 | 56 | 2.0813
交流220kV | 2005-06-20 | 2011-12-28 | 6.526 | 13 | 628 | 3207 | 14 | 2 | 3 | 0 | 19 | 0 | 0 | 0 | 5.1067
交流220kV | 2005-09-04 | 2012-03-13 | 6.526 | 5 | 430 | 604 | 16.98 | 1.56 | 2.82 | 0 | 21.36 | 0.018 | 0.133 | 52.6 | 1.4047
交流220kV | 2005-06-20 | 2011-12-30 | 6.5315 | 6.2 | 447.5 | 2928 | 10.6 | 2.6 | 3.2 | 0 | 16.4 | 0 | 0 | 0 | 6.543
交流220kV | 2006-11-23 | 2013-06-06 | 6.5397 | 8.7 | 611.5 | 611.5 | 9.3 | 11.3 | 0 | 0 | 20.6 | 0.026 | 0.176 | 0 | 1
交流220kV | 2006-07-26 | 2013-02-06 | 6.5397 | 7.9 | 271 | 598.6 | 11.2 | 0.6 | 1.5 | 0 | 13.3 | 0.008 | 0.117 | 63.4 | 2.2089
交流220kV | 2005-09-01 | 2012-03-16 | 6.5425 | 15.84 | 400.93 | 1508.34 | 5 | 0.71 | 1.26 | 0 | 6.97 | 0.007 | 0.001 | 54 | 3.7621
交流220kV | 2005-09-01 | 2012-03-16 | 6.5425 | 14.91 | 483.8 | 770.41 | 3.98 | 0.96 | 1.24 | 0 | 6.18 | 0.004 | 0.001 | 54 | 1.5924
交流220kV | 2007-08-13 | 2014-03-04 | 6.5616 | 23.8 | 44.2 | 1069.8 | 6.5 | 1.2 | 1.6 | 0.1 | 9.4 | 0.011 | 0.001 | 58 | 24.2036
交流220kV | 2005-11-01 | 2012-05-26 | 6.5699 | 53.55 | 551.61 | 743.7 | 5.84 | 1.16 | 1.37 | 0 | 8.37 | 0.015 | 0.001 | 52 | 1.3482
交流220kV | 2003-07-03 | 2010-01-27 | 6.5753 | 8 | 789 | 583 | 12.1 | 1.6 | 3.7 | 0 | 17.4 | 0.011 | 0.005 | 55 | 0.73891
交流220kV | 2006-10-24 | 2013-05-24 | 6.5863 | 28.12 | 120.9 | 2460.7 | 5.23 | 0.7 | 1.3 | 0 | 7.23 | 0.002 | 0.1 | 42 | 20.3532
交流220kV | 2005-05-16 | 2011-12-16 | 6.589 | 86.6 | 159 | 1240 | 6.3 | 1.3 | 1.4 | 0 | 9 | 0 | 0 | 0 | 7.7987
交流220kV | 2005-05-16 | 2011-12-16 | 6.589 | 6.8 | 239 | 6345 | 5.2 | 1.6 | 2.4 | 0 | 9.2 | 0 | 0 | 0 | 26.5481
220 | 2007-08-17 | 2014-03-19 | 6.5918 | 76.64 | 179.81 | 2844.67 | 9.54 | 0.73 | 2.61 | 0 | 12.88 | 0.016 | 0.152 | 52 | 15.8204
交流220kV | 2005-07-31 | 2012-03-02 | 6.5918 | 90.35 | 694.73 | 3276.33 | 8.48 | 1.2 | 1.99 | 0 | 11.67 | 0.01 | 1.181 | 52 | 4.716
交流220kV | 2004-11-12 | 2011-06-16 | 6.5945 | 20.23 | 819.61 | 1261.12 | 24.68 | 33.89 | 5.12 | 3.23 | 66.92 | 0.003 | 0.02 | 43 | 1.5387
交流220kV | 2005-05-10 | 2011-12-13 | 6.5973 | 155.18 | 300.32 | 2341.76 | 337.81 | 337.11 | 151.01 | 0 | 825.93 | 0.003 | 0.02 | 49 | 7.7975
交流220kV | 2007-07-11 | 2014-02-13 | 6.6 | 3.25 | 526.7 | 512.13 | 15.78 | 0.76 | 1.98 | 0 | 18.52 | 0.005 | 0.025 | 62.8 | 0.97234
交流220kV | 2005-11-28 | 2012-07-06 | 6.6082 | 10.3 | 630.6 | 1397.4 | 8.9 | 1.9 | 1.8 | 0.1 | 12.7 | 0.01 | 0.05 | 60 | 2.216
交流220kV | 2007-03-20 | 2013-10-30 | 6.6192 | 10.9 | 390.1 | 666.42 | 5.9 | 0.71 | 0.79 | 0 | 7.4 | 0.006 | 0.012 | 64.5 | 1.7083
220 | 2007-08-06 | 2014-03-19 | 6.6219 | 48.99 | 171.22 | 1592.33 | 8.04 | 0.74 | 2.22 | 0 | 11 | 0.012 | 0.112 | 52 | 9.2999
交流220kV | 2005-05-10 | 2011-12-23 | 6.6247 | 169.14 | 321.17 | 2513.4 | 360.34 | 377.29 | 162.06 | 0 | 899.69 | 0.003 | 0.2 | 48 | 7.8258
交流220kV | 2007-04-30 | 2013-12-12 | 6.6247 | 10.3 | 685 | 3612.3 | 8.2 | 3.4 | 1.9 | 0 | 13.5 | 0 | 0 | 0 | 5.2734
交流220kV | 2004-08-30 | 2011-04-14 | 6.6247 | 4 | 337 | 375 | 6.7 | 0.73 | 1.72 | 0 | 9.15 | 0.003 | 0.038 | 59 | 1.1128
交流220kV | 2005-06-03 | 2012-01-16 | 6.6247 | 36.39 | 221.55 | 3388.07 | 7.83 | 0.91 | 2.1 | 0 | 10.84 | 0.01 | 0.127 | 49.6 | 15.2926
交流220kV | 2007-04-20 | 2013-12-04 | 6.6301 | 10.5 | 331 | 823 | 5.9 | 0.4 | 0.5 | 0 | 6.8 | 0.03 | 0.4 | 50 | 2.4864
交流220kV | 2005-08-23 | 2012-04-12 | 6.6411 | 27.52 | 335 | 1163.53 | 8.8 | 0.82 | 1.75 | 0.21 | 11.58 | 0.001 | 0.2 | 42 | 3.4732
交流220kV | 2006-10-08 | 2013-05-28 | 6.6411 | 40.4 | 223.8 | 2549.2 | 5.7 | 0 | 0 | 0 | 5.7 | 0 | 0 | 0 | 11.3905
交流220kV | 2007-04-30 | 2013-12-20 | 6.6466 | 97.3 | 65.87 | 622.31 | 18.7 | 11.75 | 4.94 | 0 | 35.39 | 0 | 0 | 69 | 9.4475
交流220kV | 2006-02-20 | 2012-10-12 | 6.6466 | 3.56 | 509.62 | 1634.9 | 9.94 | 0.77 | 1.63 | 0 | 12.34 | 0.018 | 0.24 | 51 | 3.2081
交流220kV | 2007-02-14 | 2013-10-10 | 6.6575 | 8.29 | 894.73 | 1954.03 | 10.89 | 0.97 | 1.13 | 0 | 12.99 | 0.011 | 0.152 | 65.5 | 2.1839
交流220kV | 2006-09-04 | 2013-05-03 | 6.6658 | 6.9 | 359.7 | 1449.1 | 6.3 | 3 | 5.9 | 0 | 15.2 | 0.008 | 0.08 | 53.5 | 4.0286
交流220kV | 2005-06-13 | 2012-02-10 | 6.6658 | 104.26 | 129.48 | 1340.71 | 3.12 | 0 | 0 | 0 | 3.12 | 0 | 0 | 0 | 10.3546
交流220kV | 2004-10-10 | 2011-06-09 | 6.6658 | 138 | 362 | 3308 | 8.4 | 0.5 | 1.9 | 0 | 10.8 | 0.006 | 0.001 | 50 | 9.1381
交流220kV | 2005-05-10 | 2012-01-09 | 6.6712 | 139.48 | 299.85 | 2264.43 | 368.92 | 382.21 | 174.81 | 0 | 925.94 | 0.003 | 0.2 | 48 | 7.5519
交流220kV | 2005-12-26 | 2012-08-28 | 6.6767 | 7.04 | 1183.61 | 6033.75 | 14.87 | 6.17 | 4.31 | 0 | 25.35 | 0.011 | 0.002 | 44 | 5.0978
交流220kV | 2007-04-09 | 2013-12-11 | 6.6795 | 16.2 | 728.9 | 1755.1 | 16.3 | 1.3 | 1.7 | 0.1 | 19.4 | 0 | 0 | 0 | 2.4079
交流220kV | 2007-04-28 | 2013-12-31 | 6.6822 | 7.18 | 403.23 | 4209.38 | 9.28 | 0.82 | 1.73 | 0 | 11.83 | 0 | 0 | 0 | 10.4392
交流220kV | 2006-09-28 | 2013-06-05 | 6.6904 | 7.42 | 984.27 | 2876.62 | 12.52 | 1.73 | 1.14 | 0 | 15.39 | 0.001 | 0.033 | 67.8 | 2.9226
交流220kV | 2005-09-04 | 2012-05-16 | 6.7014 | 41.5 | 680.2 | 3067.2 | 14.3 | 1.8 | 2.4 | 0 | 18.5 | 0.005 | 0 | 72.7 | 4.5093
交流220kV | 2004-10-26 | 2011-07-08 | 6.7014 | 8.84 | 158.69 | 418.81 | 5.06 | 1.27 | 0.56 | 0 | 6.89 | 0.003 | 0.001 | 62 | 2.6392
交流220kV | 2004-10-26 | 2011-07-08 | 6.7014 | 6.35 | 165.76 | 655.03 | 6.29 | 1.79 | 0.72 | 0 | 8.8 | 0.003 | 0.001 | 62 | 3.9517
交流220kV | 2006-07-08 | 2013-03-20 | 6.7041 | 18.23 | 45 | 296 | 5.2 | 0 | 0.9 | 0 | 6.1 | 0.009 | 0.002 | 46 | 6.5778
交流220kV | 2004-04-23 | 2011-01-06 | 6.7096 | 2 | 285.4 | 1890.7 | 5.3 | 0.6 | 1.2 | 0 | 7.1 | 0.013 | 0.4 | 70.4 | 6.6247
220 | 2006-06-19 | 2013-03-04 | 6.7123 | 54.8 | 136.59 | 765.2 | 4.63 | 0.45 | 0.61 | 0 | 5.69 | 0.006 | 0.188 | 58 | 5.6022
交流220kV | 2006-06-26 | 2013-03-14 | 6.7205 | 102.2 | 175.4 | 2546.1 | 57 | 18.7 | 50 | 0.1 | 125.8 | 0.009 | 0.06 | 56.4 | 14.516
交流220kV | 2005-12-29 | 2012-09-19 | 6.7288 | 8.06 | 512.36 | 1023.08 | 7.31 | 2.03 | 2.14 | 0 | 11.48 | 0.012 | 0.051 | 56.4 | 1.9968
交流220kV | 2006-07-26 | 2013-04-18 | 6.7342 | 49.4 | 86.3 | 645.4 | 29.2 | 12.9 | 13.6 | 0.2 | 55.9 | 0.007 | 0.2 | 59.1 | 7.4786
交流220kV | 2005-05-10 | 2012-02-01 | 6.7342 | 148.44 | 293.1 | 2091.01 | 389.68 | 378.48 | 172.19 | 0 | 940.35 | 0.003 | 0.2 | 48 | 7.1341
交流220kV | 2006-06-28 | 2013-03-28 | 6.7534 | 5 | 542 | 3026 | 9.9 | 0.6 | 2.3 | 0 | 12.8 | 0.012 | 0.2 | 58 | 5.583
交流220kV | 2005-05-10 | 2012-02-09 | 6.7562 | 162.28 | 307.32 | 2167.41 | 404.94 | 395.21 | 181.09 | 0 | 981.24 | 0.002 | 0.25 | 48 | 7.0526
交流220kV | 2005-06-24 | 2012-03-26 | 6.7589 | 23 | 190.9 | 721.95 | 0.27 | 15.41 | 0 | 0.49 | 16.17 | 0 | 0 | 0 | 3.7818
交流220kV | 2001-10-09 | 2008-07-18 | 6.7781 | 10.43 | 522.97 | 3096.96 | 9.15 | 1.09 | 1.67 | 0 | 11.91 | 0.003 | 0.002 | 54.6 | 5.9219
220 | 2006-05-29 | 2013-03-11 | 6.789 | 5.34 | 493.42 | 801.33 | 5.89 | 0.54 | 0.75 | 0 | 7.18 | 0.006 | 0.078 | 58 | 1.624
交流220kV | 2006-06-30 | 2013-04-15 | 6.7973 | 20 | 241 | 3452 | 4.9 | 0.5 | 1.7 | 0 | 7.1 | 0.014 | 0.001 | 70 | 14.3237
交流220kV | 2006-01-05 | 2012-10-22 | 6.8 | 5.18 | 213.16 | 1070.45 | 3.9 | 0.28 | 0.78 | 0 | 4.96 | 0.008 | 0.002 | 60 | 5.0218
交流220kV | 2005-06-07 | 2012-03-27 | 6.8082 | 22.65 | 376.07 | 326.73 | 12.5 | 0.7 | 1.97 | 0 | 15.17 | 0.006 | 0.21 | 55 | 0.8688
交流220kV | 2005-05-10 | 2012-03-01 | 6.8137 | 159.79 | 314.79 | 2205 | 402.21 | 404.44 | 208.71 | 0 | 1015.36 | 0.003 | 0.2 | 48 | 7.0047
交流220kV | 2007-01-25 | 2013-11-18 | 6.8192 | 108.46 | 155.1 | 1626.28 | 0 | 0.88 | 1.45 | 0 | 2.33 | 0.003 | 0.25 | 51 | 10.4854
交流220kV | 2005-04-27 | 2012-02-22 | 6.8274 | 40 | 383 | 570 | 24.46 | 1.04 | 5.49 | 0 | 30.99 | 0.001 | 0.001 | 50.8 | 1.4883
交流220kV | 2006-07-08 | 2013-05-07 | 6.8356 | 10.87 | 38 | 341 | 5.71 | 0.24 | 1.02 | 0 | 6.97 | 0.014 | 0.004 | 45 | 8.9737
交流220kV | 2004-11-12 | 2011-09-18 | 6.8521 | 21.09 | 816.91 | 1246.12 | 24.56 | 34.03 | 5.12 | 3.09 | 66.8 | 0.003 | 0.03 | 44 | 1.5254
交流220kV | 2006-12-30 | 2013-11-05 | 6.8548 | 6.47 | 85.32 | 579.06 | 2.54 | 0.63 | 0.49 | 0 | 3.66 | 0.026 | 0.21 | 58 | 6.7869
交流220kV | 2007-01-13 | 2013-11-20 | 6.8575 | 4.56 | 492.66 | 1168.76 | 18.18 | 3.76 | 5.39 | 0 | 27.33 | 0.001 | 0.1 | 44 | 2.3723
交流220kV | 2006-07-09 | 2013-05-16 | 6.8575 | 11 | 18.6 | 502 | 1.5 | 0.5 | 0 | 0 | 2 | 0.026 | 0.001 | 50 | 26.9892
220 | 2004-11-24 | 2011-10-10 | 6.8795 | 14 | 527 | 3429 | 18.5 | 2 | 1.5 | 0 | 22 | 0.007 | 0.001 | 55 | 6.5066
交流220kV | 2006-12-09 | 2013-10-24 | 6.8795 | 4.09 | 575.79 | 1224.66 | 6.97 | 3.07 | 0 | 0 | 10.04 | 0.027 | 0.32 | 50 | 2.1269
交流220kV | 2006-04-15 | 2013-03-02 | 6.8849 | 7.31 | 249.17 | 998.08 | 13.64 | 6.87 | 6.24 | 0 | 26.75 | 0.01 | 0.1 | 52.4 | 4.0056
交流220kV | 2005-12-20 | 2012-11-07 | 6.8877 | 6.2 | 1065.7 | 968.1 | 15.8 | 7.3 | 3.9 | 0.1 | 27.1 | 0.015 | 0.132 | 54.3 | 0.90842
交流220kV | 2006-03-19 | 2013-02-06 | 6.8932 | 3 | 169 | 1090.2 | 47.7 | 1.7 | 32.8 | 0 | 82.2 | 0.007 | 0.135 | 61.4 | 6.4509
交流220kV | 2005-04-03 | 2012-02-22 | 6.8932 | 22 | 322 | 305 | 21.94 | 4.23 | 5.17 | 0 | 31.34 | 0.001 | 0.001 | 59.8 | 0.9472
交流220kV | 2007-02-02 | 2013-12-25 | 6.8986 | 54.17 | 246.97 | 1665.76 | 24.32 | 1.24 | 12.67 | 0 | 38.23 | 0.008 | 0.32 | 65 | 6.7448
交流220kV | 2005-06-20 | 2012-05-16 | 6.9096 | 7.3 | 562.3 | 4111.7 | 15.7 | 3.6 | 3.2 | 0 | 22.5 | 0.012 | 0 | 66.5 | 7.3123
交流220kV | 2004-10-20 | 2011-09-16 | 6.9096 | 14 | 458 | 2453 | 3.8 | 3.4 | 1.1 | 0.1 | 8.4 | 0.06 | 0.024 | 61 | 5.3559
交流220kV | 2006-07-08 | 2013-06-06 | 6.9178 | 1.7 | 358.76 | 1160.39 | 5.4 | 0 | 0 | 0 | 5.4 | 0.007 | 0.3 | 43 | 3.2344
交流220kV | 2006-02-21 | 2013-01-21 | 6.9205 | 7.28 | 791.48 | 3002.26 | 5.51 | 0.92 | 1.21 | 0.1 | 7.74 | 0.013 | 0.006 | 62.3 | 3.7932
220 | 2006-04-16 | 2013-03-20 | 6.9315 | 5.12 | 293.02 | 2514.59 | 7.21 | 0.71 | 1.88 | 0 | 9.8 | 0.05 | 0.082 | 57 | 8.5816
交流220kV | 2005-01-16 | 2011-12-22 | 6.9342 | 32.4 | 147.82 | 806.34 | 9.04 | 1.22 | 1.87 | 0 | 12.13 | 0 | 0 | 0 | 5.4549
交流220kV | 2005-06-20 | 2012-05-25 | 6.9342 | 13 | 628 | 3239 | 12 | 2 | 2 | 0 | 16 | 0.049 | 0 | 50 | 5.1576
交流220kV | 2006-03-26 | 2013-03-02 | 6.9397 | 11.15 | 262.53 | 1713.5 | 18.03 | 8.08 | 8.74 | 0 | 34.85 | 0.01 | 0.08 | 49.6 | 6.5269
交流220kV | 2001-06-04 | 2008-05-12 | 6.9425 | 5 | 994.5 | 2469.2 | 10.5 | 1.2 | 2.8 | 0 | 14.5 | 0.008 | 0.005 | 48.3 | 2.4829
交流220kV | 2006-06-19 | 2013-05-28 | 6.9452 | 110.2 | 132.7 | 2752.8 | 80.2 | 74.7 | 31.2 | 0 | 186.1 | 0 | 0 | 0 | 20.7445
交流220kV | 2005-12-25 | 2012-12-04 | 6.9479 | 5.25 | 258.24 | 1195.39 | 4.24 | 0.68 | 0.58 | 0 | 5.5 | 0.009 | 0.004 | 61 | 4.629
交流220kV | 2005-12-25 | 2012-12-04 | 6.9479 | 7.41 | 326.11 | 852.18 | 4.36 | 4.14 | 2.03 | 0 | 10.53 | 0.009 | 0.002 | 60 | 2.6132
交流220kV | 2005-12-25 | 2012-12-04 | 6.9479 | 5.49 | 313.21 | 1037.99 | 4.6 | 3.16 | 2.13 | 0 | 9.89 | 0.009 | 0.002 | 59 | 3.314
交流220kV | 2005-12-25 | 2012-12-04 | 6.9479 | 4.84 | 241.99 | 1122.99 | 4.24 | 0.59 | 0.49 | 0 | 5.32 | 0.011 | 0.002 | 62 | 4.6406
交流220kV | 2006-01-19 | 2012-12-31 | 6.9534 | 6.75 | 653.99 | 1480.41 | 5.69 | 1.85 | 0.99 | 0 | 8.53 | 0 | 0 | 0 | 2.2637
交流220kV | 2006-10-10 | 2013-09-23 | 6.9589 | 5 | 257 | 651 | 4 | 0 | 0 | 0 | 4 | 0.012 | 0.215 | 45 | 2.5331
交流220kV | 2006-10-10 | 2013-09-24 | 6.9616 | 5 | 438 | 950 | 4 | 0 | 0 | 0 | 4 | 0.012 | 0.193 | 45 | 2.1689
交流220kV | 2006-06-06 | 2013-05-22 | 6.9644 | 67.9 | 184.8 | 595.6 | 6.8 | 0.8 | 0 | 0 | 7.6 | 0.032 | 2.2 | 51 | 3.2229
交流220kV | 2005-06-02 | 2012-05-18 | 6.9644 | 12.2 | 1114.3 | 7834.4 | 11.2 | 61.7 | 2.5 | 0 | 75.4 | 0.009 | 0.09 | 52.4 | 7.0308
交流220kV | 2005-06-03 | 2012-05-23 | 6.9753 | 27 | 206 | 2396 | 6 | 1.3 | 1.4 | 0 | 8.7 | 0.002 | 0.003 | 55 | 11.6311
交流220kV | 2005-06-30 | 2012-06-21 | 6.9808 | 3.8 | 406.74 | 1392.01 | 6.79 | 0.3 | 1.31 | 0 | 8.4 | 0 | 0 | 0 | 3.4224
交流220kV | 2005-11-15 | 2012-11-07 | 6.9836 | 10.9 | 1152.6 | 1212.3 | 14.9 | 0 | 2.7 | 0 | 17.6 | 0.015 | 0.126 | 51.4 | 1.0518
220 | 2004-01-10 | 2011-01-04 | 6.989 | 2.16 | 3.73 | 244.97 | 0.63 | 0.01 | 0.04 | 0 | 0.68 | 0.014 | 0.004 | 54 | 65.6756
交流220kV | 2002-04-16 | 2009-04-12 | 6.9945 | 10.49 | 577.21 | 4323.41 | 3.43 | 93.16 | 7.15 | 0.3 | 104.04 | 0.048 | 0.317 | 50 | 7.4902
交流220kV | 2005-05-10 | 2012-05-07 | 6.9973 | 157.68 | 311.62 | 2199.14 | 395.65 | 403.27 | 189.23 | 0 | 988.15 | 0.002 | 0.2 | 49 | 7.0571
交流220kV | 2006-06-26 | 2013-06-25 | 7.0027 | 114.2 | 171.3 | 2927.9 | 56.2 | 53.9 | 19.5 | 0.1 | 129.7 | 0 | 0 | 0 | 17.0922
交流220kV | 2005-12-14 | 2012-12-14 | 7.0055 | 28.93 | 402.11 | 3794.56 | 10.96 | 1.02 | 2.76 | 0.23 | 14.97 | 0.001 | 0.2 | 40 | 9.4366
交流220kV | 2005-06-24 | 2012-07-03 | 7.0301 | 23.68 | 366.16 | 965.73 | 6.04 | 0.4 | 0 | 0 | 6.44 | 0.001 | 0 | 67.2 | 2.6375
交流220kV | 2006-03-24 | 2013-04-02 | 7.0301 | 8.3 | 517.5 | 2729 | 13 | 0.6 | 2.1 | 0 | 15.7 | 0.003 | 0.04 | 53.8 | 5.2734
交流220kV | 2006-06-14 | 2013-06-25 | 7.0356 | 12.2 | 542.2 | 5371.9 | 11.8 | 1.3 | 4.5 | 0 | 17.6 | 0.023 | 0 | 55.1 | 9.9076
交流220kV | 2005-06-13 | 2012-06-25 | 7.0384 | 145.17 | 175.44 | 2900.31 | 7.92 | 0 | 0 | 0 | 7.92 | 0 | 0 | 45 | 16.5316
交流220kV | 2005-03-15 | 2012-03-27 | 7.0384 | 13.1 | 288.38 | 144.6 | 10.25 | 1.05 | 2.14 | 0 | 13.44 | 0.006 | 0.15 | 54 | 0.50142
交流220kV | 2006-11-23 | 2013-12-12 | 7.0575 | 5.3 | 558.6 | 2405.8 | 8.6 | 9.1 | 0 | 0 | 17.7 | 0 | 0 | 0 | 4.3068
交流220kV | 2004-09-26 | 2011-10-18 | 7.063 | 17.24 | 1031.75 | 3235.97 | 12.99 | 1.38 | 1.78 | 0 | 16.15 | 0.041 | 0.001 | 62 | 3.1364
交流220kV | 2006-10-24 | 2013-11-18 | 7.074 | 21.57 | 108.38 | 2418.36 | 4.57 | 0.62 | 1.11 | 0 | 6.3 | 0.003 | 0.25 | 51 | 22.3137
交流220kV | 2006-04-28 | 2013-05-23 | 7.074 | 6.62 | 246.09 | 862.82 | 7.26 | 0.94 | 1.44 | 0 | 9.64 | 0.06 | 0.001 | 60 | 3.5061
交流220kV | 2006-06-06 | 2013-07-03 | 7.0795 | 22 | 61 | 520 | 10 | 1 | 3 | 0 | 14 | 0.046 | 0.066 | 53 | 8.5246
交流220kV | 2006-09-10 | 2013-10-10 | 7.0877 | 115.21 | 89.12 | 4396.74 | 11.13 | 4.94 | 6.65 | 0 | 22.72 | 0 | 0.056 | 50 | 49.3351
交流220kV | 2002-12-15 | 2010-01-18 | 7.0986 | 6 | 661 | 2057 | 16.3 | 8.8 | 3.7 | 0 | 28.8 | 0.001 | 0.021 | 52 | 3.112
交流220kV | 2006-09-06 | 2013-10-11 | 7.1014 | 19.49 | 659.13 | 1477.71 | 7.82 | 2.31 | 2.04 | 0 | 12.17 | 0.01 | 0.08 | 48 | 2.2419
交流220kV | 2004-11-12 | 2011-12-19 | 7.1041 | 13.62 | 862.23 | 1623.32 | 27.31 | 41.92 | 7.09 | 3.8 | 80.12 | 0.003 | 0.02 | 44 | 1.8827
交流220kV | 2006-02-20 | 2013-03-28 | 7.1041 | 1.7 | 338.4 | 1476.47 | 8.66 | 0.83 | 1.47 | 0.06 | 11.02 | 0.018 | 0.25 | 56 | 4.3631
交流220kV | 2001-10-09 | 2008-11-22 | 7.126 | 11.5 | 512.3 | 3216.7 | 10.4 | 1.2 | 1.6 | 0 | 13.2 | 0.006 | 0.008 | 45.4 | 6.2789
交流220kV | 2007-01-30 | 2014-03-19 | 7.137 | 4 | 433 | 1341 | 25.42 | 2.14 | 3.78 | 0 | 31.34 | 0.001 | 0.03 | 50 | 3.097
交流220kV | 2006-04-08 | 2013-05-27 | 7.1397 | 13.51 | 376.65 | 960.99 | 6.85 | 1.95 | 1.04 | 0 | 9.84 | 0.007 | 0.001 | 59 | 2.5514
交流220kV | 2003-05-01 | 2010-06-25 | 7.1562 | 1.04 | 3.14 | 539.92 | 1.12 | 0.2 | 0.35 | 0 | 1.67 | 0.021 | 0.094 | 45 | 171.949
交流220kV | 2003-01-08 | 2010-03-09 | 7.1699 | 7.67 | 169.96 | 1073.47 | 3.88 | 1.45 | 0.81 | 0 | 6.14 | 0.015 | 0.424 | 45 | 6.316
交流220kV | 2005-12-16 | 2013-02-18 | 7.1808 | 10 | 22.7 | 971 | 1.5 | 0 | 0.1 | 0 | 1.6 | 0.016 | 0.001 | 48 | 42.7753
交流220kV | 2002-11-15 | 2010-01-18 | 7.1808 | 26 | 412 | 694 | 7.5 | 3.8 | 1.5 | 0 | 12.8 | 0.01 | 0.002 | 55 | 1.6845
220 | 2005-04-27 | 2012-07-02 | 7.1863 | 12.56 | 448.25 | 1740.16 | 6.65 | 0.53 | 1.52 | 0 | 8.7 | 0.018 | 0.028 | 60 | 3.8821
交流220kV | 2006-10-08 | 2013-12-17 | 7.1973 | 42.9 | 281.5 | 2855.3 | 7.2 | 0 | 9.3 | 0 | 16.5 | 0.06 | 1.9 | 46 | 10.1432
交流220kV | 2005-01-16 | 2012-03-28 | 7.2 | 8.25 | 58.63 | 680.11 | 6.9 | 1.1 | 1.79 | 0 | 9.79 | 0 | 0 | 44.7 | 11.6
交流220kV | 2006-07-08 | 2013-09-18 | 7.2027 | 2.14 | 356.59 | 1102.81 | 4.88 | 0 | 1.94 | 0 | 6.82 | 0.01 | 0.3 | 60 | 3.0927
交流220kV | 2006-01-06 11:08 | 2013-03-20 | 7.2042 | 26 | 183 | 505 | 28.2 | 10.74 | 54.94 | 0 | 93.88 | 0.001 | 0.05 | 62.8 | 2.7596
交流220kV | 2006-09-28 | 2013-12-10 | 7.2055 | 6.65 | 1059.89 | 2785.91 | 13.5 | 1.69 | 1.25 | 0 | 16.44 | 0 | 0 | 0 | 2.6285
交流220kV | 2003-12-12 | 2011-02-23 | 7.2055 | 24 | 1169 | 3905 | 23.21 | 18.02 | 8.98 | 0 | 50.21 | 0.001 | 0.002 | 50 | 3.3405
交流220kV | 2004-10-01 | 2011-12-16 | 7.211 | 17 | 379 | 2073 | 4.1 | 0.7 | 0.6 | 0.1 | 5.5 | 0.002 | 0.003 | 71 | 5.4697
交流220kV | 2004-10-31 | 2012-01-16 | 7.2137 | 11.18 | 405.84 | 2796.75 | 15.9 | 27.43 | 5.99 | 0 | 49.32 | 0.011 | 0.005 | 50.2 | 6.8913
交流220kV | 2004-11-21 | 2012-02-06 | 7.2137 | 4.6 | 223.4 | 893.3 | 29 | 4.5 | 5.1 | 0 | 38.6 | 0.007 | 0.064 | 73.2 | 3.9987
交流220kV | 2004-10-23 | 2012-01-10 | 7.2192 | 11.7 | 507.89 | 1332.12 | 45.06 | 4.82 | 6.9 | 0 | 56.78 | 0.004 | 0.15 | 55 | 2.6229
交流220kV | 1997-02-24 | 2004-05-14 | 7.2219 | 8.8 | 384 | 1690.4 | 11.5 | 12.4 | 28.5 | 0.8 | 53.2 | 0.005 | 0.273 | 50 | 4.4021
交流220kV | 2006-12-28 | 2014-03-18 | 7.2247 | 66.32 | 163.88 | 2843.15 | 6.78 | 2.03 | 1.76 | 0 | 10.57 | 0 | 0.089 | 42.1 | 17.349
交流220kV | 2006-02-21 | 2013-05-14 | 7.2301 | 8.87 | 813.73 | 3062.31 | 5.74 | 1.05 | 1.44 | 0 | 8.23 | 0.011 | 0.001 | 60.7 | 3.7633
交流220kV | 2006-06-19 | 2013-09-10 | 7.2329 | 113.1 | 153.4 | 2839.1 | 83.8 | 85.3 | 30.9 | 0 | 200 | 0 | 0 | 0 | 18.5078
交流220kV | 1999-04-13 | 2006-07-07 | 7.2384 | 5.9 | 870.25 | 6437.31 | 18.32 | 75.58 | 3.54 | 0 | 97.44 | 0.013 | 0.482 | 51.5 | 7.3971
交流220kV | 2005-12-24 | 2013-03-20 | 7.2411 | 4.7 | 351.9 | 1010.6 | 5.5 | 0.5 | 1.1 | 0.06 | 7.16 | 0.006 | 0.169 | 47.2 | 2.8718
交流220kV | 2006-01-24 | 2013-04-24 | 7.2521 | 24 | 272 | 339 | 5.4 | 0 | 0 | 0 | 5.4 | 0.001 | 0.004 | 51 | 1.2463
220 | 2006-11-28 | 2014-02-28 | 7.2575 | 7.36 | 443.31 | 1798.07 | 10.48 | 2 | 2.59 | 0 | 15.07 | 0.088 | 0.024 | 59.5 | 4.056
交流220kV | 2006-07-09 | 2013-10-11 | 7.263 | 9.1 | 22 | 463 | 1.4 | 0.5 | 1.2 | 0 | 3.1 | 0.026 | 0.001 | 50 | 21.0455
交流220kV | 2005-11-02 | 2013-02-06 | 7.2685 | 5 | 428.6 | 2857.7 | 11.5 | 0.7 | 3.2 | 0 | 15.4 | 0.008 | 0.192 | 63.4 | 6.6675
交流220kV | 2004-10-31 | 2012-02-06 | 7.2712 | 11.6 | 291.2 | 796.7 | 21 | 10 | 19.9 | 0 | 50.9 | 0.006 | 0.108 | 59 | 2.7359
交流220kV | 2005-09-04 | 2012-12-11 | 7.274 | 10.9 | 436.8 | 2010.9 | 8.9 | 1.3 | 1.7 | 0 | 11.9 | 0 | 0 | 0 | 4.6037
交流220kV | 2005-07-31 | 2012-11-06 | 7.274 | 8.5 | 594.5 | 1381.3 | 6.8 | 0 | 0.5 | 0 | 7.3 | 0.012 | 0.073 | 53.6 | 2.3235
交流220kV | 2005-07-31 | 2012-11-06 | 7.274 | 9.8 | 678.8 | 1452.7 | 8.3 | 0 | 0.7 | 0 | 9 | 0.012 | 0.078 | 54.3 | 2.1401
交流220kV | 2005-01-16 | 2012-04-25 | 7.2767 | 8.25 | 58.63 | 680.11 | 6.9 | 1.1 | 1.79 | 0 | 9.79 | 0 | 0 | 61 | 11.6
交流220kV | 2006-09-04 | 2013-12-13 | 7.2795 | 5.6 | 315.2 | 1405.3 | 4 | 1 | 1.8 | 0 | 6.8 | 0 | 0 | 0 | 4.4584
交流220kV | 2001-03-15 | 2008-06-26 | 7.2877 | 6.89 | 317.63 | 1539.48 | 15.54 | 5.27 | 6.98 | 0 | 27.79 | 0.023 | 0.003 | 42.8 | 4.8468
交流220kV | 2005-11-22 | 2013-03-06 | 7.2904 | 1.4 | 312.4 | 733.1 | 6.5 | 0.8 | 1.7 | 0 | 9 | 0.011 | 0.432 | 48.8 | 2.3467
交流220kV | 2004-12-15 | 2012-04-01 | 7.2986 | 8 | 569.6 | 1147.4 | 6.2 | 1 | 2.1 | 0.1 | 9.4 | 0.002 | 0.08 | 54.4 | 2.0144
交流220kV | 2004-07-01 | 2011-10-21 | 7.3096 | 7.4 | 413.1 | 1911.5 | 4.6 | 1.3 | 0.7 | 0 | 6.6 | 0.001 | 0.04 | 70 | 4.6272
交流220kV | 2005-08-23 | 2012-12-13 | 7.3123 | 24.23 | 371.4 | 1389.02 | 9.78 | 0.82 | 1.88 | 0.23 | 12.71 | 0.003 | 0.2 | 42 | 3.74
交流220kV | 2005-09-14 | 2013-01-07 | 7.3205 | 2 | 89 | 1295 | 5.99 | 2.2 | 3.17 | 0 | 11.36 | 0.003 | 2.367 | 64 | 14.5506
交流220kV | 2005-12-30 | 2013-04-26 | 7.326 | 18.22 | 349.95 | 742.86 | 6.59 | 0.92 | 0.85 | 0 | 8.36 | 0.06 | 0.001 | 58 | 2.1228
交流220kV | 2004-12-05 | 2012-04-01 | 7.326 | 3.6 | 169.1 | 1065.5 | 2.2 | 0.9 | 0.3 | 0 | 3.4 | 0.002 | 0.13 | 58.8 | 6.301
交流220kV | 2006-06-30 | 2013-10-25 | 7.326 | 43 | 192 | 3060 | 6.9 | 0.6 | 1.8 | 0 | 9.3 | 0.021 | 0.008 | 65 | 15.9375
交流220kV | 2004-06-10 | 2011-10-10 | 7.337 | 20 | 1168 | 5883 | 28.3 | 3.5 | 5.1 | 0.5 | 37.4 | 0.023 | 0.004 | 59 | 5.0368
交流220kV | 2004-12-16 | 2012-04-17 | 7.3397 | 6.74 | 1296.44 | 4827.33 | 13.31 | 18.35 | 5.56 | 0 | 37.22 | 0.007 | 0.1 | 54 | 3.7235
交流220kV | 2006-06-02 | 2013-10-10 | 7.3616 | 1.12 | 229.71 | 989 | 3.99 | 0.36 | 0.51 | 0 | 4.86 | 0.012 | 0.223 | 60.3 | 4.3054
220 | 2004-11-24 | 2012-04-09 | 7.3781 | 5 | 274 | 16 | 4.7 | 0.1 | 0.1 | 0 | 4.9 | 0.008 | 0.088 | 52 | 0.058394
交流220kV | 2004-11-12 | 2012-03-28 | 7.3781 | 15.55 | 771.93 | 1408.41 | 25.3 | 37.77 | 7.16 | 3.08 | 73.31 | 0.002 | 0.2 | 51 | 1.8245
交流220kV | 1997-11-25 | 2005-04-11 | 7.3808 | 51.48 | 582.38 | 882.74 | 9.9 | 3.82 | 6.35 | 1.33 | 21.4 | 0.006 | 2 | 54.8 | 1.5157
交流220kV | 2006-06-13 | 2013-10-30 | 7.3863 | 10.04 | 719.8 | 1074.16 | 8.44 | 0.52 | 0.99 | 0 | 9.95 | 0.008 | 0.023 | 66.3 | 1.4923
交流220kV | 2006-01-19 | 2013-06-08 | 7.389 | 3.46 | 626 | 1583.7 | 9.79 | 1.95 | 1.27 | 0 | 13.01 | 0 | 0 | 0 | 2.5299
交流220kV | 2005-11-01 | 2013-04-01 | 7.4192 | 48.94 | 534.4 | 927.03 | 7.03 | 1.68 | 1.85 | 0 | 10.56 | 0.012 | 0.195 | 60.6 | 1.7347
交流220kV | 2004-11-16 | 2012-04-17 | 7.4219 | 4.26 | 1652.52 | 3703.83 | 7.49 | 7.29 | 3.49 | 0 | 18.27 | 0.006 | 0.1 | 56 | 2.2413
交流220kV | 2002-04-16 | 2009-09-16 | 7.4247 | 9.77 | 6.63 | 57.31 | 0.17 | 0 | 0 | 0 | 0.17 | 0.004 | 0.085 | 52 | 8.644
交流220kV | 2004-01-08 | 2011-06-20 | 7.4521 | 3 | 559 | 3329 | 11.6 | 0 | 1.3 | 0 | 12.9 | 0.01 | 0 | 0 | 5.9553
交流220kV | 2005-09-26 | 2013-03-08 | 7.4521 | 44.75 | 468.05 | 2673.72 | 5.99 | 0.76 | 1.42 | 0 | 8.17 | 0.02 | 0.041 | 68 | 5.7125
交流220kV | 2005-06-20 | 2012-12-05 | 7.4658 | 9 | 521 | 3823.4 | 14.7 | 3.3 | 2.8 | 0 | 20.8 | 0 | 0 | 0 | 7.3386
交流220kV | 2005-06-20 | 2012-12-06 | 7.4685 | 15 | 730 | 3715 | 15 | 2 | 3 | 0 | 20 | 0 | 0 | 0 | 5.089
交流220kV | 2004-04-23 | 2011-10-10 | 7.4685 | 32 | 1637 | 10120 | 35.7 | 6.1 | 7.8 | 0.7 | 50.3 | 0.029 | 0.001 | 40 | 6.182
交流220kV | 2006-06-26 | 2013-12-13 | 7.4712 | 102 | 160.1 | 2770.5 | 50.7 | 46 | 16.7 | 0.1 | 113.5 | 0 | 0 | 0 | 17.3048
交流220kV | 2001-06-04 | 2008-11-22 | 7.474 | 7.2 | 1080.2 | 2560.2 | 12.3 | 2.1 | 3.1 | 0 | 17.5 | 0.01 | 0.005 | 45.2 | 2.3701
交流220kV | 2001-06-04 | 2008-11-22 | 7.474 | 7.2 | 1080.2 | 2560.2 | 12.3 | 2.1 | 3.1 | 0 | 17.5 | 0.008 | 0.005 | 45.2 | 2.3701
交流220kV | 2005-12-14 | 2013-06-05 | 7.4795 | 16 | 441 | 4822 | 12 | 1 | 4 | 0 | 17 | 0.001 | 0.1 | 45 | 10.9342
交流220kV | 2005-06-30 | 2012-12-21 | 7.4822 | 5.62 | 515.3 | 1428.6 | 7.15 | 1.21 | 2.26 | 0 | 10.62 | 0 | 0.045 | 52 | 2.7724
交流220kV | 2005-10-01 | 2013-03-27 | 7.4904 | 47 | 70 | 1411 | 3.72 | 0.38 | 1.47 | 0 | 5.57 | 0.011 | 0.6 | 72 | 20.1571
交流220kV | 2005-06-24 | 2012-12-20 | 7.4959 | 15.24 | 92.05 | 286.22 | 4.92 | 0.34 | 0.86 | 0 | 6.12 | 0 | 0 | 0 | 3.1094
交流220kV | 2006-06-19 | 2013-12-17 | 7.5014 | 54.2 | 108.4 | 2606.2 | 105.5 | 106.7 | 42.6 | 0 | 254.8 | 0.06 | 2 | 45 | 24.0424
交流220kV | 2006-06-14 | 2013-12-12 | 7.5014 | 12.6 | 677.8 | 5094.1 | 11.8 | 1.3 | 2.6 | 0 | 15.7 | 0 | 0 | 0 | 7.5156
交流220kV | 2005-09-21 | 2013-03-26 | 7.5151 | 88.56 | 1981.59 | 2813.68 | 20.7 | 4.76 | 3.18 | 0.47 | 29.11 | 0.015 | 0.001 | 66.7 | 1.4199
交流220kV | 2004-07-01 | 2012-01-05 | 7.5178 | 7.43 | 413.05 | 1911.5 | 4.56 | 1.28 | 0.73 | 0 | 6.57 | 0.001 | 0.04 | 70 | 4.6278
交流220kV | 2006-06-06 | 2013-12-17 | 7.537 | 37.2 | 198.4 | 648.1 | 6.9 | 0 | 0.2 | 0 | 7.1 | 0.06 | 1.9 | 44 | 3.2666
交流220kV | 2006-06-06 | 2013-12-17 | 7.537 | 19 | 654 | 506 | 11 | 0 | 2 | 0 | 13 | 0 | 0 | 0 | 0.7737
交流220kV | 2006-03-15 | 2013-09-29 | 7.5479 | 7.24 | 747.35 | 2062.4 | 8.82 | 1.53 | 1.94 | 0 | 12.29 | 0.013 | 0.001 | 50.7 | 2.7596
交流220kV | 2005-06-11 | 2012-12-27 | 7.5507 | 11 | 798 | 2328 | 7.5 | 1.2 | 2.4 | 0 | 11.1 | 0.003 | 0.086 | 57 | 2.9173
交流220kV | 2003-07-03 | 2011-01-19 | 7.5534 | 8.42 | 914.32 | 1290.12 | 13.8 | 2.2 | 4.96 | 0 | 20.96 | 0.01 | 0.004 | 52.3 | 1.411
交流220kV | 2005-11-28 | 2013-06-19 | 7.5616 | 3.5 | 158.5 | 758 | 3.6 | 0.5 | 0.7 | 0 | 4.8 | 0.01 | 0.11 | 62 | 4.7823
交流220kV | 2006-06-19 | 2014-01-09 | 7.5644 | 147.9 | 132.9 | 266.9 | 126.9 | 110.2 | 40.6 | 0 | 277.7 | 0 | 0 | 0 | 2.0083
交流220kV | 2003-06-26 | 2011-01-20 | 7.5753 | 4.61 | 389 | 1047 | 11 | 3.32 | 2.94 | 0 | 17.26 | 0.022 | 0.563 | 50.9 | 2.6915
交流220kV | 2005-08-18 | 2013-03-14 | 7.5753 | 2 | 103 | 1046 | 4.69 | 1.33 | 1.84 | 0 | 7.86 | 0.003 | 0.185 | 74.1 | 10.1553
交流220kV | 2005-08-18 | 2013-03-14 | 7.5753 | 7 | 698 | 2039 | 6.33 | 4.61 | 1.21 | 0 | 12.15 | 0.003 | 0.119 | 73.6 | 2.9212
交流220kV | 2005-08-18 | 2013-03-14 | 7.5753 | 8 | 699 | 2235 | 7.51 | 4.58 | 1.36 | 0 | 13.45 | 0.003 | 0.213 | 72.1 | 3.1974
交流220kV | 2005-05-16 | 2012-12-11 | 7.5781 | 4.9 | 408.6 | 4271.9 | 5.4 | 1.8 | 1.7 | 0 | 8.9 | 0 | 0 | 0 | 10.455
交流220kV | 2006-06-19 | 2014-01-15 | 7.5808 | 168.1 | 148.7 | 2814.2 | 147.3 | 128.1 | 48 | 0 | 323.4 | 0 | 0 | 0 | 18.9254
交流220kV | 2003-11-03 | 2011-06-01 | 7.5808 | 7.03 | 801 | 1948 | 8.6 | 0.73 | 2.01 | 0 | 11.34 | 0.032 | 0.05 | 60.4 | 2.432
交流220kV | 2001-03-15 | 2008-10-11 | 7.5808 | 8.66 | 340.47 | 1656.15 | 15.96 | 5.11 | 7.08 | 0 | 28.15 | 0.025 | 0.003 | 57.4 | 4.8643
交流220kV | 2005-08-15 | 2013-03-13 | 7.5808 | 3 | 147 | 1481 | 4.41 | 0.62 | 0.55 | 0 | 5.58 | 0.003 | 0.191 | 72.1 | 10.0748
交流220kV | 2005-08-15 | 2013-03-13 | 7.5808 | 6 | 178 | 1395 | 2.92 | 0.52 | 0.46 | 0 | 3.9 | 0.003 | 0.113 | 74.5 | 7.8371
交流220kV | 2005-08-15 | 2013-03-13 | 7.5808 | 3 | 190 | 1600 | 4.07 | 0.62 | 0.57 | 0 | 5.26 | 0.003 | 0.137 | 72.8 | 8.4211
交流220kV | 2006-06-19 | 2014-01-20 | 7.5945 | 231.6 | 175.9 | 3277.8 | 167.6 | 148.5 | 56.5 | 0 | 372.6 | 0 | 0 | 0 | 18.6345
交流220kV | 2005-05-10 | 2012-12-14 | 7.6027 | 162.38 | 263.03 | 2065.01 | 480.2 | 461.02 | 223.61 | 0 | 1164.83 | 0.003 | 0.025 | 48 | 7.8509
交流220kV | 2004-11-11 | 2012-06-18 | 7.6055 | 8.29 | 1364.31 | 8918.53 | 19.74 | 23.22 | 7.22 | 0 | 50.18 | 0.018 | 0.125 | 52.4 | 6.537
交流220kV | 2002-09-28 | 2010-05-13 | 7.6274 | 2.6 | 818.68 | 1630.9 | 9.66 | 0.82 | 2.06 | 0 | 12.54 | 0.005 | 0.132 | 51.7 | 1.9921
交流220kV | 2006-03-19 | 2013-11-13 | 7.6603 | 26.51 | 96.86 | 1910.1 | 4.55 | 0.49 | 4.1 | 0 | 9.14 | 0.008 | 0.12 | 63 | 19.7202
交流220kV | 2005-12-28 | 2013-08-30 | 7.6767 | 13.18 | 113.69 | 989.51 | 7.85 | 6.58 | 2.31 | 0.13 | 16.87 | 0.008 | 0.001 | 56 | 8.7036
交流220kV | 2006-04-01 | 2013-12-04 | 7.6822 | 17.6 | 780 | 5379 | 17.9 | 6 | 5.1 | 0 | 29 | 0.04 | 0.44 | 45 | 6.8962
交流220kV | 2004-07-06 | 2012-03-15 | 7.6959 | 15.57 | 654.62 | 1526.61 | 6.47 | 0.74 | 2.09 | 0.1 | 9.4 | 0.011 | 0.063 | 52 | 2.3321
交流220kV | 2004-10-08 | 2012-06-18 | 7.6986 | 12.48 | 835.34 | 4907.61 | 9.25 | 15.22 | 3.28 | 0 | 27.75 | 0.018 | 0.113 | 56.8 | 5.875
交流220kV | 2006-07-08 | 2014-03-27 | 7.7233 | 17 | 48 | 356 | 6.17 | 0 | 0 | 0 | 6.17 | 0.008 | 0.002 | 50 | 7.4167
交流220kV | 2005-09-04 | 2013-06-05 | 7.7562 | 30.1 | 560.3 | 3567 | 12.2 | 1.9 | 2.7 | 0 | 16.8 | 0.014 | 0 | 59.1 | 6.3662
交流220kV | 2004-06-21 | 2012-03-28 | 7.7726 | 6.64 | 754.41 | 3710.78 | 12.07 | 1.38 | 2.83 | 0 | 16.28 | 0 | 0 | 0 | 4.9188
交流220kV | 2005-08-23 | 2013-05-30 | 7.7726 | 11.41 | 169.11 | 1054.63 | 9.36 | 1.04 | 2.13 | 0 | 12.53 | 0.003 | 0.25 | 51 | 6.2364
交流220kV | 2001-10-09 | 2009-07-18 | 7.7781 | 8.98 | 609.82 | 1908.78 | 9.98 | 1.15 | 1.77 | 0 | 12.9 | 0.016 | 0.001 | 45.9 | 3.1301
交流220kV | 2003-12-11 | 2011-09-29 | 7.8055 | 23 | 1018 | 2896 | 9.5 | 2.5 | 1.2 | 0.2 | 13.4 | 0.067 | 0.029 | 51 | 2.8448
交流220kV | 2005-12-16 | 2013-10-14 | 7.8329 | 8.1 | 21 | 1403 | 1.5 | 0.3 | 0 | 0 | 1.8 | 0.016 | 0.001 | 49 | 66.8095
交流220kV | 2002-05-17 | 2010-03-18 | 7.8411 | 9 | 439 | 196 | 10.86 | 4.04 | 2.29 | 0 | 17.19 | 0.001 | 0.03 | 50 | 0.44647
交流220kV | 2005-12-25 | 2013-10-29 | 7.8493 | 4.74 | 271.46 | 1114.68 | 4.7 | 0.54 | 0.46 | 0 | 5.7 | 0.012 | 0.222 | 62 | 4.1062
交流220kV | 2005-12-25 | 2013-10-29 | 7.8493 | 4.56 | 253.01 | 1084.17 | 4.79 | 0.47 | 0.47 | 0 | 5.73 | 0.009 | 0.1 | 58.6 | 4.2851
交流220kV | 2005-12-25 | 2013-10-29 | 7.8493 | 7.54 | 391.28 | 1056.11 | 4.8 | 5.39 | 2.09 | 0 | 12.28 | 0.008 | 0.007 | 60.4 | 2.6991
交流220kV | 2005-12-25 | 2013-10-29 | 7.8493 | 5.06 | 286.42 | 1067.92 | 4.42 | 3.55 | 2.29 | 0 | 10.26 | 0.011 | 0.006 | 62 | 3.7285
交流220kV | 2005-12-20 | 2013-10-25 | 7.8521 | 2.14 | 875.49 | 1658.35 | 12.82 | 3.04 | 3.18 | 0 | 19.04 | 0.011 | 0.214 | 60.2 | 1.8942
交流220kV | 2005-04-08 | 2013-02-19 | 7.874 | 13.35 | 1219.12 | 3221.11 | 10.99 | 1.13 | 1.65 | 0 | 13.77 | 0.011 | 0.067 | 52 | 2.6422
交流220kV | 2004-07-10 | 2012-05-24 | 7.8767 | 2.64 | 824.49 | 1387.45 | 39.75 | 1.22 | 5.67 | 0 | 46.64 | 0.005 | 0.1 | 56 | 1.6828
交流220kV | 2005-04-27 | 2013-03-21 | 7.9041 | 24 | 315 | 950 | 27.97 | 1.1 | 5.9 | 0 | 34.97 | 0.001 | 0.05 | 50.5 | 3.0159
220 | 2005-04-27 | 2013-03-22 | 7.9068 | 4.87 | 377.83 | 1277.8 | 6.86 | 0.41 | 1.28 | 0 | 8.55 | 0.013 | 0.024 | 59.5 | 3.3819
220 | 2006-04-16 | 2014-03-12 | 7.9096 | 2.06 | 412.94 | 3180.23 | 9.32 | 0.85 | 2.5 | 0 | 12.67 | 0.012 | 0.018 | 57.9 | 7.7014
交流220kV | 2002-04-16 | 2010-03-17 | 7.9233 | 49.02 | 96.15 | 304.97 | 2.19 | 0.27 | 0.97 | 0 | 3.43 | 0.02 | 0.23 | 49 | 3.1718
交流220kV | 2002-04-16 | 2010-03-17 | 7.9233 | 16.75 | 398.1 | 1596.61 | 9.02 | 7.88 | 3.31 | 0 | 20.21 | 0.01 | 0.362 | 51 | 4.0106
交流220kV | 2005-04-03 | 2013-03-07 | 7.9315 | 20 | 424 | 499 | 22.16 | 3.77 | 5.18 | 0 | 31.11 | 0.001 | 0.08 | 50 | 1.1769
交流220kV | 2004-01-08 | 2011-12-13 | 7.9342 | 2.28 | 638.19 | 3856.56 | 12.36 | 0.75 | 1.97 | 0 | 15.08 | 0.02 | 0 | 0 | 6.043
交流220kV | 2003-11-03 | 2011-10-10 | 7.9397 | 11.87 | 1103 | 2515 | 10.94 | 1.24 | 2.14 | 0 | 14.32 | 0.021 | 0.054 | 56.3 | 2.2801
交流220kV | 2004-12-15 | 2012-11-21 | 7.9397 | 7.7 | 571.4 | 1161 | 6.1 | 0.9 | 2.1 | 0.1 | 9.2 | 0.01 | 0.058 | 57.6 | 2.0319
交流220kV | 2005-10-18 | 2013-09-24 | 7.9397 | 15.73 | 314.04 | 4438.16 | 14.88 | 0.86 | 4.08 | 0 | 19.82 | 0.03 | 0.001 | 66 | 14.1325
交流220kV | 2005-12-14 | 2013-11-21 | 7.9425 | 15.66 | 461.67 | 4650.81 | 11.83 | 1.19 | 3.35 | 0 | 16.37 | 0.003 | 0.25 | 51 | 10.0739
交流220kV | 2005-11-15 | 2013-10-25 | 7.9479 | 2 | 705.37 | 1524.92 | 10.02 | 1.18 | 2 | 0 | 13.2 | 0.012 | 0.082 | 64.4 | 2.1619
交流220kV | 2005-10-18 | 2013-09-27 | 7.9479 | 47.78 | 548.27 | 5978.74 | 18.75 | 0.73 | 4.41 | 0 | 23.89 | 0.01 | 0.001 | 77 | 10.9047
交流220kV | 2006-01-19 | 2013-12-30 | 7.9507 | 6.7 | 800.82 | 1772.87 | 7.94 | 2.29 | 1.26 | 0 | 11.49 | 0 | 0 | 0 | 2.2138
交流220kV | 2006-03-11 | 2014-02-19 | 7.9507 | 6.25 | 147.64 | 1120.99 | 8.74 | 0.99 | 1.2 | 0 | 10.93 | 0.009 | 0.3 | 53 | 7.5927
交流220kV | 2005-06-24 | 2013-06-06 | 7.9562 | 45.85 | 257.85 | 753.71 | 6.69 | 0.86 | 0.3 | 0 | 7.85 | 0 | 0 | 0 | 2.9231
交流220kV | 2005-06-20 | 2013-06-05 | 7.9644 | 15.9 | 681 | 6479.5 | 19.4 | 4.9 | 4.6 | 0 | 28.9 | 0.028 | 0 | 61 | 9.5147
交流220kV | 2005-06-30 | 2013-06-20 | 7.9781 | 6.1 | 431 | 1573 | 5.9 | 0.4 | 0.8 | 0 | 7.1 | 0 | 0 | 0 | 3.6497
交流220kV | 2003-06-18 | 2011-06-09 | 7.9808 | 24 | 780 | 3738 | 9.8 | 0.9 | 3.5 | 0 | 14.2 | 0.008 | 0.003 | 53 | 4.7923
交流220kV | 2004-10-26 | 2012-10-17 | 7.9808 | 14.87 | 217.42 | 781.99 | 3.75 | 0.68 | 0.65 | 0 | 5.08 | 0.008 | 0.003 | 56 | 3.5967
交流220kV | 2004-10-26 | 2012-10-17 | 7.9808 | 14.87 | 234.68 | 530.45 | 4.02 | 0.61 | 0.6 | 0 | 5.23 | 0.011 | 0.002 | 60 | 2.2603
交流220kV | 2004-12-05 | 2012-11-27 | 7.9836 | 2.8 | 133.7 | 960.1 | 1.9 | 0.8 | 0.2 | 0.1 | 3 | 0.02 | 0.096 | 57.2 | 7.181
交流220kV | 2003-12-20 | 2011-12-13 | 7.9863 | 3.74 | 529.21 | 3007.96 | 9.12 | 0 | 1.62 | 0 | 10.74 | 0.01 | 0 | 0 | 5.6839
交流220kV | 2004-07-28 | 2012-07-23 | 7.9918 | 2.46 | 414.34 | 781.94 | 5.45 | 1.42 | 0.89 | 0 | 7.76 | 0.011 | 0.003 | 60 | 1.8872
交流220kV | 2004-07-28 | 2012-07-23 | 7.9918 | 5.83 | 397.59 | 1051.81 | 5.52 | 1.24 | 0.76 | 0 | 7.52 | 0.008 | 0.002 | 62 | 2.6455
交流220kV | 2005-09-01 | 2013-08-30 | 8 | 12.72 | 449.97 | 2179.7 | 7.44 | 0.91 | 2.05 | 0 | 10.4 | 0.01 | 0.001 | 56 | 4.8441
交流220kV | 2005-09-01 | 2013-08-30 | 8 | 9.27 | 349.25 | 1112.29 | 8.73 | 1.73 | 2.06 | 0 | 12.52 | 0.003 | 0.001 | 57 | 3.1848
交流220kV | 2005-06-13 | 2013-06-15 | 8.011 | 87.53 | 161.41 | 2626.45 | 7.27 | 1.55 | 2.62 | 0 | 11.44 | 0 | 0 | 50 | 16.2719
交流220kV | 2001-06-04 | 2009-06-12 | 8.0274 | 6.2 | 1102.1 | 2953.1 | 12.3 | 1.6 | 2.9 | 0.7 | 17.5 | 0.01 | 0.001 | 52.7 | 2.6795
交流220kV | 2001-06-04 | 2009-06-12 | 8.0274 | 6.18 | 1102.12 | 2953.07 | 12.34 | 1.58 | 2.89 | 0.7 | 17.51 | 0.008 | 0.001 | 52.7 | 2.6794
交流220kV | 2004-10-06 | 2012-10-18 | 8.0384 | 7.33 | 353.56 | 1119.78 | 9.09 | 7.02 | 3.07 | 0 | 19.18 | 0.009 | 0.002 | 61 | 3.1672
交流220kV | 2005-05-10 | 2013-05-24 | 8.0438 | 94.49 | 68.35 | 1183.92 | 130.15 | 132.28 | 63.14 | 0 | 325.57 | 0.003 | 0.25 | 53 | 17.3214
交流220kV | 2005-06-20 | 2013-07-05 | 8.0466 | 15 | 796 | 4305 | 16 | 2 | 3 | 0 | 21 | 0.074 | 0.21 | 52 | 5.4083
交流220kV | 2004-10-28 | 2012-11-15 | 8.0548 | 16 | 555 | 1766 | 6.48 | 0.88 | 0.94 | 0.67 | 8.97 | 0.029 | 0.014 | 72 | 3.182
交流220kV | 2006-02-21 | 2014-03-13 | 8.0603 | 10.44 | 878.59 | 3979.1 | 7.44 | 1.47 | 1.64 | 0.08 | 10.63 | 0.009 | 0.001 | 49.2 | 4.529
交流220kV | 2003-05-30 | 2011-06-21 | 8.0658 | 8.9 | 389.2 | 6191.9 | 23.9 | 0 | 3.8 | 0 | 27.7 | 0.01 | 0 | 60.4 | 15.9093
交流220kV | 2004-11-12 | 2012-12-07 | 8.074 | 17.17 | 959.53 | 1952.73 | 31.66 | 49.2 | 8.1 | 4.47 | 93.43 | 0.001 | 0.1 | 40 | 2.0351
交流220kV | 2001-10-09 | 2009-11-03 | 8.074 | 9.73 | 636.81 | 3054.44 | 10.16 | 1.17 | 1.94 | 0 | 13.27 | 0.011 | 0.001 | 46.4 | 4.7965
交流220kV | 2006-02-18 | 2014-03-21 | 8.0904 | 11.92 | 625.46 | 2915.2 | 16.9 | 6.6 | 3.83 | 0 | 27.33 | 0.012 | 0.079 | 58.6 | 4.6609
交流220kV | 2006-02-20 | 2014-03-24 | 8.0932 | 4.06 | 493.74 | 1491.49 | 9.74 | 0.79 | 1.5 | 0 | 12.03 | 0.016 | 0.42 | 58 | 3.0208
交流220kV | 2004-04-21 | 2012-05-24 | 8.0959 | 2.84 | 719.24 | 1698.95 | 43.92 | 3.56 | 6.49 | 0 | 53.97 | 0.005 | 0.1 | 56 | 2.3621
交流220kV | 2005-05-10 | 2013-06-18 | 8.1123 | 94.49 | 68.35 | 1183.92 | 130.15 | 132.28 | 63.14 | 0 | 325.57 | 0.003 | 0.25 | 49 | 17.3214
交流220kV | 2005-05-16 | 2013-06-25 | 8.1151 | 4.4 | 436.7 | 6848.1 | 6.3 | 2.7 | 2.4 | 0 | 11.4 | 0.016 | 0 | 36.4 | 15.6815
交流220kV | 2003-06-26 | 2011-08-10 | 8.1288 | 4.44 | 419 | 1504 | 13.07 | 4.52 | 2.6 | 0 | 20.19 | 0.027 | 0.673 | 51.2 | 3.5895
交流220kV | 2005-06-02 | 2013-07-18 | 8.1315 | 14.2 | 1235.6 | 9203.5 | 9.7 | 83.7 | 2.2 | 0 | 95.6 | 0.009 | 0.09 | 52.3 | 7.4486
交流220kV | 2002-11-15 | 2011-01-21 | 8.189 | 7.97 | 351.28 | 539.67 | 11.38 | 3.64 | 3.13 | 0 | 18.15 | 0.011 | 0.004 | 52.5 | 1.5363
交流220kV | 2001-12-24 | 2010-03-03 | 8.1945 | 21.84 | 270.69 | 1499.27 | 18.2 | 6.26 | 9.43 | 0.19 | 34.08 | 0.016 | 0.18 | 48 | 5.5387
交流220kV | 2003-12-12 | 2012-02-21 | 8.2 | 25 | 1166 | 3657 | 23.93 | 16.96 | 9.04 | 0 | 49.93 | 0.001 | 0.001 | 56.3 | 3.1364
交流220kV | 2005-12-21 | 2014-03-03 | 8.2027 | 20.87 | 458.4 | 2050.65 | 27.2 | 3.69 | 7.29 | 0 | 38.18 | 0.012 | 0.099 | 52.6 | 4.4735
交流220kV | 2005-04-14 | 2013-06-26 | 8.2055 | 2.1 | 97.8 | 221.2 | 4.1 | 0.5 | 0.7 | 0.3 | 5.6 | 0.006 | 0.005 | 58.6 | 2.2618
交流220kV | 2004-11-11 | 2013-01-23 | 8.2055 | 9.3 | 1603.59 | 8835.15 | 23.6 | 24.85 | 8.17 | 0 | 56.62 | 0.018 | 0.111 | 57.2 | 5.5096
交流220kV | 2006-01-06 11:08 | 2014-03-24 | 8.2152 | 16 | 205 | 564 | 28.05 | 9.97 | 50.87 | 0 | 88.89 | 0.001 | 0.031 | 50 | 2.7512
交流220kV | 2004-11-21 | 2013-02-06 | 8.2164 | 3 | 154.8 | 1075.8 | 40.3 | 6.2 | 6.5 | 0 | 53 | 0.008 | 0.148 | 66.7 | 6.9496
交流220kV | 2004-12-20 | 2013-03-07 | 8.2164 | 124.61 | 232.19 | 911.2 | 14.17 | 9.22 | 32.24 | 0 | 55.63 | 0.027 | 0.052 | 64 | 3.9244
交流220kV | 2004-04-25 | 2012-07-19 | 8.2384 | 14.74 | 69.91 | 585.22 | 1.92 | 0.61 | 0 | 0 | 2.53 | 0.021 | 0.001 | 60 | 8.371
交流220kV | 2005-07-31 | 2013-10-25 | 8.2411 | 4.61 | 688.22 | 2389.91 | 8.63 | 0.91 | 0.93 | 0 | 10.47 | 0.006 | 0.063 | 59 | 3.4726
交流220kV | 2005-12-30 | 2014-03-27 | 8.2438 | 27.41 | 406.01 | 729.75 | 6.68 | 1.08 | 1.05 | 0 | 8.81 | 0.004 | 0.001 | 58.7 | 1.7974
交流220kV | 2005-12-28 | 2014-03-26 | 8.2466 | 5.46 | 147.82 | 895.16 | 3.81 | 3.16 | 0.98 | 0.06 | 8.01 | 0.004 | 0.001 | 59.2 | 6.0557
交流220kV | 2005-12-25 | 2014-03-24 | 8.2493 | 5.36 | 312.58 | 1934.91 | 6.29 | 0.82 | 1.67 | 0 | 8.78 | 0.006 | 0.015 | 60 | 6.1901
交流220kV | 2005-07-31 | 2013-10-28 | 8.2493 | 4.62 | 617.94 | 2246.4 | 7.31 | 0.98 | 0.82 | 0 | 9.11 | 0.007 | 0.028 | 60 | 3.6353
交流220kV | 2005-08-23 | 2013-11-21 | 8.2521 | 22.12 | 418.75 | 1736.07 | 10.53 | 1.02 | 2.13 | 0 | 13.68 | 0.003 | 0.25 | 51 | 4.1458
交流220kV | 2005-09-04 | 2013-12-04 | 8.2548 | 28.7 | 677.1 | 2589.3 | 13.8 | 1.8 | 2.6 | 0 | 18.2 | 0 | 0 | 0 | 3.8241
交流220kV | 2003-06-30 | 2011-09-30 | 8.2575 | 15 | 557 | 5634 | 12.4 | 1.6 | 4.1 | 0 | 18.1 | 0.003 | 0.001 | 62 | 10.1149
交流220kV | 2004-10-08 | 2013-01-23 | 8.2986 | 6.36 | 755.84 | 5012.27 | 10.39 | 15.49 | 3.68 | 0 | 29.56 | 0.018 | 0.104 | 53.2 | 6.6314
交流220kV | 2003-07-07 | 2011-10-26 | 8.3096 | 17 | 978 | 4386 | 7.8 | 1.7 | 1.9 | 0 | 11.4 | 0.003 | 0.01 | 60 | 4.4847
交流220kV | 2004-06-28 | 2012-10-18 | 8.3123 | 4.22 | 271.94 | 1081.57 | 6.26 | 1.55 | 3.18 | 0 | 10.99 | 0.006 | 0.002 | 60 | 3.9772
交流220kV | 2005-06-02 | 2013-09-24 | 8.3178 | 12.9 | 1151.8 | 9026.8 | 11.1 | 66.1 | 2.4 | 0 | 79.6 | 0 | 0 | 0 | 7.8371
交流220kV | 2005-11-28 | 2014-03-25 | 8.326 | 10.2 | 743.8 | 1161.9 | 9.1 | 1.5 | 1.7 | 0.1 | 12.4 | 0.001 | 0.06 | 55.8 | 1.5621
交流220kV | 2005-11-28 | 2014-03-25 | 8.326 | 3.7 | 178.3 | 588.3 | 3.7 | 0.4 | 0.6 | 0 | 4.7 | 0.002 | 0.09 | 63.3 | 3.2995
交流220kV | 2005-11-28 | 2014-03-25 | 8.326 | 8.7 | 572.5 | 1189.9 | 6.8 | 1.6 | 1 | 2.8 | 12.2 | 0.002 | 0.06 | 60.5 | 2.0784
交流220kV | 2004-07-06 | 2012-11-02 | 8.3315 | 8.3 | 683.1 | 1282 | 7 | 0 | 0 | 0 | 7 | 0.015 | 0.084 | 54.2 | 1.8767
220 | 2004-11-24 | 2013-03-28 | 8.3452 | 2 | 313 | 183 | 13.8 | 0 | 0 | 0 | 13.8 | 0.008 | 0.001 | 52 | 0.58466
交流220kV | 2003-12-20 | 2012-04-24 | 8.3507 | 3 | 544.56 | 3090.12 | 9.45 | 0 | 0 | 0 | 9.45 | 0.011 | 0 | 0 | 5.6745
交流220kV | 2004-12-29 | 2013-05-04 | 8.3507 | 16 | 1200.2 | 3297.2 | 9.6 | 1 | 1.7 | 0.2 | 12.5 | 0.01 | 0.08 | 57 | 2.7472
交流220kV | 2005-07-30 | 2013-12-03 | 8.3507 | 23 | 50 | 3418 | 10.76 | 1.14 | 1.91 | 0.28 | 14.09 | 0.03 | 0.216 | 75 | 68.36
交流220kV | 2005-01-16 | 2013-05-23 | 8.3534 | 36.35 | 122.36 | 825.43 | 9.34 | 1.08 | 1.86 | 0 | 12.28 | 0 | 0.007 | 61.5 | 6.7459
交流220kV | 2005-07-27 | 2013-12-09 | 8.3753 | 14 | 42 | 2625 | 8 | 0.8 | 1.5 | 0.2 | 10.5 | 0.025 | 0.004 | 65 | 62.5
交流220kV | 2005-11-11 | 2014-03-28 | 8.3808 | 103.6 | 349.4 | 1150.4 | 7 | 0.4 | 2.4 | 0 | 9.8 | 0.009 | 0 | 56.4 | 3.2925
交流220kV | 2003-11-03 | 2012-03-20 | 8.3836 | 6.42 | 888 | 1152 | 9.85 | 0.14 | 1.7 | 0.88 | 12.57 | 0.021 | 0.048 | 55.2 | 1.2973
交流220kV | 2001-06-04 | 2009-10-22 | 8.389 | 6.5 | 1052.6 | 3294.1 | 14.8 | 2 | 4.4 | 0.8 | 22 | 0.01 | 0.003 | 54.6 | 3.1295
交流220kV | 2001-06-04 | 2009-10-22 | 8.389 | 6.53 | 1052.58 | 3294.09 | 14.76 | 2.02 | 4.35 | 0.81 | 21.94 | 0.01 | 0.003 | 54.6 | 3.1295
交流220kV | 1998-06-30 | 2006-11-22 | 8.4027 | 3.1 | 148.9 | 961.2 | 6 | 1.2 | 0.7 | 0.3 | 8.2 | 0 | 0.16 | 47 | 6.4553
交流220kV | 2004-01-08 | 2012-06-07 | 8.4192 | 4.09 | 765.57 | 5095.31 | 14.27 | 0 | 0 | 0 | 14.27 | 0.012 | 0.064 | 0 | 6.6556
交流220kV | 2005-07-01 | 2013-12-02 | 8.4274 | 4.8 | 733 | 2951 | 13.7 | 0.7 | 2.3 | 0 | 16.7 | 0.03 | 0.5 | 50 | 4.0259
交流220kV | 2003-09-29 | 2012-03-02 | 8.4301 | 76.59 | 557.41 | 2624.03 | 10.81 | 1.12 | 1.49 | 0 | 13.42 | 0.01 | 0.212 | 49.5 | 4.7075
交流220kV | 2005-07-01 | 2013-12-04 | 8.4329 | 11.2 | 507.9 | 1655.2 | 9.2 | 5.5 | 1.5 | 0 | 16.2 | 0 | 0 | 0 | 3.2589
交流220kV | 2005-06-30 | 2013-12-03 | 8.4329 | 3.4 | 461 | 1760 | 6.9 | 0.4 | 1.1 | 0 | 8.4 | 0.03 | 0.62 | 50 | 3.8178
交流220kV | 2005-06-25 | 2013-12-05 | 8.4521 | 25.9 | 460.5 | 1638.4 | 11 | 0.8 | 1.7 | 0 | 13.5 | 0 | 0 | 0 | 3.5579
交流220kV | 2005-06-20 | 2013-12-05 | 8.4658 | 9.4 | 579.6 | 4362.8 | 17.7 | 5.3 | 3.6 | 0 | 26.6 | 0 | 0 | 0 | 7.5273
交流220kV | 2003-11-02 | 2012-04-18 | 8.4658 | 31 | 445 | 180 | 12.4 | 4.9 | 3.9 | 0 | 21.2 | 0.009 | 0.002 | 54 | 0.40449
交流220kV | 2003-09-15 | 2012-03-02 | 8.4685 | 25.2 | 458.87 | 2452.63 | 11.92 | 1.23 | 1.36 | 0 | 14.51 | 0.011 | 0.301 | 50.9 | 5.3449
交流220kV | 2004-10-31 | 2013-04-24 | 8.4849 | 14.39 | 313.24 | 5182.72 | 17.83 | 26.51 | 7.83 | 0 | 52.17 | 0.012 | 0.083 | 55.1 | 16.5455
交流220kV | 2005-06-24 | 2013-12-20 | 8.4959 | 9.81 | 98.2 | 310.49 | 5.01 | 0.27 | 0 | 0 | 5.28 | 0 | 0 | 67.9 | 3.1618
交流220kV | 2005-06-20 | 2013-12-18 | 8.5014 | 14 | 724 | 4009 | 14 | 2 | 3 | 0 | 19 | 0 | 0 | 0 | 5.5373
交流220kV | 2003-06-18 | 2011-12-16 | 8.5014 | 11 | 659 | 2037 | 6.2 | 1.9 | 1.1 | 0 | 9.2 | 0.003 | 0.002 | 67 | 3.091
交流220kV | 2003-06-18 | 2011-12-16 | 8.5014 | 15 | 851 | 2650 | 8 | 2.2 | 1.4 | 0 | 11.6 | 0.003 | 0.003 | 58 | 3.114
交流220kV | 2003-06-18 | 2011-12-16 | 8.5014 | 7 | 622 | 1984 | 5.9 | 1.2 | 1 | 0 | 8.1 | 0.003 | 0.002 | 53 | 3.1897
交流220kV | 2004-11-12 | 2013-05-16 | 8.5123 | 10.18 | 832.92 | 1889.84 | 28.91 | 45.31 | 6.61 | 4.14 | 84.97 | 0.003 | 0.025 | 53 | 2.2689
交流220kV | 2004-06-10 | 2012-12-12 | 8.5123 | 30 | 261 | 449 | 1.2 | 0.3 | 0.2 | 0 | 1.7 | 0.015 | 0.1 | 58 | 1.7203
交流220kV | 2002-08-21 | 2011-02-28 | 8.5288 | 5.27 | 287.95 | 3348.62 | 18.37 | 20.97 | 8.42 | 0 | 47.76 | 0.005 | 0.269 | 52.4 | 11.6292
交流220kV | 2005-06-02 | 2013-12-13 | 8.537 | 10.4 | 1124.4 | 8590 | 11.4 | 63.5 | 2.4 | 0 | 77.3 | 0 | 0 | 0 | 7.6396
交流220kV | 2003-08-07 | 2012-02-20 | 8.5452 | 3.23 | 480.2 | 1101.2 | 5.1 | 0.4 | 1.2 | 0 | 6.7 | 0.007 | 0.233 | 58 | 2.2932
交流220kV | 2004-12-24 | 2013-07-10 | 8.5479 | 41.07 | 132.7 | 537.24 | 3.22 | 0.89 | 1.06 | 0 | 5.17 | 0.003 | 0.004 | 61.4 | 4.0485
交流220kV | 2005-05-10 | 2013-11-26 | 8.5534 | 46.37 | 83.21 | 1429.66 | 143.63 | 136.5 | 65.61 | 0 | 345.74 | 0.002 | 0.1 | 42 | 17.1813
交流220kV | 2003-05-30 | 2011-12-20 | 8.5644 | 6.2 | 270.5 | 0 | 11.6 | 1.6 | 2.9 | 0 | 16.1 | 0 | 0 | 0 | 0
220 | 2005-04-15 | 2013-11-07 | 8.5699 | 43.56 | 431.08 | 956.47 | 9.92 | 0.37 | 1.08 | 0 | 11.37 | 0.027 | 0.618 | 46 | 2.2188
交流220kV | 2005-09-01 | 2014-03-26 | 8.5699 | 6.66 | 342.31 | 2064.53 | 8.23 | 0.98 | 2.14 | 0 | 11.35 | 0.011 | 0.001 | 59.1 | 6.0312
交流220kV | 2005-09-01 | 2014-03-26 | 8.5699 | 10.51 | 240.93 | 814.77 | 7.13 | 0.4 | 1.49 | 0 | 9.02 | 0.003 | 0.001 | 59.3 | 3.3818
交流220kV | 2005-05-16 | 2013-12-12 | 8.5808 | 10.8 | 970.4 | 10875.2 | 10.7 | 4.6 | 3.9 | 0 | 19.2 | 0 | 0 | 0 | 11.2069
交流220kV | 2003-09-29 | 2012-04-28 | 8.5863 | 4.11 | 779.83 | 2154.95 | 11.46 | 1.31 | 2.81 | 0 | 15.58 | 0.009 | 0.14 | 51 | 2.7634
交流220kV | 2001-10-09 | 2010-05-18 | 8.611 | 7.33 | 631.99 | 2927.8 | 10.23 | 1.29 | 2.28 | 0 | 13.8 | 0.014 | 0.001 | 53.4 | 4.6327
交流220kV | 2004-04-23 | 2012-12-08 | 8.6329 | 26 | 356 | 721 | 2.3 | 0.4 | 0.2 | 0 | 2.9 | 0.023 | 0.154 | 56 | 2.0253
交流220kV | 2001-10-09 | 2010-05-27 | 8.6356 | 1.75 | 97.47 | 776.88 | 3.47 | 5.01 | 0.42 | 0 | 8.9 | 0.015 | 0.002 | 55.8 | 7.9705
交流220kV | 2003-12-11 | 2012-09-28 | 8.8055 | 20 | 984 | 3239 | 10.1 | 2.8 | 1.4 | 0.3 | 14.6 | 0.062 | 0.035 | 51 | 3.2917
交流220kV | 2004-06-21 | 2013-04-10 | 8.8082 | 6.49 | 862.41 | 4626.62 | 13.61 | 1.51 | 3.45 | 0 | 18.57 | 0 | 0.003 | 52.4 | 5.3648
交流220kV | 2004-04-23 | 2013-02-18 | 8.8301 | 2.2 | 246.7 | 1617.3 | 5.3 | 0.5 | 1 | 0 | 6.8 | 0.016 | 0.075 | 69.8 | 6.5557
220 | 2005-04-27 | 2014-02-28 | 8.8466 | 9.28 | 389.66 | 1386.82 | 6.2 | 0.4 | 1.4 | 0 | 8 | 0.038 | 0.045 | 59 | 3.5591
交流220kV | 2002-07-18 | 2011-05-24 | 8.8548 | 2.81 | 548.43 | 3084.08 | 24.85 | 4.77 | 2.8 | 0.11 | 32.53 | 0.01 | 0.006 | 54 | 5.6235
交流220kV | 2004-07-08 | 2013-05-28 | 8.8932 | 23.3 | 1351.9 | 15428.5 | 39.7 | 43.6 | 0 | 0 | 83.3 | 0.017 | 0.174 | 0 | 11.4125
交流220kV | 2005-04-27 | 2014-03-20 | 8.9014 | 36 | 303 | 1140 | 31.46 | 1.31 | 7.33 | 0 | 40.1 | 0.001 | 0.07 | 50 | 3.7624
220 | 2004-12-29 | 2013-11-27 | 8.9178 | 22.29 | 424.85 | 2159.79 | 13.29 | 1.14 | 2.98 | 0 | 17.41 | 0.007 | 0.077 | 62.4 | 5.0837
交流220kV | 2004-01-08 | 2012-12-10 | 8.9288 | 2.79 | 714.27 | 4200.22 | 13.97 | 0 | 1.86 | 0 | 15.83 | 0 | 0 | 0 | 5.8804
交流220kV | 2002-05-17 | 2011-04-22 | 8.937 | 6 | 422 | 258 | 13.76 | 3.94 | 2.61 | 0 | 20.31 | 0.001 | 0.03 | 50 | 0.61137
交流220kV | 2005-04-03 | 2014-03-18 | 8.9616 | 19 | 341 | 1106 | 49.74 | 2.87 | 10.27 | 0 | 62.88 | 0.001 | 0.06 | 50 | 3.2434
交流220kV | 2003-12-20 | 2012-12-07 | 8.9726 | 8.24 | 790.51 | 3769.54 | 16.74 | 0 | 0 | 0 | 16.74 | 0 | 0 | 0 | 4.7685
交流220kV | 2002-07-07 | 2011-06-28 | 8.9808 | 8.8 | 418.9 | 1891.3 | 18.2 | 1.1 | 3.8 | 0 | 23.1 | 0.01 | 0.18 | 62 | 4.5149
交流220kV | 2002-12-17 | 2011-12-21 | 9.0164 | 0.18 | 446.73 | 815.02 | 3.92 | 0 | 0.56 | 0 | 4.48 | 0 | 0 | 0 | 1.8244
交流220kV | 2002-06-30 | 2011-07-08 | 9.0274 | 1.8 | 351.9 | 1899.5 | 10 | 2.3 | 2.2 | 0 | 14.5 | 0.01 | 0.002 | 50 | 5.3978
交流220kV | 2004-10-26 | 2013-11-06 | 9.0356 | 4.24 | 500.46 | 1541.35 | 7.87 | 2.47 | 1.07 | 0 | 11.41 | 0.008 | 0.201 | 60 | 3.0799
交流220kV | 2004-10-26 | 2013-11-06 | 9.0356 | 6.34 | 381 | 1020.33 | 5.83 | 1.63 | 0.68 | 0 | 8.14 | 0.009 | 0.173 | 67 | 2.678
交流220kV | 2004-11-12 | 2013-11-26 | 9.0438 | 10.82 | 960.67 | 2203.83 | 31.95 | 49.99 | 5.48 | 3.71 | 91.13 | 0.002 | 0.1 | 41 | 2.2941
交流220kV | 2002-07-28 | 2011-08-24 | 9.0795 | 2 | 145.89 | 963.26 | 11.32 | 0.55 | 4.59 | 0 | 16.46 | 0.007 | 0.002 | 59 | 6.6026
交流220kV | 2001-03-15 | 2010-04-13 | 9.0849 | 5.51 | 330.88 | 1407.21 | 16.07 | 4.83 | 7.45 | 0 | 28.35 | 0.009 | 0.002 | 56.4 | 4.2529
交流220kV | 2002-12-15 | 2012-01-16 | 9.0932 | 4.65 | 694.45 | 1771.24 | 26.7 | 3.72 | 2.96 | 0 | 33.38 | 0.011 | 0.005 | 52.8 | 2.5506
交流220kV | 2002-04-16 | 2011-05-24 | 9.1096 | 1.7 | 626.9 | 3503.1 | 14.6 | 3.6 | 2 | 0 | 20.2 | 0.01 | 0.007 | 59 | 5.588
交流220kV | 2003-09-29 | 2012-11-06 | 9.1123 | 9.6 | 475.5 | 1247.1 | 9.3 | 0 | 1 | 0.1 | 10.4 | 0.015 | 0.089 | 57.7 | 2.6227
交流220kV | 2003-09-01 11:18 | 2012-10-11 | 9.1165 | 8.93 | 268.09 | 659.68 | 18.41 | 8.31 | 0.77 | 0 | 27.49 | 0.011 | 0.021 | 52.2 | 2.4607
交流220kV | 2004-04-22 | 2013-06-08 | 9.1342 | 4.84 | 698.56 | 1109.4 | 8 | 1.48 | 1.07 | 0 | 10.55 | 0 | 0 | 0 | 1.5881
交流220kV | 2001-06-04 | 2010-07-22 | 9.137 | 24.4 | 738.6 | 3094.8 | 16.2 | 3 | 5.8 | 0 | 25 | 0.01 | 0.005 | 61.8 | 4.1901
交流220kV | 2001-06-04 | 2010-07-22 | 9.137 | 24.4 | 738.6 | 3094.8 | 16.2 | 3 | 5.8 | 0 | 25 | 0.009 | 0.005 | 61.8 | 4.1901
交流220kV | 2003-09-15 | 2012-11-06 | 9.1507 | 10.9 | 391.3 | 1226.2 | 10.5 | 0 | 1.6 | 0.1 | 12.2 | 0.012 | 0.084 | 52.7 | 3.1337
220 | 2003-01-01 | 2012-03-07 | 9.1863 | 8.46 | 1325.46 | 11258.36 | 124.56 | 264.78 | 45.26 | 0 | 434.6 | 0.019 | 0.095 | 50 | 8.4939
交流220kV | 2002-12-28 | 2012-03-16 | 9.2219 | 21.21 | 1143.5 | 4689.3 | 26.18 | 110.03 | 51.5 | 0 | 187.71 | 0.006 | 0.001 | 55 | 4.1008
交流220kV | 2004-11-21 | 2014-02-11 | 9.2301 | 2.6 | 144.8 | 1118.4 | 37.9 | 6.7 | 7 | 0 | 51.6 | 0.008 | 0.094 | 63 | 7.7238
交流220kV | 2002-10-16 | 2012-01-09 | 9.2384 | 8.47 | 1217.92 | 1058.14 | 21.41 | 9.9 | 3.67 | 0 | 34.98 | 0.01 | 0.063 | 53 | 0.86881
交流220kV | 2000-12-16 | 2010-03-11 | 9.2384 | 18 | 622 | 2504 | 18.66 | 16.51 | 5.97 | 0.09 | 41.23 | 0.021 | 0.18 | 50 | 4.0257
交流220kV | 2004-07-28 | 2013-10-21 | 9.2384 | 3.28 | 524.07 | 879.37 | 6.24 | 1.93 | 1.05 | 0 | 9.22 | 0.008 | 0.024 | 58 | 1.678
交流220kV | 2004-07-28 | 2013-10-21 | 9.2384 | 0.56 | 344.59 | 797.77 | 4.57 | 1.03 | 0.56 | 0 | 17.21 | 0.006 | 0.024 | 56 | 2.3151
交流220kV | 2002-12-15 | 2012-03-22 | 9.274 | 9.73 | 366.29 | 662.23 | 31.99 | 5.79 | 11.69 | 0 | 49.47 | 0.015 | 0.071 | 55 | 1.8079
交流220kV | 2002-12-20 | 2012-03-28 | 9.2767 | 3.6 | 107.5 | 432.5 | 4.4 | 2.4 | 1 | 0 | 7.8 | 0.01 | 0.25 | 52.8 | 4.0233
交流220kV | 2003-12-12 | 2013-03-22 | 9.2822 | 13 | 904 | 3847 | 23.92 | 16.92 | 10.77 | 0 | 51.61 | 0.001 | 0.5 | 50.4 | 4.2555
交流220kV | 2002-03-25 | 2011-07-06 | 9.2877 | 7.61 | 1698.7 | 4032.13 | 6.43 | 3 | 1.9 | 0 | 11.33 | 0 | 0 | 0 | 2.3737
220 | 2004-12-12 | 2014-03-26 | 9.2904 | 143.77 | 116.93 | 4038.14 | 24.58 | 32.65 | 6.86 | 0.5 | 64.59 | 0.054 | 0.002 | 46.8 | 34.5347
交流220kV | 2003-12-19 | 2013-04-02 | 9.2932 | 64.6 | 161.9 | 2436.4 | 8.7 | 0.5 | 5.9 | 0 | 15.1 | 0.003 | 0.39 | 54 | 15.0488
220 | 2001-12-21 | 2011-04-18 | 9.3288 | 10.44 | 582.25 | 1203.69 | 33.41 | 12.73 | 16.66 | 0.45 | 63.25 | 0.001 | 0.001 | 55 | 2.0673
交流220kV | 2004-07-06 | 2013-11-04 | 9.337 | 12.34 | 593.71 | 1135.82 | 13.21 | 0.32 | 1.34 | 0 | 14.87 | 0.009 | 0.016 | 69 | 1.9131
交流220kV | 2000-11-07 | 2010-03-09 | 9.3397 | 5.33 | 283.49 | 1848.82 | 7.26 | 1.18 | 1.62 | 0 | 10.06 | 0.041 | 0.978 | 48 | 6.5216
交流220kV | 2003-05-26 | 2012-09-24 | 9.3397 | 3.6 | 1296.18 | 5118.68 | 15.43 | 20.27 | 5.23 | 0 | 40.93 | 0.012 | 0.003 | 62 | 3.9491
220 | 2002-10-31 | 2012-03-13 | 9.3726 | 1.06 | 85.31 | 48.75 | 4.78 | 1.13 | 3.22 | 0 | 9.13 | 0.01 | 0 | 60 | 0.57145
交流220kV | 2004-11-12 | 2014-04-03 | 9.3945 | 10.72 | 903.3 | 1954.29 | 29.6 | 47.27 | 0 | 3.35 | 80.22 | 0.002 | 0.1 | 44 | 2.1635
交流220kV | 2002-01-25 | 2011-06-21 | 9.4082 | 3.5 | 554.3 | 6119.8 | 16.7 | 1.1 | 3 | 0 | 20.8 | 0.01 | 0 | 63.6 | 11.0406
交流220kV | 2003-10-08 | 2013-03-07 | 9.4192 | 29 | 179 | 1013 | 5.46 | 0.52 | 1.43 | 0 | 7.41 | 0.014 | 0.4 | 52 | 5.6592
交流220kV | 2004-07-08 | 2013-12-10 | 9.4301 | 5.9 | 855.58 | 13147.48 | 0 | 36.44 | 6.88 | 0 | 43.32 | 0 | 0 | 0 | 15.3667
交流220kV | 2004-10-01 | 2014-03-07 | 9.4356 | 26 | 508 | 2490 | 5.68 | 0.91 | 0.78 | 0 | 7.47 | 0.023 | 0.334 | 56 | 4.9016
交流220kV | 2001-10-09 | 2011-03-17 | 9.4411 | 3.01 | 63.61 | 1147.67 | 1.33 | 2.79 | 0 | 0 | 4.12 | 0.013 | 0.001 | 61.9 | 18.0423
交流220kV | 2003-12-20 | 2013-06-06 | 9.4685 | 10 | 872 | 4918.5 | 19.2 | 0 | 0 | 0 | 19.2 | 0.012 | 0.118 | 0 | 5.6405
交流220kV | 2003-07-28 | 2013-01-17 | 9.4822 | 5 | 454 | 1620 | 6.41 | 0.99 | 0.67 | 0 | 8.07 | 0.03 | 0.793 | 69 | 3.5683
交流220kV | 2003-07-28 | 2013-01-17 | 9.4822 | 4 | 492 | 1402 | 6.33 | 1.07 | 0.81 | 0 | 8.21 | 0.03 | 0.753 | 49 | 2.8496
交流220kV | 2003-07-28 | 2013-01-17 | 9.4822 | 4 | 530 | 1903 | 6.98 | 0.89 | 0.66 | 0 | 8.53 | 0.04 | 0.168 | 72 | 3.5906
交流220kV | 2002-01-13 | 2011-07-07 | 9.4849 | 4.8 | 227.7 | 5056.2 | 4.1 | 6 | 1.7 | 0 | 11.8 | 0 | 0 | 0 | 22.2055
交流220kV | 2001-12-17 | 2011-06-14 | 9.4959 | 3.5 | 481.3 | 4304.6 | 17.1 | 0 | 2.7 | 0 | 19.8 | 0.02 | 0 | 61.5 | 8.9437
交流220kV | 2003-11-02 | 2013-05-09 | 9.5233 | 31 | 698 | 283 | 20.4 | 0 | 0 | 0 | 20.4 | 0.006 | 0.076 | 54 | 0.40544
交流220kV | 2003-05-30 | 2012-12-05 | 9.526 | 6.7 | 243.7 | 2463.3 | 12.4 | 1.6 | 3.2 | 0 | 17.2 | 0 | 0 | 0 | 10.1079
交流220kV | 2002-12-17 | 2012-06-24 | 9.526 | 2.52 | 475.27 | 2196.9 | 6.54 | 0 | 0 | 0 | 6.54 | 0.03 | 0.317 | 60 | 4.6224
交流220kV | 2003-08-07 | 2013-03-05 | 9.5836 | 4.1 | 607.1 | 1075.7 | 7.3 | 0.6 | 1.8 | 0 | 9.7 | 0.009 | 0.197 | 60.4 | 1.7719
交流220kV | 2002-09-24 | 2012-04-28 | 9.6 | 7.72 | 892.29 | 1938.62 | 18.91 | 1.62 | 3.3 | 0 | 23.83 | 0.004 | 0.15 | 51 | 2.1726
交流220kV | 2001-11-28 | 2011-07-07 | 9.611 | 21.6 | 823.8 | 3039.1 | 10.4 | 1.1 | 3.5 | 0 | 15 | 0 | 0 | 0 | 3.6891
交流220kV | 2002-03-06 | 2011-10-14 | 9.6137 | 17 | 1349 | 5528 | 15.1 | 7.1 | 3.9 | 0.1 | 26.2 | 0.015 | 0.001 | 75 | 4.0979
交流220kV | 2002-03-06 | 2011-10-14 | 9.6137 | 26 | 1078 | 5940 | 8.3 | 9.2 | 2.3 | 0 | 19.8 | 0.015 | 0.001 | 75 | 5.5102
交流220kV | 2003-05-19 | 2012-12-27 | 9.6164 | 2.18 | 432.45 | 3471.47 | 12.63 | 10.3 | 3.14 | 0 | 26.07 | 0.009 | 0.003 | 60 | 8.0274
交流220kV | 2001-12-28 | 2011-08-10 | 9.6219 | 4.76 | 65 | 535 | 3.09 | 0.43 | 0.23 | 0 | 3.75 | 0.027 | 0.345 | 59.6 | 8.2308
交流220kV | 2004-04-22 | 2013-12-30 | 9.6959 | 3.51 | 366.11 | 578.45 | 5.65 | 1.79 | 0.95 | 0 | 8.39 | 0 | 0 | 0 | 1.58
交流220kV | 2002-03-25 | 2011-12-17 | 9.737 | 6.55 | 885.47 | 1971.95 | 6.72 | 1.18 | 1.55 | 0 | 9.45 | 0 | 0 | 0 | 2.227
交流220kV | 2003-06-18 | 2013-03-14 | 9.7452 | 11 | 882 | 2726 | 7.26 | 2.49 | 1.33 | 0 | 11.08 | 0.003 | 0.301 | 74.1 | 3.0907
交流220kV | 2003-06-18 | 2013-03-14 | 9.7452 | 12 | 921 | 2832 | 7.66 | 2.5 | 1.58 | 0 | 11.74 | 0.023 | 0.211 | 64.3 | 3.0749
交流220kV | 2003-06-18 | 2013-03-14 | 9.7452 | 7 | 822 | 2722 | 7.53 | 1.71 | 1.29 | 0 | 10.53 | 0.003 | 0.317 | 74.9 | 3.3114
交流220kV | 2002-06-26 | 2012-03-28 | 9.7616 | 3.16 | 1146.45 | 5428.82 | 11.01 | 1.66 | 4.5 | 0 | 17.17 | 0.008 | 0.16 | 52 | 4.7353
交流220kV | 2002-05-17 | 2012-02-22 | 9.7753 | 4 | 403 | 100 | 14.57 | 3.45 | 2.5 | 0 | 20.52 | 0.001 | 0.001 | 64.8 | 0.24814
220 | 2001-12-24 | 2011-10-10 | 9.8 | 12 | 318 | 814 | 19 | 8 | 6.8 | 0 | 33.8 | 0.008 | 0.001 | 53 | 2.5597
交流220kV | 2003-09-01 11:18 | 2013-06-18 | 9.8014 | 6.83 | 270.12 | 396.83 | 18.89 | 12.21 | 1.26 | 0 | 32.36 | 0.011 | 0.012 | 52.3 | 1.4691
交流220kV | 2003-05-01 | 2013-02-16 | 9.8055 | 37.47 | 382.85 | 2728.61 | 5.74 | 2.71 | 1.74 | 0.06 | 10.25 | 0.009 | 0.052 | 49 | 7.1271
交流220kV | 2004-04-23 | 2014-02-13 | 9.8164 | 2.4 | 301.7 | 1951.2 | 6.1 | 0.8 | 1.1 | 0 | 8 | 0.017 | 0.329 | 47.7 | 6.4674
交流220kV | 2001-06-04 | 2011-03-29 | 9.8219 | 6.31 | 1323.86 | 3580.94 | 15.74 | 2.88 | 3.59 | 0.3 | 22.51 | 0.01 | 0.005 | 62.1 | 2.7049
交流220kV | 2001-12-25 | 2011-10-20 | 9.8247 | 10 | 1220 | 7789 | 23.9 | 2.5 | 4.9 | 0.2 | 31.5 | 0.047 | 0.005 | 66 | 6.3844
交流220kV | 2001-12-25 | 2011-10-20 | 9.8247 | 13 | 1209 | 6057 | 22.4 | 2.2 | 4.8 | 0.4 | 29.8 | 0.045 | 0.006 | 61.2 | 5.0099
220 | 2001-12-28 | 2011-11-03 | 9.8548 | 21.55 | 311.85 | 2830.97 | 17.53 | 0.99 | 5.64 | 0 | 24.16 | 0.009 | 0.032 | 56.8 | 9.078
交流220kV | 2002-01-13 | 2011-11-24 | 9.8685 | 1.47 | 18.87 | 161.29 | 0.72 | 0 | 0 | 0 | 0.72 | 0 | 0 | 0 | 8.5474
交流220kV | 2001-07-29 | 2011-06-16 | 9.8877 | 1.4 | 378.8 | 3615 | 18.5 | 5.6 | 4.1 | 0 | 28.2 | 0.02 | 0 | 62.8 | 9.5433
交流220kV | 2002-01-25 | 2011-12-20 | 9.9068 | 6.1 | 633.4 | 3349 | 10.6 | 2.4 | 3.1 | 0 | 16.1 | 0 | 0 | 0 | 5.2873
交流220kV | 1998-12-26 | 2008-11-27 | 9.9288 | 7.58 | 238.62 | 1928.05 | 4.2 | 2.24 | 3.54 | 0 | 9.98 | 0.02 | 0.09 | 57 | 8.08
交流220kV | 2002-12-20 | 2012-11-24 | 9.937 | 4.4 | 121.4 | 453.5 | 5 | 2.3 | 1.5 | 0.1 | 8.9 | 0.03 | 0.213 | 59.6 | 3.7356
交流220kV | 2002-01-13 | 2011-12-20 | 9.9397 | 0.78 | 18.45 | 136.77 | 0.69 | 0 | 0 | 0 | 0.69 | 0 | 0 | 35.6 | 7.413
交流220kV | 2002-07-18 | 2012-06-27 | 9.9507 | 10.47 | 775.43 | 2360.48 | 25.75 | 2.71 | 5.54 | 0 | 34 | 0.027 | 0 | 59 | 3.0441
交流220kV | 2002-12-28 | 2012-12-10 | 9.9589 | 7.71 | 1283.82 | 5874.01 | 14.36 | 5.54 | 3.27 | 0.43 | 23.6 | 0.027 | 0.29 | 49 | 4.5754
交流220kV | 2003-05-26 | 2013-05-08 | 9.9589 | 4.16 | 1271.15 | 5001.35 | 17.4 | 23.39 | 6.02 | 0 | 46.81 | 0.015 | 0.132 | 50.4 | 3.9345
交流220kV | 2002-09-30 | 2012-09-19 | 9.9781 | 6.89 | 1038.26 | 2583.16 | 16.39 | 12.57 | 4.03 | 0 | 32.99 | 0.012 | 0.042 | 56.3 | 2.488
交流220kV | 2003-12-20 | 2013-12-12 | 9.9863 | 2.7 | 610.1 | 3634.5 | 11.8 | 0 | 0 | 0 | 11.8 | 0 | 0 | 0 | 5.9572
交流220kV | 2003-05-30 | 2013-05-22 | 9.9863 | 3.3 | 108.9 | 3041.3 | 8.5 | 1.7 | 3.3 | 0 | 13.5 | 0.013 | 0 | 65.5 | 27.9275
交流220kV | 2001-07-17 | 2011-07-11 | 9.989 | 8.4 | 1018.9 | 4162.2 | 13 | 3 | 5.9 | 0 | 21.9 | 0.01 | 0.5 | 61 | 4.085
交流220kV | 2001-06-25 | 2011-06-21 | 9.9945 | 3.1 | 470.5 | 10894 | 24.9 | 1.1 | 5.7 | 0 | 31.7 | 0.01 | 0 | 64.2 | 23.1541
交流220kV | 2001-12-17 | 2011-12-16 | 10.0027 | 31 | 414 | 3698 | 8.6 | 1.4 | 2.4 | 0 | 12.4 | 0 | 0 | 0 | 8.9324
交流220kV | 2002-12-17 | 2012-12-18 | 10.011 | 27.71 | 475.18 | 2060.78 | 6.58 | 0 | 0 | 0 | 6.58 | 0.007 | 0.32 | 60 | 4.3368
交流220kV | 2004-02-20 | 2014-03-04 | 10.0411 | 5.2 | 827.4 | 2312.7 | 21.8 | 4.6 | 5.6 | 0 | 32 | 0.006 | 0.001 | 48 | 2.7951
交流220kV | 2001-11-28 | 2011-12-22 | 10.0712 | 18.51 | 717.04 | 1460.15 | 10.46 | 2.69 | 0.71 | 0 | 13.86 | 0 | 0 | 36.8 | 2.0364
交流220kV | 2003-09-29 | 2013-10-28 | 10.0877 | 7.17 | 492 | 2193.41 | 10.61 | 3.55 | 2.22 | 0 | 16.38 | 0.006 | 0.009 | 59 | 4.4582
交流220kV | 2002-09-12 | 2012-10-12 | 10.0904 | 6.48 | 613.32 | 1281.85 | 9.39 | 0.83 | 2.05 | 0 | 12.27 | 0.01 | 0.04 | 49 | 2.09
220 | 2003-11-06 | 2013-12-09 | 10.0986 | 2.24 | 220.55 | 1007.07 | 4.28 | 1.05 | 0.72 | 0 | 6.05 | 0.031 | 0.078 | 54 | 4.5662
交流220kV | 2001-03-15 | 2011-04-20 | 10.1041 | 5.7 | 334.26 | 1230.21 | 17.8 | 4.68 | 7.64 | 0 | 30.12 | 0.01 | 0.004 | 52.8 | 3.6804
交流220kV | 2003-09-15 | 2013-10-28 | 10.126 | 3.9 | 315.79 | 1811.41 | 9.79 | 1.44 | 1.41 | 0 | 12.64 | 0.008 | 0.018 | 60 | 5.7361
交流220kV | 2002-07-28 | 2012-09-09 | 10.126 | 5.84 | 781.51 | 3961.39 | 20.69 | 5.44 | 6.44 | 0 | 32.57 | 0.006 | 0.002 | 62 | 5.0689
交流220kV | 2002-07-28 | 2012-09-09 | 10.126 | 3.09 | 369.27 | 2122.42 | 13 | 0.54 | 6.03 | 0 | 19.57 | 0.011 | 0.003 | 62 | 5.7476
交流220kV | 2001-02-28 | 2011-04-15 | 10.1315 | 4.4 | 360.6 | 1270 | 7 | 1.6 | 1.3 | 0 | 9.9 | 0.003 | 0.09 | 51 | 3.5219
交流220kV | 2001-11-28 | 2012-01-16 | 10.1397 | 8.56 | 1009.12 | 3088.23 | 11.85 | 1 | 2.7 | 0 | 15.55 | 0.01 | 0.005 | 53.2 | 3.0603
交流220kV | 2002-10-15 | 2012-12-07 | 10.1534 | 8.03 | 1043.19 | 4088.46 | 20.23 | 9.05 | 4.51 | 0.33 | 34.12 | 0.018 | 0.015 | 52 | 3.9192
交流220kV | 2003-01-20 | 2013-03-27 | 10.189 | 36.79 | 184.21 | 1128.54 | 10.21 | 4.5 | 5.13 | 0 | 19.84 | 0.01 | 0.17 | 51 | 6.1264
交流220kV | 2001-03-31 | 2011-06-09 | 10.1973 | 11 | 605 | 3402 | 12 | 1 | 3.6 | 0 | 16.6 | 0.008 | 0.004 | 49 | 5.6231
220 | 2003-01-01 | 2013-03-15 | 10.2082 | 10.71 | 1396.64 | 12114.49 | 141.84 | 329.6 | 51.82 | 0.22 | 523.48 | 0.019 | 0.074 | 46 | 8.674
交流220kV | 2002-01-13 | 2012-04-06 | 10.2356 | 4.07 | 30.69 | 221.93 | 1.1 | 0 | 0 | 0 | 1.1 | 0 | 0 | 0 | 7.2313
交流220kV | 2001-05-31 | 2011-08-24 | 10.2384 | 1.85 | 207.57 | 1691.9 | 9.59 | 0.55 | 2.69 | 0 | 12.83 | 0.002 | 0.001 | 62 | 8.151
交流220kV | 2002-04-16 | 2012-07-10 | 10.2411 | 10.35 | 871.71 | 4287.93 | 15.47 | 2.06 | 4.34 | 0 | 21.87 | 0.006 | 0.001 | 59 | 4.919
交流220kV | 2002-12-18 | 2013-03-21 | 10.263 | 5.6 | 886.9 | 5328.6 | 14.5 | 1.8 | 3.5 | 0.2 | 20 | 0.006 | 0.06 | 55 | 6.0081
交流220kV | 2001-12-28 | 2012-04-01 | 10.2658 | 2.77 | 181.23 | 293 | 2.26 | 0.31 | 0.35 | 0.84 | 3.76 | 0.031 | 0.097 | 59 | 1.6167
交流220kV | 2002-11-20 | 2013-02-23 | 10.2685 | 2.18 | 652.63 | 4614.86 | 13.93 | 1.93 | 3.15 | 0 | 19.01 | 0.027 | 0.21 | 55 | 7.0712
交流220kV | 2000-02-26 | 2010-06-02 | 10.2712 | 4.59 | 636.82 | 1688.35 | 20.92 | 2.99 | 15.77 | 0 | 39.68 | 0.004 | 0.406 | 64.8 | 2.6512
交流220kV | 2003-12-12 | 2014-03-19 | 10.274 | 10 | 1009 | 3874 | 25.7 | 14.64 | 8.6 | 0 | 48.94 | 0.001 | 0.03 | 50 | 3.8394
220 | 2001-12-24 | 2012-04-09 | 10.2986 | 4 | 155 | 79 | 4 | 0.4 | 0.2 | 0 | 4.6 | 0.006 | 0.051 | 53 | 0.50968
交流220kV | 2001-05-07 | 2011-08-24 | 10.3041 | 11.52 | 110.65 | 1311.02 | 11.52 | 0.81 | 3.11 | 0 | 15.44 | 0.003 | 0.002 | 48 | 11.8484
交流220kV | 2001-12-09 | 2012-04-01 | 10.3178 | 6.6 | 1207.32 | 4144.89 | 26.02 | 1.87 | 8.44 | 0 | 36.33 | 0.008 | 0.118 | 55 | 3.4331
交流220kV | 2001-08-19 | 2011-12-13 | 10.3233 | 5.64 | 1050.87 | 4166.18 | 12.69 | 14.5 | 4.19 | 0 | 31.38 | 0.003 | 0.02 | 49 | 3.9645
交流220kV | 2002-03-25 | 2012-07-19 | 10.326 | 7.74 | 966.41 | 2533.72 | 10.48 | 2.03 | 3.57 | 0 | 16.08 | 0.029 | 0.018 | 56.5 | 2.6218
交流220kV | 1998-12-26 | 2009-04-23 | 10.3315 | 12.06 | 314.94 | 2351.06 | 5.32 | 3.38 | 1.1 | 0 | 9.8 | 0.013 | 0.07 | 49 | 7.4651
交流220kV | 2001-11-28 | 2012-03-27 | 10.3342 | 17.69 | 989.38 | 1752.88 | 10.71 | 3.52 | 0.76 | 0 | 14.99 | 0 | 0 | 0 | 1.7717
交流220kV | 2001-08-28 | 2011-12-27 | 10.337 | 8 | 384 | 1796 | 4 | 0 | 0 | 0 | 4 | 0 | 0 | 0 | 4.6771
交流220kV | 2002-01-27 | 2012-06-08 | 10.3699 | 5.22 | 535.55 | 4928.23 | 12.38 | 6.3 | 2.6 | 0 | 21.28 | 0.004 | 0.034 | 65.7 | 9.2022
交流220kV | 2001-11-10 | 2012-03-23 | 10.3726 | 1.44 | 57.1 | 239.2 | 5.21 | 1.97 | 1.09 | 0 | 8.27 | 0.016 | 0.086 | 53 | 4.1891
交流220kV | 2001-07-29 | 2011-12-16 | 10.389 | 6.3 | 362 | 4054 | 10.5 | 4.3 | 2.9 | 0 | 17.7 | 0 | 0 | 0 | 11.1989
交流220kV | 2001-03-08 | 2011-08-09 | 10.4274 | 270 | 969 | 3880 | 54 | 1.6 | 12 | 0 | 67.6 | 0 | 0 | 0 | 4.0041
交流220kV | 2000-08-03 | 2011-01-07 | 10.4356 | 2.54 | 1181.49 | 3102.31 | 15.35 | 4.97 | 4.08 | 0 | 24.4 | 0.011 | 0.004 | 53.5 | 2.6258
交流220kV | 2001-10-09 | 2012-03-17 | 10.4438 | 5.04 | 79.3 | 1040.57 | 1.65 | 0.37 | 0.6 | 0 | 2.62 | 0.011 | 0.001 | 49.4 | 13.1219
交流220kV | 2001-06-28 | 2011-12-08 | 10.4521 | 9 | 673 | 1856 | 6.1 | 0.7 | 1.2 | 0 | 8 | 0.01 | 0.001 | 55 | 2.7578
交流220kV | 2001-04-18 | 2011-09-30 | 10.4575 | 8 | 254 | 2375 | 3.8 | 0.9 | 1.1 | 0 | 5.8 | 0.003 | 0.001 | 62 | 9.3504
交流220kV | 2003-05-19 | 2013-11-01 | 10.463 | 1.46 | 364.88 | 2895.97 | 14.01 | 10.66 | 3.39 | 0 | 28.06 | 0.012 | 0.049 | 60 | 7.9368
交流220kV | 2002-12-17 | 2013-06-06 | 10.4767 | 1.63 | 474.02 | 2229.04 | 5.93 | 0 | 0 | 0 | 5.93 | 0.006 | 0.32 | 45 | 4.7024
交流220kV | 2001-06-25 | 2011-12-20 | 10.4932 | 3.7 | 903.7 | 5812 | 21.4 | 4.8 | 5.2 | 0 | 31.4 | 0 | 0 | 0 | 6.4313
交流220kV | 2003-08-30 | 2014-03-04 | 10.5178 | 4.4 | 924.2 | 2249 | 30.4 | 24.3 | 9.9 | 0 | 64.6 | 0.006 | 0.001 | 61.8 | 2.4335
交流220kV | 2003-06-01 | 2013-12-05 | 10.5205 | 23.4 | 208.3 | 3547.5 | 20.2 | 1.9 | 4.3 | 0 | 26.4 | 0 | 0 | 0 | 17.0307
交流220kV | 2003-05-30 | 2013-12-10 | 10.5397 | 6.9 | 283 | 4190.3 | 14.5 | 2.2 | 4.1 | 0 | 20.8 | 0 | 0 | 0 | 14.8067
交流220kV | 2001-03-08 | 2011-09-26 | 10.5589 | 442 | 1293 | 4391 | 67.6 | 2 | 16 | 0 | 85.6 | 0 | 0 | 0 | 3.396
交流220kV | 2000-12-04 | 2011-06-28 | 10.5699 | 20.5 | 847.9 | 2871.6 | 11.5 | 11.9 | 0 | 0 | 23.4 | 0 | 0 | 0 | 3.3867
交流220kV | 2001-08-19 | 2012-03-16 | 10.5808 | 9.9 | 1201.02 | 4671.87 | 14.13 | 16.51 | 4.85 | 0.47 | 35.96 | 0.003 | 0.2 | 41 | 3.8899
交流220kV | 2003-05-26 | 2013-12-23 | 10.5863 | 3.08 | 992.95 | 3254.64 | 14.42 | 18.82 | 4.76 | 0 | 38 | 0.015 | 0.087 | 58 | 3.2777
交流220kV | 2001-01-19 | 2011-08-24 | 10.6 | 18.73 | 196.36 | 1719.36 | 14.53 | 1.19 | 3.71 | 0 | 19.43 | 0.004 | 0.002 | 61 | 8.7562
交流220kV | 2001-11-28 | 2012-07-03 | 10.6027 | 18.2 | 1018.76 | 1889.22 | 12.81 | 0.84 | 7.23 | 0 | 20.88 | 0.001 | 0 | 63.8 | 1.8544
交流220kV | 2001-03-15 | 2011-10-26 | 10.6219 | 14 | 902 | 3673 | 7.2 | 2.5 | 1.4 | 0.4 | 11.5 | 0.048 | 0.081 | 70.2 | 4.0721
交流220kV | 2002-12-28 | 2013-08-19 | 10.6493 | 14.12 | 1053.89 | 5284.46 | 29.2 | 101.62 | 46.9 | 0 | 177.72 | 0.005 | 0.001 | 56 | 5.0142
交流220kV | 2001-07-29 | 2012-03-28 | 10.6712 | 3.6 | 223.9 | 1780 | 7.4 | 2.6 | 2 | 0 | 12 | 0.012 | 0 | 67 | 7.95
交流220kV | 2001-06-21 | 2012-02-23 | 10.6822 | 11.67 | 1379.77 | 4617.77 | 28.85 | 8.04 | 8.08 | 0.18 | 45.15 | 0.021 | 0.003 | 64.8 | 3.3468
交流220kV | 2000-08-23 | 2011-05-23 | 10.7534 | 38.68 | 298.51 | 465.36 | 23.26 | 5.23 | 5.78 | 0 | 34.27 | 0.01 | 0.001 | 58 | 1.5589
交流220kV | 2001-08-28 | 2012-05-31 | 10.7644 | 8 | 335 | 1813 | 4.53 | 0.47 | 1.03 | 0 | 6.03 | 0.043 | 0.095 | 53 | 5.4119
交流220kV | 2001-03-08 | 2011-12-14 | 10.7753 | 381 | 1152 | 3551 | 75 | 1.7 | 14.2 | 0 | 90.9 | 0.016 | 0 | 0 | 3.0825
交流220kV | 2002-03-25 | 2012-12-31 | 10.7781 | 5.3 | 818.89 | 1850.92 | 7.2 | 2.03 | 1.85 | 0 | 11.08 | 0 | 0 | 0 | 2.2603
220 | 2003-01-01 | 2013-10-15 | 10.7945 | 0.4 | 0.4 | 186.43 | 1.35 | 3.73 | 1.2 | 0 | 6.28 | 0.026 | 0.153 | 56 | 466.075
交流220kV | 2000-05-17 | 2011-03-02 | 10.7973 | 12 | 1498 | 4397 | 16.3 | 2.6 | 5.2 | 0 | 24.1 | 0.007 | 0.001 | 49 | 2.9352
交流220kV | 2001-06-04 | 2012-03-28 | 10.8219 | 4.69 | 564.49 | 1937.78 | 16.21 | 12.91 | 5.71 | 0.28 | 35.11 | 0.001 | 0.005 | 56 | 3.4328
交流220kV | 2002-12-28 | 2013-10-24 | 10.8301 | 9.83 | 1590.18 | 7653.05 | 18.35 | 6.59 | 3.94 | 0.53 | 29.41 | 0.028 | 0.13 | 43 | 4.8127
交流220kV | 2002-03-06 | 2012-12-31 | 10.8301 | 6 | 158 | 258 | 0.3 | 0.2 | 0.1 | 0 | 0.6 | 0.032 | 0.21 | 56 | 1.6329
交流220kV | 2002-03-06 | 2012-12-31 | 10.8301 | 9 | 154 | 245 | 0.2 | 0.1 | 0.2 | 0 | 0.5 | 0.015 | 0.14 | 56 | 1.5909
交流220kV | 2002-05-17 | 2013-03-21 | 10.8521 | 5 | 371 | 140 | 15.08 | 3.39 | 2.99 | 0 | 21.46 | 0.006 | 0.15 | 50 | 0.37736
交流220kV | 2002-07-18 | 2013-05-24 | 10.8575 | 8.63 | 637.77 | 2973.03 | 26.91 | 2.84 | 5.35 | 0 | 35.1 | 0.06 | 0.001 | 60 | 4.6616
交流220kV | 2002-01-25 | 2012-12-05 | 10.8685 | 7.4 | 791.9 | 4820.6 | 14.8 | 3.2 | 3.9 | 0 | 21.9 | 0 | 0 | 0 | 6.0874
交流220kV | 2002-01-27 | 2012-12-10 | 10.8767 | 4.8 | 567.48 | 2042.96 | 13.24 | 5.59 | 2.27 | 0 | 21.1 | 0 | 0 | 0 | 3.6001
交流220kV | 2001-07-10 | 2012-05-23 | 10.8767 | 6.96 | 606.88 | 1985.21 | 16.7 | 4.56 | 10.41 | 0 | 31.67 | 0.015 | 0.341 | 56.2 | 3.2712
交流220kV | 2002-04-07 | 2013-03-03 | 10.9123 | 13.04 | 204.13 | 650.38 | 18.23 | 5.75 | 0 | 0 | 23.98 | 0.007 | 0.005 | 46.8 | 3.1861
交流220kV | 2002-01-13 | 2012-12-20 | 10.9425 | 2.18 | 26.88 | 169.2 | 3.7 | 0.23 | 0.44 | 0 | 4.37 | 0 | 0 | 0 | 6.2946
交流220kV | 2002-07-16 | 2013-06-28 | 10.9589 | 5 | 587.9 | 7581.2 | 25.8 | 7.3 | 5.5 | 0 | 38.6 | 0.003 | 0.09 | 51.3 | 12.8954
交流220kV | 2001-12-17 | 2012-12-11 | 10.9918 | 5.3 | 425.9 | 2766.3 | 10.1 | 0.7 | 2.6 | 0 | 13.4 | 0 | 0 | 0 | 6.4952
交流220kV | 1995-10-14 | 2006-10-10 | 10.9973 | 28.1 | 1427 | 10665.1 | 16.5 | 32.1 | 5 | 0 | 53.6 | 0.009 | 0.119 | 56 | 7.4738
交流220kV | 2001-03-08 | 2012-03-07 | 11.0055 | 386 | 1166 | 3500 | 74.7 | 1.6 | 13.4 | 0 | 89.7 | 0 | 0 | 0 | 3.0017
交流220kV | 2000-12-11 | 2011-12-21 | 11.0329 | 7.84 | 756.47 | 3263.69 | 15.67 | 0.73 | 0.51 | 0 | 16.91 | 0 | 0.006 | 52 | 4.3144
交流220kV | 1999-12-22 | 2011-01-10 | 11.0603 | 28.22 | 527 | 1598 | 17.67 | 7.69 | 5 | 0.19 | 30.55 | 0.035 | 0.479 | 47.7 | 3.0323
交流220kV | 2002-10-15 | 2013-11-05 | 11.0658 | 9.93 | 1102.01 | 4667.34 | 20.27 | 9.04 | 4.56 | 0.34 | 34.21 | 0.021 | 0.28 | 49 | 4.2353
交流220kV | 2001-11-28 | 2012-12-20 | 11.0685 | 9.95 | 251.63 | 569.87 | 7.36 | 0.55 | 2.17 | 0 | 10.08 | 0 | 0 | 0 | 2.2647
交流220kV | 2001-03-15 | 2012-04-09 | 11.0767 | 4.2 | 250.2 | 1184.3 | 17.8 | 5.6 | 7.7 | 0 | 31.1 | 0.008 | 0.003 | 58.2 | 4.7334
交流220kV | 2001-03-15 | 2012-04-17 | 11.0986 | 3.8 | 222.4 | 1214.9 | 13.3 | 3.7 | 6.6 | 0 | 23.6 | 0.01 | 0.003 | 59.2 | 5.4627
交流220kV | 2002-04-16 | 2013-05-23 | 11.1096 | 6.92 | 764.23 | 3931.72 | 16.59 | 2.44 | 4.39 | 0 | 23.42 | 0.06 | 0.001 | 59 | 5.1447
交流220kV | 2002-03-06 | 2013-04-15 | 11.1178 | 16 | 680 | 4873 | 5.9 | 10.6 | 1.8 | 0 | 18.3 | 0.015 | 0.001 | 74 | 7.1662
交流220kV | 2000-08-01 | 2011-09-15 | 11.1288 | 27 | 1490 | 7492 | 16.1 | 5.4 | 3.2 | 0 | 24.7 | 0.004 | 0.002 | 74.8 | 5.0282
交流220kV | 2001-03-31 | 2012-05-22 | 11.1507 | 7 | 170 | 2734 | 5.4 | 1.6 | 6 | 0 | 13 | 0.014 | 0.002 | 48 | 16.0824
交流220kV | 2000-08-01 | 2011-09-30 | 11.1699 | 10 | 312 | 2257 | 4.4 | 0.9 | 1.1 | 0 | 6.4 | 0.003 | 0.001 | 49.9 | 7.234
交流220kV | 2001-11-10 | 2013-01-11 | 11.1781 | 10.57 | 52.3 | 2834.37 | 5.2 | 5.3 | 4.85 | 0 | 15.35 | 0.02 | 0.181 | 53 | 54.1945
交流220kV | 2000-01-20 | 2011-03-25 | 11.1836 | 16 | 956 | 4238 | 13 | 2.6 | 0.8 | 0 | 16.4 | 0.005 | 0.001 | 49 | 4.4331
交流220kV | 2002-03-25 | 2013-06-06 | 11.2082 | 5.87 | 1051.7 | 2347.9 | 14.19 | 2.54 | 2.12 | 0 | 18.85 | 0 | 0 | 0 | 2.2325
交流220kV | 2002-07-28 | 2013-10-15 | 11.2247 | 1.91 | 303.91 | 1782.27 | 13.68 | 0.55 | 6.36 | 0 | 20.59 | 0.012 | 0.051 | 63.5 | 5.8645
交流220kV | 1999-10-20 | 2011-01-10 | 11.2329 | 12.13 | 1602 | 3594 | 20.65 | 8.69 | 5.43 | 0.13 | 34.9 | 0.031 | 0.512 | 57.8 | 2.2434
交流220kV | 2001-03-08 | 2012-06-01 | 11.2411 | 304.22 | 1254.03 | 4350.08 | 71.02 | 1.74 | 14.12 | 0 | 86.88 | 0.018 | 0.136 | 0 | 3.4689
交流220kV | 2002-12-20 | 2014-03-17 | 11.2466 | 44.4 | 113.9 | 756 | 6.4 | 2.3 | 1.9 | 0 | 10.6 | 0.003 | 0.26 | 52 | 6.6374
220 | 2001-12-24 | 2013-03-28 | 11.2658 | 4 | 190 | 787 | 13 | 6 | 6.1 | 0 | 25.1 | 0.007 | 0.001 | 51 | 4.1421
交流220kV | 2000-12-16 | 2012-03-23 | 11.274 | 7 | 284 | 1423 | 21.49 | 22.51 | 8.96 | 0.11 | 53.07 | 0.001 | 0.001 | 46.7 | 5.0106
交流220kV | 2001-08-28 | 2012-12-05 | 11.2795 | 7 | 442 | 2216 | 4 | 1 | 1 | 0 | 6 | 0 | 0 | 0 | 5.0136
交流220kV | 2001-01-17 | 2012-04-26 | 11.2795 | 5.25 | 699.21 | 3860.72 | 24.66 | 1.25 | 6.98 | 0 | 32.89 | 0.026 | 0.086 | 54 | 5.5215
交流220kV | 2001-05-31 | 2012-09-09 | 11.2849 | 2.13 | 674.68 | 4343.86 | 11.96 | 1.35 | 3.26 | 0.14 | 16.71 | 0.008 | 0.001 | 63 | 6.4384
交流220kV | 2000-11-29 | 2012-03-14 | 11.2959 | 6 | 475 | 1224 | 15.93 | 2.98 | 3.85 | 0 | 22.76 | 0.021 | 0.057 | 52.8 | 2.5768
交流220kV | 2001-05-07 | 2012-08-24 | 11.3068 | 19.8 | 375.5 | 1989 | 14.9 | 0 | 4.1 | 0 | 19 | 0.015 | 0.132 | 55.7 | 5.2969
交流220kV | 2001-06-01 | 2012-09-24 | 11.3233 | 5.25 | 340.1 | 2919.23 | 4.09 | 13.6 | 2.16 | 0 | 19.85 | 0.009 | 0.002 | 62 | 8.5834
交流220kV | 2000-12-04 | 2012-03-31 | 11.3288 | 12.8 | 635.7 | 1737.1 | 7.6 | 7.1 | 0 | 0 | 14.7 | 0 | 0 | 0 | 2.7326
交流220kV | 2001-08-19 | 2012-12-14 | 11.3288 | 10.06 | 1006.4 | 3997.53 | 12.78 | 14.63 | 3.85 | 0.5 | 31.76 | 0.003 | 0.2 | 40 | 3.9721
交流220kV | 2002-01-27 | 2013-06-04 | 11.3589 | 4.94 | 583.96 | 2329.22 | 12.83 | 6.14 | 2.39 | 0 | 21.36 | 0.002 | 0.047 | 62 | 3.9887
交流220kV | 2001-04-21 | 2012-08-27 | 11.3589 | 4.09 | 1102.39 | 2996.55 | 12.7 | 6.52 | 2.36 | 0 | 21.58 | 0.008 | 0.003 | 45 | 2.7182
交流220kV | 2001-12-28 | 2013-05-10 | 11.3726 | 7.91 | 226.73 | 1120.39 | 10.53 | 1.32 | 1.39 | 2.7 | 15.94 | 0.058 | 0.219 | 54 | 4.9415
交流220kV | 2001-07-29 | 2012-12-11 | 11.3781 | 4.3 | 375.5 | 2514.3 | 10.9 | 2.9 | 2.4 | 0 | 16.2 | 0 | 0 | 0 | 6.6959
交流220kV | 2001-12-28 | 2013-05-13 | 11.3808 | 7.91 | 314.2 | 1120.39 | 2.54 | 1.32 | 1.39 | 3.1 | 8.35 | 0.058 | 0.219 | 53 | 3.5658
交流220kV | 2002-01-13 | 2013-06-06 | 11.4027 | 41.36 | 85.4 | 564.51 | 7.07 | 0 | 0.36 | 0 | 7.43 | 0 | 0 | 0 | 6.6102
交流220kV | 2000-11-01 | 2012-03-29 | 11.4137 | 3.41 | 104.29 | 721.22 | 18.86 | 0.73 | 0.58 | 0 | 20.17 | 0.009 | 0.05 | 58 | 6.9155
交流220kV | 2002-01-25 | 2013-06-25 | 11.4219 | 6.5 | 645 | 6747.5 | 13.4 | 4.1 | 4.2 | 0 | 21.7 | 0.012 | 0 | 63.4 | 10.4612
交流220kV | 2002-07-12 | 2013-12-12 | 11.4274 | 11.1 | 1074.15 | 4210.1 | 16.67 | 7.74 | 3.3 | 1.15 | 28.86 | 0.007 | 0.1 | 60 | 3.9195
交流220kV | 2001-12-09 | 2013-05-14 | 11.4356 | 6.12 | 1061.3 | 4102.1 | 31.91 | 1.98 | 9.87 | 0 | 43.76 | 0.006 | 0.165 | 57 | 3.8652
交流220kV | 2000-12-16 | 2012-05-22 | 11.4384 | 18 | 651 | 2472 | 22.16 | 19.31 | 6.46 | 0.13 | 48.06 | 0.001 | 0.001 | 50 | 3.7972
交流220kV | 2001-06-25 | 2012-12-05 | 11.4548 | 3.9 | 949.1 | 5256.4 | 22.7 | 4.5 | 4.6 | 0 | 31.8 | 0 | 0 | 0 | 5.5383
交流220kV | 2000-05-17 | 2011-11-02 | 11.4685 | 14 | 1405 | 4218 | 16.8 | 3.1 | 5.7 | 0 | 25.6 | 0.008 | 0.001 | 50 | 3.0021
交流220kV | 2001-08-28 | 2013-02-20 | 11.4904 | 7 | 397 | 1682 | 5 | 1 | 1 | 0 | 7 | 0 | 0 | 0 | 4.2368
交流220kV | 1999-09-27 | 2011-03-22 | 11.4904 | 11 | 168.36 | 1606.85 | 2.95 | 2.39 | 1.31 | 0 | 6.65 | 0.004 | 0.001 | 53.6 | 9.5441
交流220kV | 1996-01-04 | 2007-07-02 | 11.4986 | 23.02 | 132.26 | 468.16 | 9.18 | 14.81 | 3.58 | 0 | 27.57 | 0.011 | 0.037 | 60.9 | 3.5397
交流220kV | 2001-06-28 | 2012-12-27 | 11.5068 | 8 | 798 | 2340 | 7.32 | 0.81 | 1.66 | 0 | 9.79 | 0.004 | 0.153 | 52 | 2.9323
交流220kV | 2001-12-17 | 2013-06-21 | 11.5178 | 6.9 | 454.3 | 4969.5 | 11.3 | 0.9 | 3.6 | 0 | 15.8 | 0.036 | 0 | 55.3 | 10.9388
交流220kV | 2001-11-28 | 2013-06-06 | 11.5288 | 15.33 | 715.84 | 1458.29 | 10.25 | 2.24 | 0.61 | 0 | 13.1 | 0 | 0 | 0 | 2.0372
交流220kV | 2000-12-11 | 2012-06-21 | 11.5342 | 8.73 | 488.46 | 3910.29 | 7.84 | 4.04 | 0.84 | 0 | 12.72 | 0 | 0 | 0 | 8.0053
交流220kV | 2001-09-22 | 2013-04-10 | 11.5562 | 7 | 519 | 2021 | 3.66 | 24.54 | 1.55 | 0.49 | 30.24 | 0.008 | 0.3 | 71 | 3.894
交流220kV | 2001-01-19 | 2012-08-24 | 11.6027 | 26.5 | 570.4 | 2448 | 16 | 0 | 3.9 | 0 | 19.9 | 0.015 | 0.116 | 53.6 | 4.2917
交流220kV | 1999-12-22 | 2011-08-01 | 11.6164 | 13.06 | 523 | 2208 | 17.47 | 7.08 | 5.72 | 0 | 30.27 | 0.034 | 0.482 | 57.3 | 4.2218
交流220kV | 2002-03-06 | 2013-10-25 | 11.6466 | 15 | 532 | 4084 | 6.5 | 12.9 | 2.1 | 0 | 21.5 | 0.021 | 0.009 | 68 | 7.6767
交流220kV | 2001-03-15 | 2012-11-25 | 11.7068 | 3.1 | 169.2 | 1854.4 | 11.2 | 3.2 | 5.9 | 0 | 20.3 | 0.013 | 0.002 | 59.8 | 10.9598
交流220kV | 2001-11-28 | 2013-08-13 | 11.7151 | 6.47 | 903.21 | 4343.41 | 12.17 | 0.83 | 2.66 | 0 | 15.66 | 0.01 | 0.078 | 54.6 | 4.8089
交流220kV | 2000-07-03 | 2012-03-22 | 11.726 | 8.49 | 635.49 | 1721.8 | 21.78 | 3.6 | 3.44 | 0 | 28.82 | 0.007 | 0.001 | 54.3 | 2.7094
交流220kV | 2000-06-20 | 2012-03-13 | 11.737 | 4 | 275 | 317 | 62.62 | 3.4 | 10.66 | 0 | 76.68 | 0.012 | 0.12 | 51.4 | 1.1527
交流220kV | 1997-03-06 | 2008-12-03 | 11.7534 | 3 | 250 | 1825 | 4.66 | 2.67 | 1.07 | 0 | 8.4 | 0.02 | 0.11 | 48 | 7.3
交流220kV | 2000-08-23 | 2012-05-24 | 11.7589 | 66.42 | 469.11 | 1212.47 | 34.18 | 5.72 | 6.54 | 0 | 46.44 | 0.003 | 0.001 | 58 | 2.5846
交流220kV | 2001-03-08 | 2012-12-11 | 11.7699 | 328 | 1260 | 3971 | 69.8 | 1.9 | 14 | 0 | 85.7 | 0 | 0 | 0 | 3.1516
交流220kV | 2001-08-19 | 2013-05-24 | 11.7699 | 29.16 | 375.25 | 4224.16 | 6.61 | 10.18 | 2.77 | 0.37 | 19.93 | 0.003 | 0.25 | 56 | 11.2569
交流220kV | 2002-03-25 | 2013-12-30 | 11.7753 | 5.94 | 992.64 | 2140.97 | 10.41 | 2.73 | 2.51 | 0 | 15.65 | 0 | 0 | 0 | 2.1568
交流220kV | 1999-10-20 | 2011-08-01 | 11.789 | 27.86 | 1008 | 3592 | 13.48 | 4.67 | 3.81 | 0 | 21.96 | 0.033 | 0.547 | 55.4 | 3.5635
220 | 2001-06-01 | 2013-03-15 | 11.7945 | 8.58 | 395.67 | 1540.24 | 39.6 | 14.66 | 13.91 | 0 | 68.17 | 0.003 | 1.7 | 49.7 | 3.8927
交流220kV | 2000-06-01 | 2012-03-16 | 11.7973 | 10.07 | 724.59 | 1061.11 | 7.28 | 1.23 | 1.49 | 0 | 10 | 0.005 | 0.001 | 54 | 1.4644
交流220kV | 1998-06-24 | 2010-04-14 | 11.8137 | 2.98 | 261.48 | 1137.58 | 5.22 | 0.95 | 1.31 | 0 | 7.48 | 0.016 | 0.775 | 46 | 4.3505
交流220kV | 2001-07-29 | 2013-05-22 | 11.8219 | 4.1 | 374.5 | 5121.8 | 12.8 | 3.8 | 3.6 | 0 | 20.2 | 0.02 | 0 | 66.7 | 13.6764
交流220kV | 2001-08-28 | 2013-07-03 | 11.8548 | 9 | 514 | 2529 | 5 | 1 | 1 | 0 | 7 | 0.045 | 0.034 | 51 | 4.9202
交流220kV | 2002-05-17 | 2014-03-24 | 11.8603 | 3 | 356 | 185 | 16.72 | 4.3 | 3.74 | 0 | 24.76 | 0.001 | 0.07 | 50 | 0.51966
交流220kV | 2000-12-06 | 2012-10-18 | 11.874 | 21.82 | 186.88 | 1471.18 | 14.27 | 1.38 | 10.66 | 0 | 26.31 | 0.018 | 0.18 | 64 | 7.8723
交流220kV | 2002-01-27 | 2013-12-10 | 11.8767 | 4.34 | 645.22 | 2721.22 | 13.65 | 5.79 | 2.29 | 0 | 21.73 | 0 | 0 | 0 | 4.2175
交流220kV | 2000-12-04 | 2012-10-19 | 11.8822 | 13.5 | 545.3 | 2133.1 | 11.4 | 7.4 | 2.1 | 0 | 20.9 | 0 | 0 | 0 | 3.9118
交流220kV | 2000-12-04 | 2012-10-19 | 11.8822 | 13.54 | 545.25 | 2133.07 | 11.39 | 7.36 | 2.06 | 0 | 20.81 | 0 | 0 | 0 | 3.9121
交流220kV | 2002-01-25 | 2013-12-11 | 11.8849 | 5.7 | 781.4 | 5488.2 | 15.5 | 3.2 | 4.4 | 0 | 23.1 | 0 | 0 | 0 | 7.0235
交流220kV | 2001-06-04 | 2013-04-24 | 11.8959 | 5.7 | 1467.9 | 3972.5 | 23 | 14.9 | 6.4 | 0 | 44.3 | 0.012 | 0.004 | 52.4 | 2.7062
交流220kV | 2001-06-04 | 2013-04-26 | 11.9014 | 5.9 | 1351.2 | 3664.9 | 21.3 | 13.8 | 5.8 | 0.2 | 41.1 | 0.001 | 0.001 | 60.2 | 2.7123
交流220kV | 2001-06-25 | 2013-05-21 | 11.9123 | 1.6 | 404.8 | 6261.7 | 15.1 | 4.6 | 5.2 | 0 | 24.9 | 0.017 | 0 | 65.4 | 15.4686
交流220kV | 2002-01-13 | 2013-12-19 | 11.9397 | 1.46 | 7.08 | 48.36 | 5.95 | 0 | 0 | 0 | 5.95 | 0 | 0 | 55.3 | 6.8305
交流220kV | 2000-12-25 | 2012-11-30 | 11.9397 | 11.14 | 135 | 1473 | 5 | 3.21 | 3.42 | 0.11 | 11.74 | 0.012 | 0.002 | 42 | 10.9111
交流220kV | 2001-06-01 | 2013-05-08 | 11.9425 | 2.16 | 211.96 | 3355.62 | 4.27 | 17.62 | 2.94 | 0 | 24.83 | 0.015 | 0.104 | 52.2 | 15.8314
交流220kV | 2001-12-17 | 2013-12-10 | 11.989 | 18.2 | 267.5 | 1431.8 | 3.6 | 0.5 | 0.5 | 0 | 4.6 | 0 | 0 | 0 | 5.3525
交流220kV | 2001-01-17 | 2013-01-10 | 11.989 | 4.38 | 677.25 | 3718.52 | 25.75 | 1.28 | 6.66 | 0 | 33.69 | 0.028 | 0.093 | 53 | 5.4906
交流220kV | 1999-12-25 | 2011-12-19 | 11.9918 | 2.17 | 1042.23 | 3540.99 | 25.88 | 53.95 | 9.67 | 0 | 89.5 | 0.003 | 0.02 | 44 | 3.3975
交流220kV | 2000-03-31 | 2012-03-28 | 12 | 7.3 | 595.7 | 935.1 | 7.8 | 2 | 1.9 | 0.1 | 11.8 | 0.01 | 0.2 | 50.8 | 1.5697
交流220kV | 2000-04-28 | 2012-05-03 | 12.0219 | 28.97 | 1370.62 | 4166.12 | 15.7 | 26.12 | 3.06 | 0 | 44.88 | 0.005 | 0.001 | 55.5 | 3.0396
交流220kV | 2000-08-20 | 2012-08-27 | 12.0274 | 2.56 | 736.38 | 2831.19 | 14.59 | 1.21 | 15.31 | 0 | 31.11 | 0.011 | 0.002 | 62 | 3.8447
交流220kV | 2000-12-11 | 2012-12-21 | 12.0356 | 5.8 | 536.33 | 3637.02 | 6.52 | 4.35 | 1.74 | 0 | 12.61 | 0 | 0.255 | 46 | 6.7813
交流220kV | 2001-11-30 | 2013-12-10 | 12.0356 | 4.09 | 887.45 | 3526.1 | 13.22 | 1.29 | 1.8 | 0 | 16.31 | 0 | 0 | 0 | 3.9733
交流220kV | 2001-03-15 | 2013-03-27 | 12.0411 | 7.4 | 312.2 | 1282.4 | 14 | 3.9 | 7.7 | 0 | 25.6 | 0.01 | 0.002 | 57.7 | 4.1076
交流220kV | 2001-11-28 | 2013-12-19 | 12.0658 | 13.63 | 173.99 | 342.72 | 9.35 | 0.52 | 2.5 | 0 | 12.37 | 0 | 0 | 49.6 | 1.9698
交流220kV | 1999-09-27 | 2011-10-20 | 12.0712 | 30 | 1237 | 4569 | 22.3 | 8.8 | 4.6 | 0 | 35.7 | 0.05 | 0.178 | 61 | 3.6936
交流220kV | 1999-09-27 | 2011-10-20 | 12.0712 | 30 | 1237 | 4569 | 22.3 | 8.8 | 4.6 | 0 | 35.7 | 0.05 | 0.018 | 61.2 | 3.6936
交流220kV | 1999-09-27 | 2011-10-20 | 12.0712 | 30 | 183 | 1740 | 5.1 | 2.8 | 1.3 | 0 | 9.2 | 0.047 | 0.008 | 74.7 | 9.5082
交流220kV | 2001-03-24 | 2013-04-25 | 12.0959 | 4.9 | 762.6 | 2908.5 | 13 | 2.8 | 3 | 0 | 18.8 | 0.003 | 0.05 | 54.8 | 3.8139
交流220kV | 2001-10-09 | 2013-11-11 | 12.0986 | 9.91 | 228.91 | 2058.68 | 3.39 | 1.54 | 0.9 | 0 | 5.83 | 0.01 | 0.001 | 52.3 | 8.9934
交流220kV | 1999-05-25 | 2011-07-01 | 12.1096 | 3.03 | 1120.42 | 1679.95 | 21.48 | 3.38 | 4.35 | 0 | 29.21 | 0 | 0 | 0 | 1.4994
交流220kV | 1999-10-20 | 2011-11-30 | 12.1205 | 25.01 | 573.08 | 2109.14 | 22.15 | 27.46 | 5.4 | 0.18 | 55.19 | 0.002 | 0.03 | 48 | 3.6804
交流220kV | 2001-01-11 | 2013-02-23 | 12.126 | 2.04 | 115.05 | 299.23 | 1.35 | 0.72 | 1.74 | 0 | 3.81 | 0.021 | 0.19 | 58 | 2.6009
交流220kV | 1999-10-20 | 2011-12-12 | 12.1534 | 4.87 | 477.57 | 2125.63 | 21.28 | 26.04 | 6.8 | 0 | 54.12 | 0.003 | 0.02 | 51 | 4.4509
交流220kV | 1999-07-12 | 2011-09-20 | 12.2 | 5.72 | 1047.95 | 2359.01 | 83.84 | 148.07 | 35.4 | 0.15 | 267.46 | 0.011 | 0.04 | 49.7 | 2.2511
交流220kV | 2000-12-25 | 2013-03-11 | 12.2164 | 17.8 | 134 | 2285 | 5.2 | 3.2 | 3.1 | 0.17 | 11.67 | 0.01 | 0 | 50.5 | 17.0522
交流220kV | 2000-01-20 | 2012-04-09 | 12.2274 | 16 | 956 | 4238 | 13 | 0.8 | 2.6 | 0 | 16.4 | 0.005 | 0.001 | 49 | 4.4331
交流220kV | 2001-03-08 | 2013-06-03 | 12.2466 | 231.6 | 1047.3 | 4096.5 | 58.4 | 1.4 | 12.7 | 0 | 72.5 | 0.02 | 0 | 0 | 3.9115
交流220kV | 2000-12-16 | 2013-03-15 | 12.2521 | 6 | 520 | 2251 | 22.42 | 19.91 | 6.98 | 0.05 | 49.36 | 0.008 | 0.05 | 51.3 | 4.3288
交流220kV | 2001-08-19 | 2013-11-26 | 12.2795 | 3.19 | 454.04 | 4112.34 | 6.82 | 10.44 | 2.57 | 0.27 | 20.1 | 0.002 | 0.1 | 41 | 9.0572
交流220kV | 1997-03-06 | 2009-06-17 | 12.2904 | 4 | 339 | 1677 | 5.75 | 5.24 | 1.56 | 0 | 12.55 | 0.01 | 0.13 | 49 | 4.9469
交流220kV | 1999-12-25 | 2012-04-12 | 12.3068 | 4.79 | 1031.52 | 3538.73 | 25.04 | 52.76 | 9.36 | 0 | 87.16 | 0.001 | 0.1 | 41 | 3.4306
交流220kV | 2001-08-28 | 2013-12-17 | 12.3123 | 8 | 492 | 2240 | 5 | 1 | 0 | 0 | 6 | 0 | 0 | 0 | 4.5528
交流220kV | 2000-08-01 | 2012-11-21 | 12.3151 | 8.9 | 30 | 413 | 2.88 | 0.13 | 0.46 | 0 | 3.47 | 0.015 | 0 | 43.3 | 13.7667
交流220kV | 1999-02-11 | 2011-06-09 | 12.3315 | 15 | 1215 | 5468 | 24 | 3.7 | 4.7 | 0 | 32.4 | 0.007 | 0.003 | 48 | 4.5004
交流220kV | 1999-08-10 | 2011-12-08 | 12.337 | 10 | 1132 | 4724 | 11.4 | 4.6 | 2.8 | 0.1 | 18.9 | 0.013 | 0.001 | 46 | 4.1731
交流220kV | 2001-07-29 | 2013-12-10 | 12.3753 | 3.4 | 409.9 | 4714 | 15.3 | 2.9 | 3.7 | 0 | 21.9 | 0 | 0 | 0 | 11.5004
交流220kV | 1998-11-27 | 2011-04-12 | 12.3808 | 7 | 1260 | 5278 | 22.6 | 5.8 | 5.4 | 0 | 33.8 | 0.01 | 0.001 | 53 | 4.1889
交流220kV | 1998-12-23 | 2011-05-13 | 12.3945 | 3 | 312 | 1043 | 10.67 | 1.66 | 1.57 | 0.24 | 14.14 | 0.005 | 0.08 | 60 | 3.3429
交流220kV | 1999-07-14 | 2011-12-16 | 12.4329 | 9.5 | 261.7 | 0 | 10.5 | 1.7 | 3.7 | 0 | 15.9 | 0 | 0 | 0 | 0
交流220kV | 1999-10-20 | 2012-03-26 | 12.4411 | 6.76 | 505.75 | 2207.82 | 20.81 | 25.67 | 6.68 | 0 | 53.16 | 0.002 | 0.2 | 49 | 4.3654
交流220kV | 2001-09-10 | 2014-02-17 | 12.4466 | 7.8 | 418.5 | 4290.6 | 19.1 | 2.8 | 5.7 | 0 | 27.6 | 0.006 | 0.001 | 44.8 | 10.2523
交流220kV | 2001-05-07 | 2013-10-16 | 12.4521 | 13.72 | 398.28 | 3093.35 | 15.7 | 1.08 | 4.05 | 0 | 20.83 | 0.009 | 0.029 | 63 | 7.7668
交流220kV | 2001-06-25 | 2013-12-10 | 12.4685 | 5.8 | 1116 | 8398.3 | 26.9 | 5.3 | 5.8 | 0 | 38 | 0 | 0 | 0 | 7.5254
交流220kV | 1997-11-25 | 2010-05-12 | 12.4685 | 36.84 | 557.46 | 1230.99 | 14.01 | 3.65 | 4.95 | 0.21 | 22.82 | 0.007 | 0.618 | 61.4 | 2.2082
交流220kV | 2000-12-04 | 2013-05-23 | 12.474 | 13.9 | 502.4 | 2595.9 | 20.8 | 12.1 | 1.7 | 0 | 34.6 | 0 | 0 | 0 | 5.167
交流220kV | 1999-09-10 | 2012-03-07 | 12.4986 | 21.88 | 198.18 | 1700.16 | 4.78 | 0.52 | 1.12 | 0.09 | 6.51 | 0.018 | 0.151 | 50.8 | 8.5789
交流220kV | 1999-09-10 | 2012-03-07 | 12.4986 | 28.13 | 254.16 | 1819.62 | 35.37 | 48.57 | 5.64 | 0.67 | 90.25 | 0.02 | 0.142 | 48.9 | 7.1593
交流220kV | 1996-01-04 | 2008-07-02 | 12.5014 | 23 | 132.3 | 468.2 | 9.2 | 14.8 | 3.6 | 0 | 27.6 | 0.01 | 0.037 | 60.9 | 3.5389
交流220kV | 2001-04-21 | 2013-10-18 | 12.5014 | 5.08 | 742.07 | 2256.19 | 17.83 | 1.2 | 3.6 | 0 | 22.63 | 0.009 | 0.086 | 60.1 | 3.0404
交流220kV | 1999-06-17 | 2011-12-27 | 12.537 | 6 | 1203 | 1829 | 14 | 2 | 0 | 0 | 16 | 0 | 0 | 0 | 1.5204
交流220kV | 1998-12-15 | 2011-06-28 | 12.5425 | 10.8 | 946.2 | 5526.3 | 7 | 3.3 | 2 | 0 | 12.3 | 0.01 | 0.05 | 61 | 5.8405
交流220kV | 2000-12-11 | 2013-06-27 | 12.5507 | 4.5 | 385 | 3598 | 6.8 | 3.3 | 1.7 | 0 | 11.8 | 0 | 0 | 0 | 9.3455
交流220kV | 2001-06-04 | 2013-12-20 | 12.5534 | 15.51 | 1215.77 | 3081.35 | 31.46 | 26.72 | 8.55 | 0.22 | 66.95 | 0.009 | 0.005 | 56.7 | 2.5345
交流220kV | 1999-04-06 | 2011-10-26 | 12.5644 | 8 | 1169 | 5240 | 13.7 | 3.4 | 3.9 | 0 | 21 | 0.003 | 0.002 | 61 | 4.4825
交流220kV | 2001-06-01 | 2013-12-23 | 12.5699 | 8.16 | 429.91 | 2607.66 | 5.9 | 16.13 | 2.44 | 0 | 24.47 | 0.015 | 0.018 | 56 | 6.0656
交流220kV | 1999-05-25 | 2011-12-17 | 12.5726 | 4.4 | 775.84 | 1224.71 | 13.45 | 2.64 | 3.49 | 0 | 19.58 | 0 | 0 | 0 | 1.5786
交流220kV | 2000-11-01 | 2013-06-05 | 12.6 | 106.02 | 109.8 | 1278.7 | 19.12 | 0.7 | 0.24 | 0 | 20.06 | 0.02 | 0.076 | 59 | 11.6457
交流220kV | 1994-03-20 | 2006-10-25 | 12.6082 | 9.6 | 1985.9 | 15297.8 | 28.9 | 49.5 | 8.6 | 0.4 | 87.4 | 0.01 | 1.65 | 46 | 7.7032
交流220kV | 2000-08-01 | 2013-03-21 | 12.6438 | 19.9 | 30 | 338 | 2.7 | 0.26 | 0.51 | 0 | 3.47 | 0.016 | 0 | 49 | 11.2667
交流220kV | 1999-07-12 | 2012-02-29 | 12.6438 | 1.81 | 897.22 | 1660.64 | 81.97 | 155.13 | 34.92 | 0.13 | 272.15 | 0.012 | 0.078 | 50.2 | 1.8509
交流220kV | 2000-01-08 | 2012-08-27 | 12.6438 | 4.52 | 1445.84 | 9139.77 | 13.18 | 5.31 | 4.45 | 0 | 22.94 | 0.012 | 0.003 | 63 | 6.3214
交流220kV | 1999-08-08 | 2012-03-28 | 12.6466 | 7.6 | 524.5 | 1319 | 10.4 | 0 | 2.2 | 0 | 12.6 | 0 | 0 | 0 | 2.5148
交流220kV | 2000-08-23 | 2013-04-28 | 12.6877 | 67.3 | 482.83 | 678.9 | 38.73 | 6.21 | 8.04 | 0 | 52.98 | 0.07 | 0.001 | 59 | 1.4061
交流220kV | 2001-01-19 | 2013-10-16 | 12.7479 | 20.48 | 648.13 | 4048 | 18.2 | 1.27 | 4.3 | 0 | 23.77 | 0.008 | 0.031 | 62 | 6.2457
220 | 1999-07-09 | 2012-04-10 | 12.7644 | 5 | 130 | 54 | 1.5 | 0.3 | 0.1 | 0 | 1.9 | 0.008 | 0.057 | 50 | 0.41538
交流220kV | 2000-12-06 | 2013-09-10 | 12.7699 | 32.77 | 237.23 | 1620.2 | 17.72 | 1.44 | 10.99 | 0 | 30.15 | 0.016 | 0.15 | 53 | 6.8297
交流220kV | 2001-03-08 | 2013-12-12 | 12.7726 | 210.3 | 1122.6 | 3951.2 | 66.3 | 1.9 | 14.5 | 0 | 82.7 | 0 | 0 | 0 | 3.5197
交流220kV | 2000-05-26 | 2013-03-02 | 12.7753 | 19.89 | 237.41 | 1960.73 | 13.61 | 7.14 | 7.67 | 0 | 28.42 | 0.007 | 0.1 | 46 | 8.2588
交流220kV | 1999-12-13 | 2012-09-19 | 12.7781 | 6.2 | 817 | 7435.2 | 23.5 | 9 | 6.3 | 0 | 38.8 | 0.006 | 0.11 | 51.3 | 9.1006
交流220kV | 1999-12-13 | 2012-09-19 | 12.7781 | 6.9 | 954.5 | 7107.4 | 22.2 | 16.6 | 7 | 0 | 45.8 | 0.006 | 0.09 | 51 | 7.4462
交流220kV | 1999-06-17 | 2012-03-29 | 12.7918 | 6 | 1054 | 1993 | 14.4 | 1.4 | 2.1 | 0 | 17.9 | 0 | 0 | 0 | 1.8909
交流220kV | 1999-10-20 | 2012-08-06 | 12.8055 | 8.91 | 624.54 | 3120.52 | 23.99 | 28.47 | 7.58 | 0 | 60.04 | 0.003 | 0.2 | 43 | 4.9965
交流220kV | 1998-11-20 | 2011-09-10 | 12.8137 | 12.3 | 920.4 | 2944.3 | 13.5 | 6.3 | 5 | 0 | 24.8 | 0 | 0 | 0 | 3.1989
交流220kV | 1996-10-26 | 2009-08-21 | 12.8274 | 1.16 | 23.47 | 280.14 | 2.1 | 3.37 | 1.52 | 0 | 6.99 | 0.032 | 0.629 | 62 | 11.9361
交流220kV | 2001-05-23 | 2014-03-21 | 12.8356 | 9.33 | 406.9 | 3203.54 | 10.7 | 9.12 | 2.58 | 0.14 | 22.54 | 0.011 | 0.082 | 62 | 7.873
交流220kV | 1999-07-14 | 2012-05-16 | 12.8493 | 11.6 | 370.5 | 2336.3 | 16.2 | 2.8 | 4.8 | 0 | 23.8 | 0.006 | 0 | 52.9 | 6.3058
交流220kV | 2000-08-03 | 2013-06-25 | 12.9014 | 3.78 | 1080.18 | 4736.81 | 18.12 | 4.33 | 4.6 | 0 | 27.05 | 0.014 | 0.122 | 55.6 | 4.3852
交流220kV | 1998-11-27 | 2011-10-25 | 12.9178 | 5 | 1134 | 4562 | 22 | 5.6 | 5.6 | 0 | 33.2 | 0.01 | 0.001 | 53 | 4.0229
交流220kV | 2000-03-31 | 2013-03-04 | 12.9342 | 5.3 | 565.6 | 816.5 | 7.5 | 2.1 | 1.4 | 0.1 | 11.1 | 0.01 | 0.32 | 58.8 | 1.4436
交流220kV | 1998-06-05 | 2011-05-11 | 12.9397 | 7.38 | 764.14 | 2118.02 | 23.68 | 7.17 | 6.55 | 0 | 37.4 | 0.01 | 0.001 | 57 | 2.7718
交流220kV | 1998-12-28 | 2011-12-14 | 12.9699 | 5.02 | 867.62 | 2895.07 | 22.46 | 11.24 | 6.56 | 0 | 40.26 | 0 | 0 | 0 | 3.3368
交流220kV | 1999-06-17 | 2012-06-05 | 12.9781 | 6 | 1113 | 2240 | 12 | 2 | 2 | 0 | 16 | 0.059 | 0.1 | 52 | 2.0126
交流220kV | 1999-12-25 | 2012-12-13 | 12.9781 | 5.6 | 1021.74 | 3568.84 | 26.22 | 56.65 | 9.36 | 0 | 92.23 | 0.001 | 0.2 | 42 | 3.4929
交流220kV | 2000-12-11 | 2013-12-02 | 12.9836 | 5.5 | 622 | 5566 | 13 | 5.9 | 3.4 | 0 | 22.3 | 0.04 | 0.34 | 48 | 8.9486
交流220kV | 1998-07-19 | 2011-07-12 | 12.989 | 1.7 | 174 | 1385 | 5.1 | 0.8 | 1.3 | 0 | 7.2 | 0 | 0 | 0 | 7.9598
交流220kV | 1999-12-13 | 2012-12-20 | 13.0301 | 4.8 | 657.6 | 6775.3 | 20.9 | 8.4 | 5.9 | 0 | 35.2 | 0.006 | 0.11 | 51.3 | 10.3031
交流220kV | 1998-12-15 | 2011-12-27 | 13.0411 | 5 | 943 | 1856 | 15 | 6 | 3 | 0.43 | 24.43 | 0 | 0 | 0 | 1.9682
交流220kV | 2000-12-04 | 2013-12-17 | 13.0438 | 11.5 | 536.8 | 2130.5 | 21.7 | 8.5 | 6.4 | 0 | 36.6 | 0.07 | 0.8 | 47 | 3.9689
交流220kV | 1999-05-25 | 2012-07-06 | 13.126 | 24.6 | 1126.7 | 1772.5 | 26.13 | 4.51 | 7.82 | 0 | 38.46 | 0 | 0 | 0 | 1.5732
交流220kV | 1999-05-25 | 2012-07-06 | 13.126 | 5.03 | 851.33 | 1415.5 | 20.08 | 3.54 | 5.98 | 0 | 29.6 | 0 | 0 | 0 | 1.6627
交流220kV | 1999-05-25 | 2012-07-06 | 13.126 | 12.58 | 630.53 | 1122 | 15.23 | 2.85 | 3.6 | 0 | 21.68 | 0 | 0 | 0 | 1.7795
交流220kV | 1998-12-25 | 2012-02-22 | 13.1699 | 14.81 | 445.95 | 5068.89 | 21.64 | 6.02 | 4.27 | 0 | 31.93 | 0.011 | 0.045 | 64.8 | 11.3665
交流220kV | 2000-08-20 | 2013-10-18 | 13.1699 | 2.36 | 1162.62 | 2234.94 | 13.62 | 7.95 | 2.47 | 0 | 24.04 | 0.006 | 1.236 | 49 | 1.9223
交流220kV | 2000-06-01 | 2013-08-19 | 13.2247 | 10.01 | 1095.43 | 2513.13 | 13.68 | 1.41 | 2.4 | 0 | 17.49 | 0.003 | 0.001 | 54 | 2.2942
交流220kV | 1998-07-05 | 2011-09-29 | 13.2438 | 4 | 573 | 3610 | 9.7 | 1.5 | 3.6 | 0 | 14.8 | 0.053 | 0.003 | 54.4 | 6.3002
交流220kV | 1996-01-04 | 2009-04-03 | 13.2548 | 5.4 | 272.5 | 1481.1 | 9.4 | 17.3 | 3.9 | 0 | 30.6 | 0.01 | 0.029 | 59.1 | 5.4352
交流220kV | 1996-01-04 | 2009-04-03 | 13.2548 | 5.38 | 272.45 | 1481.11 | 9.4 | 17.26 | 3.93 | 0 | 30.59 | 0.014 | 0.029 | 59.1 | 5.4363
交流220kV | 1998-12-28 | 2012-03-28 | 13.2575 | 5.68 | 817.08 | 3559.03 | 26.17 | 17.27 | 7.69 | 0 | 51.13 | 0 | 0 | 0 | 4.3558
交流220kV | 1997-02-24 | 2010-06-02 | 13.2767 | 4.35 | 478.21 | 1686.56 | 8.95 | 8.25 | 7.21 | 0.11 | 24.52 | 0.005 | 0.414 | 67 | 3.5268
交流220kV | 2000-12-16 | 2014-03-25 | 13.2795 | 9 | 575 | 2162 | 22.94 | 19.64 | 6.94 | 0.06 | 49.58 | 0.001 | 0.05 | 50 | 3.76
交流220kV | 1999-02-11 | 2012-05-22 | 13.2849 | 12 | 996 | 4335 | 23 | 6.7 | 9 | 0 | 38.7 | 0.013 | 0.002 | 44 | 4.3524
交流220kV | 1998-06-28 | 2011-10-10 | 13.2932 | 9 | 1015 | 4555 | 15.9 | 22.9 | 4.5 | 0 | 43.3 | 0.048 | 0.002 | 57 | 4.4877
交流220kV | 1998-10-29 | 2012-02-17 | 13.3123 | 4.47 | 457.43 | 3506.55 | 15.27 | 9 | 6.32 | 0 | 30.59 | 0.005 | 0.1 | 56 | 7.6658
交流220kV | 1998-12-10 | 2012-04-06 | 13.3315 | 3.12 | 852.62 | 5273.88 | 15.83 | 6.33 | 2.89 | 0 | 25.05 | 0.021 | 0.21 | 60 | 6.1855
交流220kV | 1998-08-23 | 2011-12-21 | 13.337 | 4.02 | 380.12 | 1028.47 | 5.6 | 0.23 | 0.55 | 0 | 6.38 | 0 | 0.004 | 53 | 2.7056
交流220kV | 1999-11-18 | 2013-03-22 | 13.3507 | 1.06 | 100.04 | 2345.68 | 9.8 | 2.36 | 7.2 | 0 | 19.36 | 0.002 | 0.15 | 60 | 23.4474
交流220kV | 1999-11-18 | 2013-03-25 | 13.3589 | 11.06 | 400.04 | 3597.75 | 19.8 | 3.36 | 7.2 | 0 | 30.36 | 0.002 | 0.15 | 60 | 8.9935
交流220kV | 1990-11-02 | 2004-03-10 | 13.3616 | 31.5 | 1244.8 | 6275.9 | 46.5 | 82.6 | 14.6 | 0 | 143.7 | 0.004 | 0.224 | 50 | 5.0417
交流220kV | 1998-11-20 | 2012-03-29 | 13.3644 | 12.96 | 1137.72 | 3019.96 | 14.54 | 6.28 | 5.91 | 0 | 26.73 | 0 | 0 | 0 | 2.6544
交流220kV | 1998-12-23 | 2012-05-07 | 13.3808 | 4 | 327 | 1295 | 12.6 | 2.06 | 2.8 | 0.23 | 17.69 | 0.005 | 0.08 | 60 | 3.9602
交流220kV | 2000-11-04 | 2014-03-20 | 13.3808 | 9.24 | 150.69 | 1113.65 | 9.32 | 1.22 | 2.01 | 0 | 12.55 | 0.009 | 0.094 | 60 | 7.3903
交流220kV | 1998-11-23 | 2012-04-13 | 13.3973 | 13 | 670 | 4289 | 11.4 | 1.2 | 2.8 | 0 | 15.4 | 0.008 | 0.002 | 58 | 6.4015
交流220kV | 1999-11-18 | 2013-04-15 | 13.4164 | 2.92 | 729.55 | 8359.98 | 10.95 | 40.36 | 5.23 | 0 | 56.54 | 0.003 | 0.16 | 60 | 11.4591
交流220kV | 1999-07-14 | 2012-12-11 | 13.4219 | 10.5 | 340.6 | 2044.8 | 13.2 | 2.3 | 4.1 | 0 | 19.6 | 0 | 0 | 0 | 6.0035
交流220kV | 1998-01-18 | 2011-06-18 | 13.4219 | 20.69 | 1121.39 | 6336.11 | 20.81 | 5.32 | 3.89 | 0.21 | 30.23 | 0.003 | 0.02 | 48 | 5.6502
交流220kV | 1998-12-15 | 2012-05-17 | 13.4301 | 5 | 827 | 2186 | 15 | 6 | 3 | 0.5 | 24.5 | 0.043 | 0 | 50 | 2.6433
交流220kV | 1999-12-25 | 2013-05-30 | 13.4384 | 6.39 | 401.8 | 2502.6 | 22.26 | 43.8 | 6.38 | 0 | 72.44 | 0.003 | 0.25 | 51 | 6.2285
交流220kV | 1998-07-19 | 2011-12-27 | 13.4493 | 2 | 322 | 1772 | 6 | 3 | 4 | 0 | 13 | 0 | 0 | 0 | 5.5031
交流220kV | 1998-07-01 | 2011-12-16 | 13.4685 | 5.3 | 687 | 2351 | 10.7 | 2 | 2.9 | 0 | 15.6 | 0 | 0 | 0 | 3.4221
交流220kV | 1999-06-17 | 2012-12-05 | 13.4795 | 7 | 1133 | 2016 | 14 | 2 | 2 | 0 | 18 | 0 | 0 | 0 | 1.7793
交流220kV | 1999-10-20 | 2013-04-10 | 13.4822 | 5.98 | 456.41 | 2664.66 | 17.95 | 20.69 | 4.98 | 0 | 43.62 | 0.002 | 0.1 | 40 | 5.8383
交流220kV | 1999-11-18 | 2013-05-10 | 13.4849 | 1.26 | 33.1 | 959.52 | 1.28 | 2.11 | 0.24 | 0.37 | 4 | 0.003 | 0.16 | 60 | 28.9885
交流220kV | 2000-01-14 | 2013-07-15 | 13.5096 | 8.99 | 856.2 | 3876.7 | 8.9 | 7.7 | 0 | 0 | 16.6 | 0.034 | 0 | 51 | 4.5278
交流220kV | 2000-01-12 | 2013-07-15 | 13.5151 | 21.1 | 698.5 | 3292.4 | 14.2 | 1.4 | 0 | 0 | 15.6 | 0.032 | 0 | 52 | 4.7135
交流220kV | 1999-10-16 | 2013-05-13 | 13.5836 | 4.61 | 480.41 | 1918.37 | 9.22 | 5.85 | 4.92 | 0 | 19.99 | 0.011 | 0.372 | 57 | 3.9932
交流220kV | 1998-12-15 | 2012-07-18 | 13.6 | 4.9 | 1446.7 | 5900.8 | 7.3 | 4.1 | 2.2 | 0 | 13.6 | 0.01 | 0.02 | 60 | 4.0788
交流220kV | 1999-05-25 | 2012-12-31 | 13.6137 | 3.08 | 829.88 | 1300.6 | 12.49 | 3.04 | 3.52 | 0 | 19.05 | 0 | 0 | 0 | 1.5672
交流220kV | 1999-05-25 | 2012-12-31 | 13.6137 | 2.22 | 571.49 | 914.36 | 8.77 | 2.24 | 2.64 | 0 | 13.65 | 0 | 0 | 0 | 1.6
交流220kV | 1999-05-25 | 2012-12-31 | 13.6137 | 3.18 | 836.18 | 1289.44 | 12.23 | 2.96 | 3.47 | 0 | 18.66 | 0 | 0 | 0 | 1.5421
交流220kV | 2000-08-01 | 2014-03-11 | 13.6164 | 21.5 | 50.5 | 524 | 6.16 | 0 | 0.98 | 0 | 7.14 | 0.016 | 0 | 50 | 10.3762
交流220kV | 2000-05-17 | 2014-01-09 | 13.6575 | 7 | 1222 | 4214 | 15.5 | 4.4 | 5.4 | 0 | 25.3 | 0.02 | 0.1 | 59 | 3.4484
220 | 2000-03-31 | 2013-12-03 | 13.6849 | 21.6 | 844.16 | 7844.82 | 18.74 | 2.17 | 4.04 | 0.3 | 25.25 | 0.007 | 0.067 | 71.6 | 9.293
交流220kV | 1998-01-18 | 2011-09-22 | 13.6849 | 20.66 | 1121.98 | 6334.23 | 20.12 | 5.03 | 3.69 | 0.19 | 29.03 | 0.003 | 0.02 | 49 | 5.6456
交流220kV | 1997-10-25 | 2011-07-01 | 13.6904 | 9.09 | 550.86 | 14480.19 | 10.58 | 112.23 | 5.95 | 4.09 | 132.85 | 0 | 0 | 0 | 26.2865
220 | 1999-07-09 | 2013-03-22 | 13.7123 | 10 | 366 | 539 | 10.5 | 3.9 | 3.1 | 0 | 17.5 | 0.007 | 0.001 | 50 | 1.4727
交流220kV | 1999-09-27 | 2013-06-18 | 13.7342 | 27 | 56 | 2071 | 8.93 | 3.45 | 2.83 | 0 | 15.21 | 0.026 | 0.033 | 67 | 36.9821
交流220kV | 1997-12-20 | 2011-09-16 | 13.7479 | 17 | 877 | 2231 | 14.2 | 3.6 | 2.8 | 0 | 20.6 | 0.058 | 0.036 | 75 | 2.5439
220 | 1998-01-14 | 2011-10-13 | 13.7534 | 18.81 | 780 | 1286.35 | 27.8 | 0.5 | 13.82 | 0 | 42.12 | 0.003 | 0.001 | 60 | 1.6492
交流220kV | 2000-07-03 | 2014-04-01 | 13.7534 | 5.44 | 583.09 | 2052.16 | 22.13 | 3.79 | 4.45 | 0 | 30.37 | 0.008 | 0.001 | 59.7 | 3.5195
交流220kV | 1997-10-03 | 2011-07-06 | 13.7644 | 5.48 | 1089.95 | 4842.2 | 15.9 | 15.59 | 2.73 | 1.32 | 35.54 | 0 | 0 | 0 | 4.4426
交流220kV | 2000-05-26 | 2014-03-02 | 13.7753 | 19.15 | 280.44 | 2317.29 | 12.43 | 7.19 | 7.46 | 0 | 27.08 | 0.007 | 0.05 | 42 | 8.2631
交流220kV | 2000-01-20 | 2013-10-30 | 13.7863 | 1.4 | 19.3 | 373.4 | 0.6 | 0.3 | 0.2 | 0 | 1.1 | 0 | 0 | 0 | 19.3472
交流220kV | 2000-01-20 | 2013-11-05 | 13.8027 | 1.2 | 23.7 | 431.5 | 0.7 | 0.3 | 0.3 | 0 | 1.3 | 0 | 0 | 0 | 18.2068
交流220kV | 1998-08-23 | 2012-06-21 | 13.8384 | 5.77 | 390.05 | 2334.72 | 6.28 | 1.85 | 0.31 | 0 | 8.44 | 0 | 0 | 0 | 5.9857
交流220kV | 1999-09-27 | 2013-08-01 | 13.8548 | 29 | 56 | 2083 | 8.37 | 3.83 | 3.23 | 0 | 15.43 | 0.022 | 0.171 | 53 | 37.1964
交流220kV | 1999-09-27 | 2013-08-01 | 13.8548 | 17 | 833 | 4643 | 24.48 | 8.74 | 6.91 | 0 | 40.13 | 0.026 | 0.759 | 60 | 5.5738
220 | 1998-05-01 | 2012-03-07 | 13.8603 | 10.23 | 895.46 | 9365.78 | 24.28 | 4.95 | 7.52 | 0 | 36.75 | 0.017 | 0.355 | 57 | 10.4592
交流220kV | 1998-12-28 | 2012-11-05 | 13.8658 | 7.85 | 967.27 | 3797.18 | 33.48 | 17.63 | 13.16 | 0 | 64.27 | 0 | 0.002 | 57.2 | 3.9257
交流220kV | 1998-07-19 | 2012-05-31 | 13.8767 | 3 | 362 | 2481 | 8.5 | 2.5 | 2.5 | 0 | 13.5 | 0.02 | 0.493 | 50 | 6.8536
220 | 1999-12-28 | 2013-11-12 | 13.8849 | 4.32 | 1439.67 | 4167.43 | 33.33 | 25 | 7.44 | 0 | 65.77 | 0.033 | 0.149 | 56 | 2.8947
交流220kV | 1999-07-14 | 2013-06-06 | 13.9068 | 10.8 | 297.6 | 2846.9 | 13.6 | 2.9 | 4.9 | 0 | 21.4 | 0.011 | 0 | 65.9 | 9.5662
交流220kV | 1999-12-25 | 2013-11-21 | 13.9178 | 1.75 | 939.02 | 3751.56 | 23.91 | 53.96 | 5.75 | 0 | 83.62 | 0.003 | 0.25 | 51 | 3.9952
交流220kV | 1998-01-18 | 2011-12-19 | 13.926 | 10.85 | 1345.58 | 7170.55 | 21.15 | 6.54 | 5.08 | 0.24 | 33.01 | 0.003 | 0.01 | 45 | 5.329
交流220kV | 1998-11-12 | 2012-10-12 | 13.926 | 14.06 | 591.3 | 2639.53 | 85.53 | 1.5 | 15.67 | 0 | 102.7 | 0.016 | 0.12 | 44 | 4.4639
交流220kV | 2000-01-07 | 2013-12-10 | 13.9342 | 4 | 614.28 | 1954 | 11.84 | 2.94 | 1.78 | 0 | 16.56 | 0 | 0 | 0 | 3.181
交流220kV | 2000-01-14 | 2013-12-17 | 13.9342 | 16.5 | 1271.4 | 4962.4 | 12.9 | 8.7 | 1.6 | 0 | 23.2 | 0.06 | 1.4 | 44 | 3.9031
交流220kV | 2000-04-28 | 2014-04-01 | 13.9342 | 25.46 | 1407.36 | 4878.93 | 19.37 | 27.13 | 3.5 | 0 | 50 | 0.007 | 0.001 | 59 | 3.4667
交流220kV | 1999-08-08 | 2013-07-12 | 13.937 | 16.3 | 910.5 | 3063.4 | 15.4 | 0 | 2.9 | 0 | 18.3 | 0.035 | 2.1 | 52 | 3.3645
交流220kV | 2000-01-12 | 2013-12-17 | 13.9397 | 18.9 | 628.1 | 2563.9 | 13.4 | 1 | 0.2 | 0 | 14.6 | 0.05 | 1.6 | 46 | 4.082
交流220kV | 1999-08-10 | 2013-07-15 | 13.9397 | 11.1 | 1192.9 | 6453.9 | 9.5 | 3.5 | 0 | 0 | 13 | 0.028 | 0 | 52 | 5.4103
交流220kV | 1998-01-09 | 2011-12-20 | 13.9534 | 9.2 | 590.6 | 4170 | 10 | 4.4 | 2.6 | 0 | 17 | 0 | 0 | 0 | 7.0606
交流220kV | 1999-08-10 | 2013-07-22 | 13.9589 | 6 | 115 | 4869 | 13.66 | 4.78 | 5.22 | 0.07 | 23.73 | 0.025 | 0.006 | 42 | 42.3391
交流220kV | 1998-07-19 | 2012-07-02 | 13.9644 | 3 | 306 | 2070 | 9 | 2 | 3 | 0 | 14 | 0 | 0 | 0 | 6.7647
交流220kV | 2000-03-31 | 2014-03-17 | 13.9699 | 44.2 | 537.3 | 1014.2 | 7.7 | 2.5 | 1.4 | 0 | 11.6 | 0.003 | 0.2 | 60.4 | 1.8876
交流220kV | 1998-07-19 | 2012-07-05 | 13.9726 | 3 | 311 | 2291 | 9 | 2 | 3 | 0 | 14 | 0 | 0 | 0 | 7.3666
交流220kV | 1998-12-15 | 2012-12-05 | 13.9836 | 5 | 843 | 1871 | 10 | 4 | 2 | 0 | 16 | 0 | 0 | 0 | 2.2195
交流220kV | 1999-05-25 | 2013-06-09 | 14.0521 | 3 | 851.26 | 1517.9 | 21.94 | 5.01 | 13 | 0 | 39.95 | 0 | 0 | 0 | 1.7831
交流220kV | 1998-07-19 | 2012-08-03 | 14.0521 | 3 | 292 | 2135 | 8 | 2 | 2 | 0 | 12 | 0 | 0 | 0 | 7.3116
交流220kV | 1999-05-25 | 2013-06-09 | 14.0521 | 20.59 | 756.09 | 1339.6 | 21.13 | 4.39 | 6.68 | 0 | 32.2 | 0 | 0 | 0 | 1.7717
交流220kV | 1999-06-17 | 2013-07-02 | 14.0521 | 9 | 1235 | 2535 | 15 | 2 | 5 | 0 | 22 | 0.055 | 0.06 | 54 | 2.0526
交流220kV | 1999-05-25 | 2013-06-09 | 14.0521 | 2.2 | 809.05 | 1463.9 | 16.55 | 3.83 | 4.12 | 0 | 24.5 | 0 | 0 | 0 | 1.8094
交流220kV | 1997-12-26 | 2012-01-13 | 14.0575 | 18 | 71 | 3842 | 25.3 | 31.6 | 10.9 | 0 | 67.8 | 0.034 | 0.46 | 46 | 54.1127
交流220kV | 1997-10-25 | 2011-11-25 | 14.0932 | 18.39 | 363.6 | 11639.61 | 7.44 | 97.27 | 4.96 | 3.59 | 113.26 | 0 | 0 | 0 | 32.0121
交流220kV | 1997-11-20 | 2011-12-21 | 14.0932 | 2.55 | 231.15 | 1671.09 | 3.35 | 1.29 | 0 | 0 | 4.64 | 0 | 0 | 0 | 7.2295
交流220kV | 1999-10-20 | 2013-11-27 | 14.1151 | 4.79 | 726.15 | 6229.19 | 26.72 | 21.38 | 6.51 | 0 | 54.61 | 0.003 | 0.25 | 51 | 8.5784
交流220kV | 1999-01-27 | 2013-03-06 | 14.1151 | 7.12 | 447.02 | 3514.23 | 4.07 | 8.64 | 2.15 | 0 | 14.86 | 0.003 | 0.003 | 52 | 7.8615
交流220kV | 1998-06-05 | 2012-07-18 | 14.1288 | 16.57 | 938.09 | 3087.27 | 27.93 | 7.05 | 8.09 | 0 | 43.07 | 0.005 | 0.001 | 59 | 3.291
交流220kV | 1999-10-28 | 2013-12-13 | 14.137 | 3 | 236.4 | 1775.7 | 6.6 | 1.5 | 1 | 0 | 9.1 | 0 | 0 | 0 | 7.5114
交流220kV | 1997-10-25 | 2011-12-17 | 14.1534 | 10.11 | 335.98 | 11422.17 | 6.74 | 91.75 | 5.09 | 3.09 | 106.67 | 0 | 0 | 0 | 33.9966
交流220kV | 1997-04-28 | 2011-07-07 | 14.2 | 3.3 | 436.3 | 9462.1 | 20 | 3.6 | 0 | 0 | 23.6 | 0 | 0 | 0 | 21.6871
交流220kV | 1998-12-22 | 2013-03-02 | 14.2027 | 9.21 | 190 | 1967.07 | 13.27 | 10.83 | 7.79 | 0 | 31.89 | 0.005 | 0.12 | 46.8 | 10.353
交流220kV | 1998-07-05 | 2012-09-28 | 14.2438 | 6 | 697 | 4747 | 14.1 | 2 | 4 | 0 | 20.1 | 0.042 | 0.03 | 55 | 6.8106
交流220kV | 1997-12-26 | 2012-04-01 | 14.274 | 3.46 | 185.21 | 299.86 | 4.1 | 0.69 | 1.23 | 0 | 6.02 | 0.021 | 0.988 | 57 | 1.619
交流220kV | 1998-01-18 | 2012-04-25 | 14.2767 | 66.85 | 9456.68 | 47635.21 | 65.9 | 21.46 | 16.84 | 0.91 | 105.11 | 0.001 | 0.1 | 42 | 5.0372
220 | 1996-12-27 | 2011-04-18 | 14.3151 | 8.11 | 649.6 | 4167.04 | 25.56 | 12.23 | 13.88 | 0.13 | 51.8 | 0.001 | 0.028 | 55 | 6.4148
交流220kV | 1998-08-23 | 2012-12-20 | 14.337 | 5.35 | 461.12 | 2104.15 | 5.27 | 1.95 | 0.83 | 0.24 | 8.29 | 0 | 0.313 | 47 | 4.5631
交流220kV | 1998-12-10 | 2013-04-08 | 14.337 | 3.84 | 322.51 | 2301.64 | 2.42 | 5.06 | 0.33 | 0 | 7.81 | 0.019 | 0.17 | 45 | 7.1366
交流220kV | 1998-11-27 | 2013-03-28 | 14.3425 | 4 | 1217 | 4733 | 22.6 | 5.9 | 5.8 | 0 | 34.3 | 0.015 | 0.1 | 57 | 3.8891
交流220kV | 1999-08-10 | 2013-12-17 | 14.3644 | 9.2 | 924.4 | 4496 | 8.3 | 2.9 | 0.3 | 0 | 11.5 | 0.05 | 1.08 | 44 | 4.8637
交流220kV | 1999-08-08 | 2013-12-17 | 14.3699 | 14.9 | 837.9 | 2545.1 | 14.9 | 0.9 | 0.5 | 0 | 16.3 | 0.05 | 1.5 | 46 | 3.0375
交流220kV | 1998-11-12 | 2013-03-28 | 14.3836 | 13.16 | 626.46 | 2685.39 | 87.73 | 1.98 | 14.96 | 0 | 104.67 | 0.017 | 0.32 | 57 | 4.2866
交流220kV | 1997-10-25 | 2012-03-12 | 14.389 | 4.25 | 263.64 | 9757.2 | 6.24 | 88.35 | 4.63 | 3.22 | 102.44 | 0 | 0 | 0 | 37.0096
交流220kV | 1998-07-19 | 2012-12-05 | 14.3918 | 4 | 349 | 2330 | 10 | 2 | 3 | 0 | 15 | 0 | 0 | 0 | 6.6762
交流220kV | 1999-07-14 | 2013-12-04 | 14.4027 | 9.3 | 340.7 | 2334.3 | 14.2 | 3.2 | 4.9 | 0 | 22.3 | 0 | 0 | 0 | 6.8515
220 | 1998-11-28 | 2013-04-26 | 14.4192 | 4.85 | 596.04 | 6733.68 | 5.41 | 42.66 | 3.64 | 0 | 51.71 | 0.025 | 0.066 | 58.9 | 11.2974
交流220kV | 1998-07-01 | 2012-12-05 | 14.4411 | 7.5 | 948.4 | 3796.9 | 15.6 | 3.8 | 3.2 | 0 | 22.6 | 0 | 0 | 0 | 4.0035
220 | 1997-10-29 | 2012-04-10 | 14.4575 | 2 | 174 | 40 | 4.8 | 0.2 | 0.4 | 0 | 5.4 | 0.007 | 0.069 | 52 | 0.22989
交流220kV | 1998-11-23 | 2013-05-09 | 14.4685 | 5 | 151 | 2172 | 7.8 | 0 | 0 | 0 | 7.8 | 0.002 | 0.005 | 58 | 14.3841
交流220kV | 1997-12-05 | 2012-06-02 | 14.5014 | 15.2 | 510.3 | 5211.6 | 13.3 | 4.5 | 3.9 | 0 | 21.7 | 0.012 | 0.208 | 54 | 10.2128
交流220kV | 1999-09-27 | 2014-03-26 | 14.5041 | 3.89 | 309.62 | 2309.01 | 5.42 | 8.99 | 1.97 | 0.05 | 16.43 | 0.003 | 0.001 | 59.2 | 7.4576
交流220kV | 1999-06-17 | 2013-12-17 | 14.5123 | 6 | 940 | 1689 | 10 | 2 | 2 | 0 | 14 | 0 | 0 | 0 | 1.7968
交流220kV | 1997-06-01 | 2011-12-08 | 14.5288 | 32 | 444 | 2734 | 18.7 | 4.3 | 2.6 | 0 | 25.6 | 0.013 | 0.001 | 42 | 6.1577
交流220kV | 1999-08-10 | 2014-02-26 | 14.5589 | 6 | 116 | 4118 | 13.77 | 4.65 | 5.28 | 0.06 | 23.76 | 0.026 | 0.618 | 45 | 35.5
交流220kV | 1998-12-15 | 2013-07-05 | 14.5644 | 5 | 946 | 2451 | 15 | 6 | 3 | 0.4 | 24.4 | 0.097 | 1 | 50 | 2.5909
交流220kV | 1997-10-14 | 2012-05-04 | 14.5644 | 22 | 323 | 1436 | 6.7 | 1.1 | 0 | 0 | 7.8 | 0.017 | 0.002 | 49 | 4.4458
交流220kV | 1997-11-20 | 2012-06-24 | 14.6027 | 5.74 | 253.87 | 5963.32 | 5.65 | 0.56 | 0.23 | 0 | 6.44 | 0.016 | 0.328 | 43 | 23.4897
交流220kV | 1999-05-25 | 2013-12-31 | 14.6137 | 5.17 | 892.64 | 1303.17 | 15.75 | 4.68 | 4.27 | 0 | 24.7 | 0 | 0 | 0 | 1.4599
交流220kV | 1999-05-25 | 2013-12-31 | 14.6137 | 4.25 | 836.86 | 1244.33 | 14.93 | 4.63 | 4.14 | 0 | 23.7 | 0 | 0 | 0 | 1.4869
交流220kV | 1999-05-25 | 2013-12-31 | 14.6137 | 3.51 | 811.68 | 1202.39 | 15.09 | 4.34 | 4.11 | 0 | 23.54 | 0 | 0 | 0 | 1.4814
交流220kV | 1998-11-20 | 2013-07-04 | 14.6301 | 12.8 | 1102.9 | 3997.7 | 15.5 | 6.6 | 5.6 | 0 | 27.7 | 0.036 | 0 | 52 | 3.6247
交流220kV | 1990-11-02 | 2005-06-24 | 14.6521 | 19.05 | 877.71 | 6929.48 | 39.63 | 71.45 | 17.59 | 0.5 | 129.17 | 0.005 | 0.141 | 50 | 7.895
交流220kV | 1997-05-03 | 2011-12-27 | 14.6603 | 9 | 1199 | 2471 | 31 | 17 | 10 | 0 | 58 | 0 | 0 | 0 | 2.0609
交流220kV | 1997-04-28 | 2011-12-22 | 14.6603 | 2.47 | 401.21 | 5019.29 | 19.77 | 4.71 | 3.04 | 0 | 27.52 | 0 | 0 | 35.1 | 12.5104
交流220kV | 1995-08-15 | 2010-04-14 | 14.674 | 3.46 | 1148.39 | 3725.13 | 10.5 | 5.08 | 4 | 0 | 19.58 | 0.013 | 0.074 | 50 | 3.2438
交流220kV | 1997-10-25 | 2012-07-06 | 14.7068 | 13.1 | 430.33 | 14080.28 | 8.09 | 130.9 | 6.63 | 3.43 | 149.05 | 0 | 0 | 0 | 32.7197
交流220kV | 1997-07-17 | 2012-03-29 | 14.7096 | 35.35 | 786.5 | 3284.21 | 21.13 | 8.24 | 4.05 | 0 | 33.42 | 0.009 | 0.086 | 57 | 4.1757
220 | 1999-07-09 | 2014-03-30 | 14.7342 | 20 | 593 | 523 | 13.2 | 0 | 0 | 0 | 13.2 | 0.007 | 0.001 | 48 | 0.88196
交流220kV | 1997-10-03 | 2012-07-17 | 14.7973 | 8.73 | 891.53 | 3798.72 | 16.32 | 20.05 | 3.23 | 1.08 | 40.68 | 0.007 | 0.175 | 42.9 | 4.2609
交流220kV | 1996-06-22 | 2011-04-12 | 14.8137 | 9 | 608.7 | 6583.3 | 18.3 | 2.5 | 4.7 | 0.1 | 25.6 | 0.006 | 0.35 | 56.3 | 10.8153
交流220kV | 1998-08-23 | 2013-06-26 | 14.8521 | 6.3 | 600 | 3100 | 6.7 | 2.6 | 1.1 | 0 | 10.4 | 0 | 0 | 0 | 5.1667
220 | 1998-05-01 | 2013-03-15 | 14.8822 | 6.45 | 833.64 | 8996.88 | 22.58 | 3.78 | 6.28 | 0 | 32.64 | 0.016 | 0.072 | 57 | 10.7923
交流220kV | 1994-03-20 | 2009-02-10 | 14.9068 | 2.2 | 128 | 1270.4 | 2.4 | 21.4 | 0 | 0 | 23.8 | 0.02 | 0.211 | 52 | 9.925
交流220kV | 1998-01-18 | 2012-12-14 | 14.9151 | 17.85 | 1192.78 | 8801.41 | 22.38 | 7.79 | 5.6 | 0 | 35.77 | 0.001 | 0.1 | 42 | 7.3789
交流220kV | 1998-01-09 | 2012-12-05 | 14.9151 | 3.7 | 517.8 | 3422.2 | 9.4 | 5 | 2.8 | 0 | 17.2 | 0 | 0 | 0 | 6.6091
交流220kV | 1998-07-01 | 2013-05-28 | 14.9178 | 7.6 | 1003.7 | 4069.5 | 17.6 | 3.8 | 3.7 | 0 | 25.1 | 0.005 | 0 | 59 | 4.0545
交流220kV | 1997-04-28 | 2012-03-27 | 14.9233 | 4.49 | 487.5 | 5817.07 | 19.12 | 4.39 | 3.1 | 0 | 26.61 | 0 | 0 | 0 | 11.9325
交流220kV | 1998-07-19 | 2013-07-03 | 14.9671 | 1 | 318 | 2243 | 11 | 2 | 3 | 0 | 16 | 0.029 | 0.413 | 52 | 7.0535
交流220kV | 1998-03-18 | 2013-03-06 | 14.9781 | 10 | 1014 | 6393 | 15.35 | 3.19 | 5.38 | 0 | 23.92 | 0.018 | 0.046 | 53.6 | 6.3047
交流220kV | 1998-03-18 | 2013-03-06 | 14.9781 | 2 | 105 | 1449 | 1.31 | 0.44 | 0.35 | 0 | 2.1 | 0.019 | 0.067 | 52.8 | 13.8
交流220kV | 1998-06-05 | 2013-05-24 | 14.9781 | 10.72 | 550.07 | 2219.27 | 19.75 | 5.83 | 6.63 | 0 | 32.21 | 0.03 | 0.001 | 58 | 4.0345
交流220kV | 1996-01-04 | 2010-12-29 | 14.9945 | 3.82 | 321.31 | 2135.39 | 10.12 | 13.3 | 3.33 | 0 | 26.75 | 0.012 | 0.004 | 54.5 | 6.6459
交流220kV | 1996-01-04 | 2010-12-30 | 14.9973 | 3.8 | 321.3 | 2135.4 | 10.1 | 13.3 | 3.3 | 0 | 26.7 | 0.01 | 0.004 | 54.5 | 6.6461
交流220kV | 1998-12-15 | 2013-12-17 | 15.0164 | 6 | 1150 | 3364 | 22 | 8 | 5 | 0.36 | 35.36 | 0 | 0 | 0 | 2.9252
交流220kV | 1998-12-01 | 2013-12-11 | 15.0384 | 57.7 | 1157.9 | 27867 | 19.6 | 12.3 | 13.2 | 0 | 45.1 | 0 | 0 | 0 | 24.0668
交流220kV | 1998-03-01 | 2013-03-12 | 15.0411 | 8 | 363 | 1567 | 8.52 | 2.76 | 1.13 | 0 | 12.41 | 0.015 | 0.114 | 49.8 | 4.3168
交流220kV | 1997-05-03 | 2012-05-17 | 15.0493 | 6 | 999 | 2843 | 28 | 15 | 10 | 0 | 53 | 0.051 | 0 | 51 | 2.8458
交流220kV | 1996-12-13 | 2011-12-28 | 15.0493 | 6 | 417 | 1569 | 22 | 7 | 7 | 0 | 36 | 0 | 0 | 0 | 3.7626
交流220kV | 1998-11-20 | 2013-12-17 | 15.0849 | 13.1 | 1229 | 4021.2 | 15.8 | 6.1 | 5.3 | 0 | 27.2 | 0.05 | 1.4 | 46 | 3.2719
交流220kV | 1997-11-20 | 2012-12-18 | 15.0877 | 24.95 | 253.47 | 6860.96 | 5.11 | 1.26 | 0 | 0 | 6.37 | 0.009 | 0.33 | 60 | 27.0681
交流220kV | 1997-12-01 | 2013-01-03 | 15.1014 | 5.6 | 43.1 | 115.7 | 0.2 | 0 | 0 | 0 | 0.2 | 0.009 | 0.019 | 58 | 2.6845
交流220kV | 1998-07-19 | 2013-08-22 | 15.1041 | 9 | 445 | 3369 | 13 | 3 | 5 | 0 | 21 | 0 | 0 | 55 | 7.5708
交流220kV | 1998-10-31 | 2013-12-11 | 15.1233 | 2.8 | 192.3 | 1845.4 | 13.8 | 10.9 | 8.6 | 0 | 33.3 | 0 | 0 | 0 | 9.5965
交流220kV | 1998-12-25 | 2014-02-13 | 15.1479 | 6.93 | 551.36 | 5481.88 | 25.98 | 3.79 | 6.21 | 0 | 35.98 | 0.005 | 0.015 | 58.4 | 9.9425
交流220kV | 1995-01-25 | 2010-03-18 | 15.1534 | 14 | 612 | 2659 | 44.15 | 8.52 | 16.08 | 0 | 68.75 | 0.001 | 0.002 | 50 | 4.3448
交流220kV | 1997-12-01 | 2013-02-01 | 15.1808 | 2.9 | 563.4 | 665.1 | 10 | 6.5 | 4.6 | 0 | 21.1 | 0.009 | 0.486 | 57.7 | 1.1805
交流220kV | 1997-04-28 | 2012-07-03 | 15.1918 | 2.98 | 586.85 | 7761.48 | 24.45 | 3.7 | 5.01 | 0 | 33.16 | 0.001 | 0 | 68.5 | 13.2257
交流220kV | 1997-10-25 | 2012-12-31 | 15.1945 | 8.95 | 297.27 | 9846.4 | 5.35 | 86.66 | 4.37 | 3.42 | 99.8 | 0 | 0 | 0 | 33.1228
交流220kV | 1998-12-22 | 2014-03-02 | 15.2027 | 16.26 | 318.66 | 2296.41 | 20.43 | 16.27 | 7.18 | 0 | 43.88 | 0.007 | 0.43 | 46.4 | 7.2065
交流220kV | 1997-09-09 | 2012-12-05 | 15.2493 | 4.2 | 438.2 | 2756.1 | 4.1 | 19.2 | 1.8 | 0 | 25.1 | 0 | 0 | 0 | 6.2896
交流220kV | 1996-01-04 | 2011-04-12 | 15.2795 | 4.96 | 310.03 | 2135.26 | 9.27 | 12.5 | 3.11 | 0 | 24.88 | 0.022 | 0.004 | 52.7 | 6.8873
交流220kV | 1998-08-23 | 2013-12-03 | 15.2904 | 6.3 | 658 | 2966 | 8.3 | 4.5 | 1.5 | 0.2 | 14.5 | 0.03 | 0.29 | 46 | 4.5076
交流220kV | 1996-05-31 | 2011-10-10 | 15.3699 | 9 | 866 | 7025 | 23.3 | 23 | 10 | 0.1 | 56.4 | 0.047 | 0.002 | 62 | 8.112
交流220kV | 1998-11-12 | 2014-03-24 | 15.3726 | 11.68 | 618.42 | 2677.76 | 88.06 | 1.58 | 15.1 | 0 | 104.74 | 0.015 | 1.2 | 50 | 4.33
交流220kV | 1997-12-26 | 2013-05-08 | 15.3753 | 18.9 | 152.7 | 2334.5 | 10.71 | 4.08 | 8.82 | 0 | 23.61 | 0.007 | 0.045 | 51 | 15.2881
交流220kV | 1997-07-24 | 2012-12-05 | 15.3781 | 3.5 | 409.6 | 2896.6 | 7.5 | 28.5 | 6.5 | 0 | 42.5 | 0 | 0 | 0 | 7.0718
交流220kV | 1997-06-28 | 2012-11-19 | 15.4055 | 5.4 | 1316.82 | 4460.21 | 10.92 | 11.02 | 4.13 | 0 | 26.07 | 0.009 | 0.004 | 60 | 3.3871
交流220kV | 1997-06-28 | 2012-11-19 | 15.4055 | 3.87 | 984.1 | 4039.66 | 12.72 | 8.68 | 4.36 | 0 | 25.76 | 0.008 | 0.003 | 60 | 4.1049
220 | 1997-10-29 | 2013-03-28 | 15.4219 | 8 | 253 | 375 | 3 | 3.3 | 3 | 0 | 9.3 | 0.007 | 0.001 | 51 | 1.4822
交流220kV | 1998-01-18 | 2013-06-17 | 15.4219 | 15.14 | 1317.99 | 10688 | 0 | 6.36 | 6.16 | 0 | 12.52 | 0.003 | 0.1 | 43 | 8.1093
交流220kV | 1996-10-10 | 2012-03-09 | 15.4219 | 6.7 | 1856.29 | 9822.22 | 28.63 | 3.05 | 9.76 | 0 | 41.44 | 0.006 | 0.001 | 54 | 5.2913
交流220kV | 1998-07-19 | 2013-12-17 | 15.4247 | 4 | 358 | 2494 | 11 | 2 | 3 | 0 | 16 | 0 | 0 | 0 | 6.9665
交流220kV | 1998-07-01 | 2013-12-04 | 15.4384 | 6.5 | 983.3 | 3901.6 | 15.9 | 4.4 | 3.9 | 0 | 24.2 | 0 | 0 | 0 | 3.9679
交流220kV | 1997-10-06 | 2013-03-12 | 15.4411 | 21.23 | 123.9 | 1768.03 | 5.24 | 1.87 | 1.3 | 0 | 8.41 | 0.013 | 0.6 | 70.6 | 14.2698
交流220kV | 1998-01-09 | 2013-06-20 | 15.4548 | 9.9 | 754.7 | 7058.6 | 13.6 | 8.1 | 4.4 | 0 | 26.1 | 0.012 | 0 | 67.9 | 9.3529
交流220kV | 1996-12-13 | 2012-05-25 | 15.4575 | 6 | 461 | 2038 | 27 | 9 | 11 | 0 | 47 | 0.056 | 0 | 49 | 4.4208
交流220kV | 1997-11-20 | 2013-05-13 | 15.4877 | 10.28 | 239.12 | 1094.08 | 5 | 0 | 0 | 0 | 5 | 0.025 | 0.33 | 40 | 4.5754
交流220kV | 1990-11-02 | 2006-04-29 | 15.4986 | 21.84 | 971.76 | 6847.76 | 43.96 | 65.68 | 14.51 | 0 | 124.15 | 0.006 | 0.039 | 51.6 | 7.0468
交流220kV | 1996-06-16 | 2011-12-16 | 15.5096 | 3.6 | 1368.2 | 0 | 20.8 | 12.1 | 8 | 0 | 40.9 | 0 | 0 | 0 | 0
交流220kV | 1996-08-09 | 2012-02-14 | 15.526 | 2.4 | 327.6 | 1609.2 | 8.6 | 3 | 2 | 0 | 13.6 | 0.014 | 0.979 | 65.4 | 4.9121
交流220kV | 1996-08-09 | 2012-02-14 | 15.526 | 2.4 | 327.6 | 1609.2 | 8.6 | 2 | 3 | 0 | 13.6 | 0.014 | 0.979 | 65.4 | 4.9121
220 | 1997-01-13 | 2012-07-23 | 15.5342 | 111.48 | 1134.96 | 4145.59 | 40.32 | 1.83 | 6.65 | 0 | 48.8 | 0.015 | 0.168 | 59.2 | 3.6526
交流220kV | 1997-11-20 | 2013-06-06 | 15.5534 | 1.84 | 238.49 | 5719.54 | 1.97 | 1.48 | 1.76 | 0 | 5.21 | 0.013 | 0.33 | 55 | 23.9823
交流220kV | 1997-10-14 | 2013-05-04 | 15.5644 | 10 | 128 | 1136 | 7.8 | 0 | 0 | 0 | 7.8 | 0.006 | 0.034 | 54 | 8.875
交流220kV | 1996-02-28 | 2011-09-28 | 15.5918 | 10.42 | 184.92 | 3013.43 | 24.47 | 2.15 | 4.49 | 0 | 31.11 | 0 | 0 | 0 | 16.2959
交流220kV | 1997-05-03 | 2012-12-05 | 15.6027 | 7 | 1190 | 3081 | 32 | 16 | 9 | 0 | 57 | 0 | 0 | 0 | 2.5891
交流220kV | 1997-05-03 | 2012-12-05 | 15.6027 | 5 | 843 | 1871 | 10 | 4 | 2 | 0 | 16 | 0 | 0 | 0 | 2.2195
交流220kV | 1997-10-25 | 2013-06-08 | 15.6301 | 3.32 | 195.25 | 7423.2 | 4.93 | 81.48 | 4.09 | 4.07 | 94.57 | 0 | 0 | 14.64 | 38.019
交流220kV | 1997-05-03 | 2012-12-17 | 15.6356 | 5 | 765 | 1746 | 21 | 11 | 6 | 0 | 38 | 0 | 0 | 0 | 2.2824
交流220kV | 1997-04-28 | 2012-12-20 | 15.6575 | 19.12 | 147.17 | 2056.44 | 17.66 | 4.17 | 4.57 | 0 | 26.4 | 0 | 0 | 0 | 13.9732
交流220kV | 1997-02-01 | 2012-09-29 | 15.6685 | 28.82 | 203.44 | 2287.44 | 10.46 | 5.97 | 2.78 | 0 | 19.21 | 0.026 | 0.18 | 55 | 11.2438
交流220kV | 1997-10-03 | 2013-06-08 | 15.6904 | 4.57 | 958.25 | 3647.7 | 15.6 | 21.59 | 3.27 | 0.74 | 41.2 | 0 | 0 | 0 | 3.8066
交流220kV | 1997-09-09 | 2013-06-05 | 15.7479 | 5 | 393.4 | 4497.8 | 4.2 | 23.9 | 1.8 | 0 | 29.9 | 0.01 | 0 | 69.4 | 11.4331
交流220kV | 1996-05-03 | 2012-02-14 | 15.7945 | 2.6 | 395.4 | 2108.7 | 9.2 | 3.1 | 2.3 | 0 | 14.6 | 0.012 | 0.123 | 65.7 | 5.3331
交流220kV | 1996-06-01 | 2012-03-14 | 15.7945 | 14.79 | 484.97 | 2803.36 | 5.85 | 2.34 | 1 | 0 | 9.19 | 0.033 | 0.001 | 55.3 | 5.7805
交流220kV | 1995-08-14 | 2011-06-09 | 15.8301 | 12 | 346 | 3893 | 5.4 | 4.5 | 1 | 0 | 10.9 | 0.007 | 0.009 | 41 | 11.2514
交流220kV | 1996-02-01 | 2011-12-27 | 15.9123 | 15 | 395 | 2009 | 5 | 4 | 0 | 0 | 9 | 0 | 0 | 0 | 5.0861
交流220kV | 1998-01-09 | 2013-12-11 | 15.9315 | 9.7 | 888.7 | 5830.3 | 14.8 | 8.1 | 4.2 | 0 | 27.1 | 0 | 0 | 0 | 6.5605
220 | 1998-04-10 | 2014-03-13 | 15.9342 | 8.3 | 630.9 | 1249.8 | 9.7 | 2.1 | 4.4 | 0 | 16.2 | 0.049 | 0.083 | 60.8 | 1.981
交流220kV | 1997-01-07 | 2012-12-10 | 15.9342 | 13.09 | 584.35 | 5186.74 | 16.64 | 9.48 | 4.69 | 0.21 | 31.02 | 0.028 | 0.35 | 57 | 8.8761
交流220kV | 1996-12-13 | 2012-12-06 | 15.9918 | 6 | 471 | 2076 | 27 | 9 | 10 | 0 | 46 | 0 | 0 | 0 | 4.4076
220 | 1998-02-13 | 2014-03-10 | 16.0795 | 48.83 | 618.36 | 3183.98 | 106.55 | 11.93 | 25.47 | 0 | 143.95 | 0.054 | 0.045 | 57.1 | 5.1491
交流220kV | 1996-02-28 | 2012-03-29 | 16.0932 | 8.47 | 150.92 | 2584.87 | 21.67 | 1.86 | 1.11 | 0 | 24.64 | 0 | 0 | 0 | 17.1274
交流220kV | 1995-01-25 | 2011-02-24 | 16.0932 | 6 | 410 | 2669 | 38.67 | 7.65 | 16.57 | 0 | 62.89 | 0.001 | 0.001 | 50 | 6.5098
220 | 1997-01-13 | 2013-02-21 | 16.1178 | 1.43 | 8.76 | 461.43 | 0.07 | 1.59 | 0.3 | 0 | 1.96 | 0.017 | 0.051 | 58 | 52.6747
交流220kV | 1997-04-28 | 2013-06-06 | 16.1178 | 75.5 | 393.56 | 2415.35 | 24.71 | 4.97 | 4.19 | 0 | 33.87 | 0 | 0 | 0 | 6.1372
交流220kV | 1996-02-28 | 2012-04-18 | 16.1479 | 10.16 | 151.92 | 2901.36 | 21.68 | 1.87 | 1.24 | 0 | 24.79 | 0 | 0.001 | 59.8 | 19.0979
交流220kV | 1997-06-01 | 2013-07-22 | 16.1507 | 18 | 122 | 3016 | 21.38 | 5.45 | 5.97 | 0 | 32.8 | 0.046 | 0.005 | 41 | 24.7213
交流220kV | 1997-05-03 | 2013-07-05 | 16.1836 | 5 | 984 | 3055 | 26 | 15 | 8 | 0 | 49 | 0.083 | 0.064 | 53 | 3.1047
交流220kV | 1997-10-25 | 2013-12-27 | 16.1836 | 6.88 | 296.95 | 10366.77 | 5.85 | 119.98 | 5.44 | 2.91 | 134.18 | 0 | 0 | 0 | 34.9108
交流220kV | 1987-12-28 | 2004-03-10 | 16.211 | 34.6 | 1365.5 | 7291.9 | 38.3 | 23.8 | 14.2 | 0 | 76.3 | 0.004 | 0.599 | 50 | 5.3401
交流220kV | 1996-12-18 | 2013-03-08 | 16.2301 | 12 | 697 | 3590 | 12.18 | 7.47 | 3.84 | 0 | 23.49 | 0.023 | 0.099 | 52.4 | 5.1506
交流220kV | 1997-09-09 | 2013-12-04 | 16.2466 | 9.9 | 662.1 | 3672.1 | 5.2 | 26.5 | 1.6 | 0 | 33.3 | 0 | 0 | 0 | 5.5461
交流220kV | 1997-10-03 | 2013-12-30 | 16.2521 | 5.7 | 1015.82 | 4051.3 | 14.01 | 26.33 | 3.93 | 0.58 | 44.85 | 0 | 0 | 0 | 3.9882
220 | 1997-01-18 | 2013-04-24 | 16.274 | 5.32 | 521.01 | 5795.78 | 7.71 | 70.66 | 7.5 | 0 | 85.87 | 0.026 | 0.102 | 63 | 11.1241
交流220kV | 1995-08-24 | 2011-12-15 | 16.3205 | 16.6 | 2077.9 | 5825.7 | 24.3 | 8.3 | 6.3 | 0 | 38.9 | 0 | 0 | 0 | 2.8036
交流220kV | 1995-01-17 | 2011-05-11 | 16.3233 | 15.91 | 556.21 | 2630.12 | 7.57 | 1.83 | 8.25 | 1.31 | 18.96 | 0.01 | 0.001 | 59 | 4.7286
交流220kV | 1996-02-01 | 2012-05-31 | 16.3397 | 25.6 | 369.7 | 2177.3 | 5.3 | 5.4 | 1.4 | 0 | 12.1 | 0.049 | 0.059 | 42 | 5.8894
交流220kV | 1996-01-04 | 2012-05-10 | 16.3589 | 7.5 | 403.67 | 3046.24 | 11.04 | 11.42 | 3.55 | 0 | 26.01 | 0.02 | 0.001 | 53.9 | 7.5464
交流220kV | 1995-10-10 | 2012-02-17 | 16.3671 | 11 | 201 | 657 | 3.1 | 0.4 | 0 | 0 | 3.5 | 0.014 | 0.001 | 46 | 3.2687
交流220kV | 1997-07-24 | 2013-12-04 | 16.3753 | 7.6 | 512.6 | 3591.9 | 8.6 | 40.1 | 6.6 | 0 | 55.3 | 0 | 0 | 0 | 7.0072
交流220kV | 1996-10-21 | 2013-03-08 | 16.389 | 2.24 | 171.78 | 1081.22 | 4.97 | 5.81 | 3.71 | 0 | 14.49 | 0.01 | 0.145 | 65 | 6.2942
220 | 1996-12-22 | 2013-05-13 | 16.4 | 19.67 | 1729.55 | 104698.1 | 17.72 | 12.65 | 6.84 | 0 | 37.21 | 0.016 | 0.06 | 67.2 | 60.5349
交流220kV | 1995-12-20 | 2012-05-10 | 16.4 | 26.6 | 616.33 | 3105.59 | 164.02 | 180.06 | 131.3 | 0 | 475.38 | 0.009 | 0.002 | 55 | 5.0388
交流220kV | 1997-03-06 | 2013-07-30 | 16.411 | 5.46 | 453.42 | 2241.72 | 15.11 | 5.54 | 5.77 | 0 | 26.42 | 0.01 | 0.29 | 47 | 4.944
交流220kV | 1997-03-06 | 2013-07-30 | 16.411 | 5.46 | 453.42 | 2241.72 | 15.11 | 5.54 | 5.77 | 0 | 26.42 | 0.01 | 0.29 | 45 | 4.944
220 | 1996-10-28 | 2013-03-28 | 16.4247 | 6 | 29 | 215 | 6 | 8 | 4.4 | 0 | 18.4 | 0.007 | 0.001 | 52 | 7.4138
交流220kV | 1995-06-07 | 2011-11-22 | 16.4712 | 2.1 | 5.8 | 687.4 | 0.6 | 1 | 0.8 | 0 | 2.4 | 0 | 0 | 54.3 | 118.5172
交流220kV | 1995-11-16 | 2012-05-02 | 16.4712 | 13.6 | 811.4 | 3967.2 | 8 | 9.6 | 2.2 | 0 | 19.8 | 0.03 | 0.28 | 58.8 | 4.8893
交流220kV | 1996-09-26 | 2013-03-14 | 16.474 | 2 | 174.2 | 2309.6 | 2 | 6.2 | 1.5 | 0 | 9.7 | 0.012 | 0.075 | 62.3 | 13.2583
交流220kV | 1996-06-16 | 2012-12-11 | 16.4986 | 8.5 | 1598.9 | 9067.6 | 27.1 | 17.8 | 10.7 | 0 | 55.6 | 0 | 0 | 0 | 5.6711
交流220kV | 1996-08-09 | 2013-02-18 | 16.5397 | 3 | 409.4 | 2278.5 | 9.8 | 2.1 | 3.6 | 0 | 15.5 | 0.014 | 0.672 | 62.8 | 5.5655
交流220kV | 1996-12-13 | 2013-06-28 | 16.5507 | 7 | 415 | 1033 | 12 | 6 | 4 | 0 | 22 | 0.058 | 0.084 | 50 | 2.4892
交流220kV | 1995-08-14 | 2012-03-05 | 16.5699 | 43 | 248 | 3683 | 17 | 6.7 | 11 | 2.5 | 37.2 | 0.008 | 0.005 | 52 | 14.8508
220 | 1997-08-31 | 2014-04-04 | 16.6027 | 12.44 | 355.52 | 3502.1 | 3.73 | 36.2 | 1.36 | 0 | 41.29 | 0.045 | 0.001 | 50.9 | 9.8506
220 | 1997-08-31 | 2014-04-04 | 16.6027 | 10.41 | 1056.06 | 3980.75 | 29.99 | 8.86 | 7.27 | 0 | 46.12 | 0.03 | 0.001 | 53.9 | 3.7694
交流220kV | 1995-08-24 | 2012-03-29 | 16.6082 | 21.8 | 2268 | 5611.8 | 26.2 | 8.9 | 5.4 | 0 | 40.5 | 0.008 | 0.06 | 56.5 | 2.4743
交流220kV | 1995-09-27 | 2012-05-02 | 16.6082 | 10.3 | 249.8 | 2088.6 | 5.8 | 3.5 | 0.9 | 0 | 10.2 | 0.02 | 0.06 | 45.2 | 8.3611
交流220kV | 1997-05-03 | 2013-12-17 | 16.6356 | 6 | 1127 | 3381 | 31 | 15 | 9 | 0 | 55 | 0 | 0 | 0 | 3
交流220kV | 1997-04-28 | 2013-12-19 | 16.6548 | 8.4 | 58.08 | 834.15 | 18.67 | 3.47 | 4.57 | 0 | 26.71 | 0 | 0 | 51.4 | 14.3621
交流220kV | 1996-05-09 | 2013-01-18 | 16.7068 | 6.05 | 208.89 | 2198.07 | 2.2 | 2.48 | 0.69 | 0 | 5.37 | 0.015 | 0.175 | 45.3 | 10.5226
交流220kV | 1997-06-01 | 2014-02-20 | 16.7342 | 19 | 123 | 3005 | 21.61 | 5.33 | 5.99 | 0 | 32.93 | 0.047 | 0.522 | 44 | 24.4309
交流220kV | 1995-10-14 | 2012-07-05 | 16.737 | 16.7 | 1199.3 | 7391.6 | 15.7 | 31.5 | 5.1 | 0 | 52.3 | 0.009 | 0.119 | 56 | 6.1633
交流220kV | 1995-10-14 | 2012-07-05 | 16.737 | 10.61 | 1350.31 | 9475.52 | 21.88 | 35.97 | 6.26 | 0 | 64.11 | 0.028 | 0.136 | 54 | 7.0173
交流220kV | 1995-09-27 | 2012-07-09 | 16.7945 | 14.9 | 315.1 | 2364.5 | 6.5 | 3.5 | 1.1 | 0 | 11.1 | 0.01 | 0.13 | 55.2 | 7.504
交流220kV | 1997-01-07 | 2013-10-24 | 16.8055 | 8.51 | 514.34 | 6008.77 | 18.85 | 12.15 | 5.32 | 0.2 | 36.52 | 0.03 | 0.34 | 53 | 11.6825
交流220kV | 1996-05-03 | 2013-02-18 | 16.8082 | 3 | 579.4 | 2974.7 | 10.5 | 2.5 | 3.3 | 0 | 16.3 | 0.012 | 0.369 | 64.2 | 5.1341
交流220kV | 1995-10-14 | 2012-08-13 | 16.8438 | 12.02 | 1297.84 | 10533.22 | 22.89 | 35.46 | 6.55 | 0 | 64.9 | 0.026 | 0.137 | 55 | 8.116
交流220kV | 1996-06-01 | 2013-04-01 | 16.8438 | 12.94 | 448.5 | 4252.14 | 7.6 | 3.03 | 1.55 | 0 | 12.18 | 0.011 | 0.081 | 60.4 | 9.4808
交流220kV | 1996-02-01 | 2012-12-05 | 16.8548 | 18 | 416 | 2149 | 6 | 4 | 1 | 0 | 11 | 0 | 0 | 0 | 5.1659
交流220kV | 1995-08-24 | 2012-06-29 | 16.8603 | 23 | 2176.3 | 7233.7 | 29.7 | 13.2 | 7.3 | 0 | 50.2 | 0 | 0 | 0 | 3.3239
交流220kV | 1996-04-10 | 2013-02-19 | 16.874 | 15.82 | 460.61 | 4272.57 | 13.32 | 1.31 | 3.08 | 0 | 17.71 | 0.013 | 0.423 | 40.3 | 9.2759
交流220kV | 1995-01-18 | 2011-12-16 | 16.9205 | 4.6 | 700 | 7539 | 12.4 | 40.5 | 5.7 | 0 | 58.6 | 0 | 0 | 0 | 10.77
交流220kV | 1993-04-09 | 2010-03-17 | 16.9479 | 13 | 317 | 2509 | 17.75 | 32.55 | 3.55 | 0.13 | 53.98 | 0.001 | 0.002 | 50 | 7.9148
交流220kV | 1996-06-16 | 2013-06-06 | 16.9836 | 4.6 | 1715.3 | 14152.2 | 29.1 | 23.5 | 14.2 | 0 | 66.8 | 0.008 | 0 | 49.6 | 8.2506
220 | 1996-10-28 | 2013-10-22 | 16.9945 | 5 | 20 | 473 | 10.8 | 21.9 | 0 | 0 | 32.7 | 0.008 | 0.008 | 51 | 23.65
交流220kV | 1994-12-17 | 2011-12-15 | 17.0055 | 10.3 | 652.5 | 2982.6 | 14.4 | 6.2 | 4.3 | 0 | 24.9 | 0 | 0 | 0 | 4.571
交流220kV | 1996-12-13 | 2013-12-18 | 17.0247 | 6 | 415 | 2166 | 28 | 8 | 10 | 0 | 46 | 0 | 0 | 0 | 5.2193
交流220kV | 1995-09-27 | 2012-10-23 | 17.0849 | 11 | 289.4 | 2037.1 | 6.3 | 3.2 | 2.6 | 0 | 12.1 | 0.02 | 0.15 | 56 | 7.039
交流220kV | 1995-01-25 | 2012-02-22 | 17.0877 | 9 | 581 | 2404 | 51.1 | 8.53 | 20.74 | 0 | 80.37 | 0.001 | 0.001 | 60.5 | 4.1377
交流220kV | 1994-11-10 | 2011-12-13 | 17.1014 | 4.42 | 1004.99 | 6376.04 | 21.68 | 50.03 | 8.8 | 0 | 80.51 | 0.018 | 0 | 0 | 6.3444
交流220kV | 1995-02-16 | 2012-03-26 | 17.1178 | 2.69 | 251.97 | 1860.04 | 2.04 | 2.42 | 0.5 | 0 | 4.96 | 0.02 | 0.27 | 57 | 7.382
交流220kV | 1995-02-16 | 2012-03-26 | 17.1178 | 3.21 | 141.1 | 1442.82 | 6.39 | 11.8 | 2.07 | 0 | 20.26 | 0.019 | 0.14 | 57 | 10.2255
交流220kV | 1996-04-19 | 2013-05-30 | 17.1233 | 47.68 | 885.18 | 1801.64 | 5.18 | 22.46 | 15.4 | 0 | 43.04 | 0.012 | 0.182 | 56 | 2.0353
交流220kV | 1994-12-09 | 2012-01-19 | 17.1233 | 17 | 32 | 3674 | 10 | 21.1 | 2.4 | 0 | 33.5 | 0.037 | 0.48 | 46 | 114.8125
交流220kV | 1995-10-10 | 2012-11-21 | 17.1288 | 1.19 | 105 | 515 | 2.1 | 0.3 | 0.5 | 0 | 2.9 | 0.014 | 0 | 46.7 | 4.9048
交流220kV | 1995-10-10 | 2012-11-21 | 17.1288 | 12.19 | 115 | 515 | 2.1 | 0.3 | 0.5 | 0 | 2.9 | 0.014 | 0 | 46.7 | 4.4783
交流220kV | 1994-12-02 | 2012-01-18 | 17.1397 | 5 | 25 | 1557 | 7.5 | 5.6 | 3.1 | 0 | 16.2 | 0.037 | 0.46 | 46 | 62.28
220 | 1997-01-13 | 2014-03-03 | 17.1452 | 109.36 | 1083.84 | 2932.24 | 42.67 | 1.68 | 6.58 | 0 | 50.93 | 0.051 | 0.182 | 60 | 2.7054
交流220kV | 1994-10-21 | 2011-12-13 | 17.1562 | 3.99 | 507.41 | 4644.13 | 20.26 | 10.19 | 6.41 | 0 | 36.86 | 0.003 | 0.02 | 49 | 9.1526
交流220kV | 1996-02-28 | 2013-04-25 | 17.1671 | 13.07 | 106.59 | 1908.92 | 4.93 | 0.81 | 0.65 | 0 | 6.39 | 0 | 0.001 | 59.8 | 17.909
交流220kV | 1996-02-28 | 2013-04-25 | 17.1671 | 13.07 | 106.59 | 1908.92 | 4.93 | 0.81 | 0.65 | 0 | 6.39 | 0 | 0.001 | 65 | 17.909
交流220kV | 1995-12-28 | 2013-03-12 | 17.2164 | 2.8 | 115 | 2199.2 | 2.8 | 0.9 | 1.3 | 0 | 5 | 0.009 | 0.451 | 55.3 | 19.1235
交流220kV | 1995-08-24 | 2012-11-14 | 17.2384 | 19.3 | 2206.4 | 6224.6 | 29.1 | 8.2 | 6.6 | 0 | 43.9 | 0 | 0 | 0 | 2.8212
交流220kV | 1995-01-27 | 2012-05-15 | 17.3096 | 23.52 | 668.75 | 6711.6 | 19.51 | 6.75 | 7.07 | 0 | 33.33 | 0.04 | 0.001 | 60 | 10.036
交流220kV | 1995-08-24 | 2012-12-13 | 17.3178 | 15.8 | 1848.1 | 6098.2 | 24.5 | 12.7 | 12.1 | 0 | 49.3 | 0 | 0 | 0 | 3.2997
交流220kV | 1994-02-01 | 2011-05-24 | 17.3178 | 7.21 | 453.67 | 4004.7 | 13.97 | 8.18 | 20 | 0 | 42.15 | 0.01 | 0.008 | 60 | 8.8273
交流220kV | 1989-06-17 | 2006-10-10 | 17.326 | 32.8 | 1591 | 12773 | 46 | 68.3 | 11.5 | 0.3 | 126.1 | 0.006 | 0.08 | 48 | 8.0283
交流220kV | 1994-11-10 | 2012-03-07 | 17.3342 | 8 | 1171 | 8558 | 25.1 | 67.8 | 11.2 | 0 | 104.1 | 0 | 0 | 0 | 7.3083
交流220kV | 1996-02-01 | 2013-06-27 | 17.4137 | 19 | 918 | 3830 | 8 | 29 | 3 | 0 | 40 | 0.057 | 0.053 | 50 | 4.1721
交流220kV | 1993-12-21 | 2011-05-24 | 17.4329 | 62.1 | 12 | 278.4 | 0.9 | 0.5 | 0.1 | 0 | 1.5 | 0.01 | 0.13 | 60 | 23.2
交流220kV | 1994-12-28 | 2012-06-05 | 17.4493 | 3.35 | 738.39 | 3805.31 | 7.27 | 14.94 | 1.61 | 0 | 23.82 | 0.004 | 0.281 | 65.8 | 5.1535
交流220kV | 1995-01-26 | 2012-07-04 | 17.4493 | 19.17 | 412.41 | 728.4 | 12.31 | 18.42 | 2.14 | 0.44 | 33.31 | 0.008 | 0.001 | 58 | 1.7662
交流220kV | 1994-10-01 | 2012-03-09 | 17.4493 | 2.21 | 173.69 | 2497.51 | 3.44 | 16.53 | 1.86 | 0.1 | 21.93 | 0.014 | 0.001 | 54 | 14.3791
交流220kV | 1995-10-10 | 2013-03-21 | 17.4575 | 16.6 | 115 | 425 | 2.1 | 0.28 | 0.5 | 0 | 2.88 | 0.016 | 0 | 49 | 3.6957
交流220kV | 1996-10-10 | 2014-03-26 | 17.4685 | 2.51 | 1299.03 | 7623.83 | 24.83 | 2.82 | 9.23 | 0 | 36.88 | 0.003 | 0.001 | 61.2 | 5.8689
交流220kV | 1996-06-16 | 2013-12-04 | 17.4795 | 3.8 | 1651.2 | 9273 | 27.1 | 19 | 10.9 | 0 | 57 | 0 | 0 | 0 | 5.6159
交流220kV | 1995-06-07 | 2012-12-06 | 17.5123 | 5.3 | 100.9 | 1502.5 | 1.9 | 4.5 | 0.5 | 0 | 6.9 | 0 | 0 | 0 | 14.891
交流220kV | 1995-01-17 | 2012-07-18 | 17.5123 | 23.71 | 698.25 | 3164.36 | 9.64 | 9.7 | 1.1 | 0.6 | 21.04 | 0.006 | 0.001 | 59 | 4.5318
交流220kV | 1987-12-28 | 2005-07-01 | 17.5205 | 4.2 | 223 | 1802.3 | 2.9 | 8.5 | 3.1 | 0 | 14.5 | 0.008 | 0.106 | 58.3 | 8.0821
交流220kV | 1994-10-21 | 2012-04-25 | 17.5233 | 21.39 | 979.28 | 7289.04 | 8.46 | 9.2 | 1.45 | 0.41 | 19.52 | 0.002 | 0.2 | 41 | 7.4433
交流220kV | 1996-08-09 | 2014-02-13 | 17.526 | 2.2 | 450.8 | 2703.4 | 12 | 2.6 | 3.6 | 0 | 18.2 | 0.016 | 0.342 | 62.6 | 5.9969
交流220kV | 1994-11-10 | 2012-05-18 | 17.5315 | 13.24 | 933.36 | 9309.15 | 7.55 | 107.7 | 5.15 | 0 | 120.4 | 0 | 0.118 | 0 | 9.9738
交流220kV | 1994-10-07 | 2012-04-24 | 17.5589 | 7.77 | 851.98 | 7349.13 | 29.2 | 33.21 | 13.22 | 0 | 75.63 | 0.01 | 0.3 | 52 | 8.6259
交流220kV | 1994-12-17 | 2012-07-05 | 17.5616 | 10.7 | 574 | 2801.7 | 16.6 | 7.2 | 4.5 | 0 | 28.3 | 0 | 0 | 57.6 | 4.881
220 | 1994-04-01 | 2011-11-03 | 17.6027 | 33.51 | 636.1 | 2502.75 | 5.66 | 13.78 | 1.86 | 0 | 21.3 | 0.008 | 0.054 | 64.4 | 3.9345
交流220kV | 1995-09-15 | 2013-04-27 | 17.6274 | 62 | 252 | 1941 | 13.83 | 0.73 | 1.87 | 0 | 16.43 | 0.006 | 0.073 | 50 | 7.7024
交流220kV | 1993-12-03 | 2011-07-20 | 17.6384 | 0.76 | 3.09 | 69.39 | 0.3 | 0.21 | 0 | 0 | 0.51 | 0.003 | 0.03 | 49 | 22.4563
交流220kV | 1995-08-24 | 2013-04-18 | 17.663 | 18.4 | 1937.4 | 6598.2 | 27.3 | 11.3 | 7.3 | 0.1 | 46 | 0.009 | 0.04 | 52.4 | 3.4057
交流220kV | 1994-12-17 | 2012-08-17 | 17.6795 | 10.6 | 667.8 | 3472.6 | 18.4 | 8 | 5 | 0 | 31.4 | 0 | 0 | 0 | 5.2001
交流220kV | 1994-12-17 | 2012-08-17 | 17.6795 | 9 | 618.6 | 3496.1 | 16.3 | 8 | 7.5 | 0 | 31.8 | 0 | 0 | 0 | 5.6516
交流220kV | 1993-12-21 | 2011-08-25 | 17.6877 | 3 | 84.8 | 388.4 | 2.2 | 0.6 | 0.4 | 0 | 3.2 | 0.012 | 0.28 | 58 | 4.5802
交流220kV | 1992-09-27 | 2010-06-28 | 17.7616 | 15 | 946 | 8459 | 25 | 39 | 18 | 0 | 82 | 0.006 | 0 | 48 | 8.9419
交流220kV | 1996-02-28 | 2013-12-03 | 17.7753 | 18.5 | 108.47 | 1399.28 | 5.5 | 0.64 | 0.46 | 0 | 6.6 | 0 | 0.001 | 63 | 12.9002
交流220kV | 1996-06-01 | 2014-03-07 | 17.7753 | 18.31 | 547.19 | 4737.07 | 7.88 | 2.67 | 1.61 | 0 | 12.16 | 0.025 | 0.07 | 60.04 | 8.6571
交流220kV | 1996-05-03 | 2014-02-13 | 17.7945 | 2.8 | 620.3 | 3313.9 | 13 | 2.8 | 3.7 | 0 | 19.5 | 0.013 | 0.083 | 51.6 | 5.3424
交流220kV | 1996-02-01 | 2013-12-17 | 17.8877 | 19 | 446 | 2465 | 6 | 5 | 2 | 0 | 13 | 0 | 0 | 0 | 5.5269
交流220kV | 1995-01-18 | 2012-12-05 | 17.8932 | 5.7 | 772.9 | 4734.4 | 12.9 | 33.7 | 4 | 0 | 50.6 | 0 | 0 | 0 | 6.1255
交流220kV | 1993-12-03 | 2011-11-01 | 17.9233 | 0.69 | 3.39 | 69.22 | 0.23 | 0.26 | 0 | 0 | 0.49 | 0.003 | 0.03 | 49 | 20.4189
交流220kV | 1993-10-29 | 2011-09-28 | 17.926 | 29.28 | 1257.93 | 7816.18 | 26.88 | 29.73 | 6.67 | 1.16 | 64.44 | 0 | 0 | 0 | 6.2135
交流220kV | 1994-12-28 | 2012-12-10 | 17.9644 | 2.03 | 723.96 | 2974.31 | 6.74 | 15.06 | 1.14 | 0 | 22.94 | 0 | 0 | 0 | 4.1084
交流220kV | 1994-12-17 | 2012-12-13 | 18.0027 | 13.6 | 731.1 | 2908.2 | 18.4 | 9.3 | 4.8 | 0 | 32.5 | 0 | 0 | 0 | 3.9778
交流220kV | 1995-06-07 | 2013-06-04 | 18.0055 | 7 | 118.4 | 3292.2 | 2.5 | 7.3 | 0.8 | 0 | 10.6 | 0.028 | 0 | 69.5 | 27.8057
交流220kV | 1996-02-28 | 2014-03-06 | 18.0301 | 17.86 | 109.81 | 1266.12 | 5.86 | 0.68 | 0.7 | 0 | 7.24 | 0 | 0.069 | 50.2 | 11.5301
交流220kV | 1993-04-09 | 2011-04-22 | 18.0466 | 12 | 499 | 2552 | 20.1 | 35.24 | 4.31 | 0.11 | 59.76 | 0.006 | 0.08 | 50 | 5.1142
交流220kV | 1993-12-03 | 2011-12-19 | 18.0548 | 1.26 | 111.98 | 1981.53 | 1.54 | 4.06 | 0.54 | 0.12 | 6.26 | 0.003 | 0.02 | 44 | 17.6954
交流220kV | 1994-01-24 | 2012-02-09 | 18.0548 | 19.12 | 604.78 | 6017.99 | 47.75 | 95.63 | 18.45 | 0.88 | 162.71 | 0.011 | 0.056 | 58.4 | 9.9507
交流220kV | 1994-11-10 | 2012-12-07 | 18.0877 | 4.46 | 1132.77 | 7695.51 | 28.94 | 64.78 | 11.46 | 0 | 105.18 | 0.017 | 0 | 0 | 6.7935
交流220kV | 1993-11-14 | 2011-12-12 | 18.0877 | 9.8 | 1069.2 | 3019.2 | 15.2 | 8.6 | 3.3 | 0 | 27.1 | 0 | 0 | 0 | 2.8238
交流220kV | 1994-12-09 | 2013-01-10 | 18.1014 | 13 | 236 | 3289 | 11.9 | 30.1 | 5.8 | 0 | 47.8 | 0.026 | 0.04 | 46 | 13.9364
交流220kV | 1995-02-16 | 2013-03-20 | 18.1014 | 4.43 | 318.06 | 1722.8 | 9.27 | 14.78 | 3.12 | 0 | 27.17 | 0.016 | 0.47 | 58 | 5.4166
交流220kV | 1995-02-16 | 2013-03-20 | 18.1014 | 3.56 | 425.64 | 2077.21 | 3.59 | 4.74 | 0.94 | 0 | 9.27 | 0.014 | 0.37 | 61 | 4.8802
交流220kV | 1994-10-21 | 2012-12-14 | 18.1616 | 4.1 | 436.69 | 4247.92 | 19.84 | 9.49 | 6.09 | 0 | 35.42 | 0.003 | 0.1 | 40 | 9.7275
交流220kV | 1995-01-25 | 2013-03-22 | 18.1671 | 4 | 96 | 903 | 6.67 | 1.14 | 1.28 | 0 | 9.09 | 0.001 | 0.3 | 44.8 | 9.4062
交流220kV | 1993-09-30 | 2011-12-16 | 18.2219 | 5.9 | 567.1 | 2607 | 5.1 | 16.4 | 1.7 | 0 | 23.2 | 0 | 0 | 0 | 4.5971
交流220kV | 1995-01-26 | 2013-04-28 | 18.2658 | 12.89 | 410.45 | 389.77 | 15.14 | 17.77 | 3.76 | 0.42 | 37.09 | 0.06 | 0.001 | 60 | 0.94962
交流220kV | 1995-09-01 | 2013-12-05 | 18.274 | 5.1 | 220.7 | 2534.1 | 4.5 | 6 | 1.1 | 0 | 11.6 | 0 | 0 | 0 | 11.4821
交流220kV | 1993-12-09 | 2012-03-29 | 18.3151 | 9.61 | 166.17 | 758.74 | 11.41 | 5.6 | 1.64 | 0 | 18.65 | 0.014 | 0.072 | 59 | 4.566
交流220kV | 1992-09-27 | 2011-01-19 | 18.3233 | 32 | 1489 | 8737 | 31 | 42 | 18 | 0 | 91 | 0.005 | 0.001 | 46 | 5.8677
交流220kV | 1995-01-27 | 2013-05-21 | 18.326 | 6.09 | 483.7 | 7751.46 | 22.53 | 6.25 | 7.26 | 0 | 36.04 | 0.05 | 0.001 | 59 | 16.0253
交流220kV | 1993-11-14 | 2012-03-14 | 18.3425 | 9.7 | 1056.5 | 2930.4 | 14.1 | 9.1 | 3.5 | 0.3 | 27 | 0.02 | 0.04 | 56.8 | 2.7737
交流220kV | 1987-12-28 | 2006-04-29 | 18.3479 | 5.09 | 425.38 | 2141.81 | 4.78 | 14.27 | 7.43 | 0 | 26.48 | 0.008 | 0.219 | 51.3 | 5.0351
交流220kV | 1995-01-17 | 2013-05-24 | 18.3616 | 6.91 | 211.42 | 2204.4 | 4.12 | 7.18 | 2.19 | 0.58 | 14.07 | 0.05 | 0.001 | 59 | 10.4266
交流220kV | 1993-10-20 | 2012-03-02 | 18.3781 | 7.28 | 750.56 | 4950.75 | 17.29 | 36.47 | 9.76 | 0 | 63.52 | 0.015 | 0.002 | 60.1 | 6.5961
交流220kV | 1995-01-18 | 2013-06-04 | 18.389 | 8.5 | 813.8 | 6433.2 | 13.4 | 38 | 4.5 | 0 | 55.9 | 0.043 | 0 | 66.1 | 7.9051
交流220kV | 1993-12-03 | 2012-04-25 | 18.4055 | 8.96 | 510.63 | 7643.77 | 4.35 | 9.54 | 1.47 | 0.48 | 15.84 | 0.001 | 0.1 | 42 | 14.9693
交流220kV | 1994-12-17 | 2013-05-13 | 18.4164 | 13.1 | 735.9 | 3313.1 | 17 | 7.6 | 4.2 | 0 | 28.8 | 0.01 | 0.23 | 58.3 | 4.5021
交流220kV | 1993-10-29 | 2012-03-29 | 18.4274 | 18.7 | 840.09 | 5528.83 | 20.8 | 23.24 | 5.07 | 0 | 49.11 | 0 | 0 | 0 | 6.5812
交流220kV | 1995-10-10 | 2014-03-11 | 18.4301 | 9.58 | 191 | 489 | 3.22 | 0.44 | 0.4 | 0 | 4.06 | 0.011 | 0 | 50 | 2.5602
交流220kV | 1994-12-28 | 2013-06-07 | 18.4548 | 1.56 | 700.13 | 3751.71 | 6.44 | 15.52 | 0.79 | 0 | 22.75 | 0.013 | 0.726 | 42.6 | 5.3586
交流220kV | 1993-10-29 | 2012-04-18 | 18.4822 | 30.26 | 840.1 | 6520.94 | 26.25 | 29.1 | 7.14 | 0 | 62.49 | 0 | 0.069 | 63.1 | 7.7621
交流220kV | 1995-06-07 | 2013-12-05 | 18.5096 | 7.4 | 181.6 | 2039.3 | 3.3 | 8.4 | 1 | 0 | 12.7 | 0 | 0 | 0 | 11.2296
交流220kV | 1994-11-10 | 2013-05-18 | 18.5315 | 19 | 1230.7 | 12417.7 | 9.3 | 132 | 5 | 0 | 146.3 | 0.021 | 0.58 | 0 | 10.0899
交流220kV | 1993-05-11 | 2011-11-30 | 18.5671 | 35.86 | 1382.78 | 7489.31 | 30.34 | 49.96 | 8.34 | 0.08 | 88.72 | 0.003 | 0.03 | 49 | 5.4161
交流220kV | 1993-05-11 | 2011-12-12 | 18.6 | 11.68 | 1119.84 | 6453.39 | 28.38 | 46.97 | 10.15 | 0 | 85.5 | 0.002 | 0.03 | 49 | 5.7628
交流220kV | 1993-12-01 | 2012-07-04 | 18.6027 | 4.25 | 166.32 | 2496.97 | 1.4 | 2.39 | 0 | 0 | 3.79 | 0.004 | 0.139 | 58.7 | 15.013
交流220kV | 1995-08-24 | 2014-04-02 | 18.6192 | 0.71 | 12.4 | 192 | 0.83 | 0.06 | 0 | 0 | 0.89 | 0 | 0 | 0 | 15.4839
交流220kV | 1993-08-18 | 2012-03-31 | 18.6301 | 5 | 417 | 4114 | 15 | 6.3 | 7.6 | 0 | 28.9 | 0.031 | 0.37 | 46 | 9.8657
交流220kV | 1994-10-21 | 2013-06-05 | 18.6356 | 15 | 555 | 5965 | 23 | 10 | 8 | 0 | 41 | 0.001 | 0.1 | 45 | 10.7477
交流220kV | 1993-09-30 | 2012-05-16 | 18.6384 | 8.2 | 756.1 | 3569.2 | 6.4 | 21.8 | 2.6 | 0 | 30.8 | 0.014 | 0 | 67.9 | 4.7205
交流220kV | 1993-11-14 | 2012-07-12 | 18.6712 | 9.2 | 1079.7 | 0 | 16.1 | 12.9 | 4.5 | 0.3 | 33.8 | 0 | 0 | 0 | 0
交流220kV | 1994-11-10 | 2013-08-13 | 18.7699 | 5.5 | 1176.9 | 9196.9 | 31.7 | 72.58 | 11.9 | 0 | 116.18 | 0 | 0 | 0 | 7.8145
交流220kV | 1992-04-01 | 2011-01-19 | 18.8137 | 4.29 | 1647.04 | 5091.29 | 29.99 | 7.74 | 4.04 | 0 | 41.77 | 0.011 | 0.005 | 52.1 | 3.0912
交流220kV | 1993-04-09 | 2012-02-22 | 18.8849 | 48 | 677 | 2949 | 24.08 | 39.05 | 5.52 | 0.09 | 68.74 | 0.001 | 0.002 | 57.8 | 4.356
交流220kV | 1993-05-11 | 2012-03-26 | 18.8877 | 13.45 | 1026.31 | 5665.46 | 27.1 | 43.91 | 9.51 | 0 | 80.52 | 0.002 | 0.2 | 47 | 5.5202
交流220kV | 1995-01-18 | 2013-12-11 | 18.9096 | 5.2 | 909.9 | 6151.2 | 15.7 | 38.8 | 4.3 | 0 | 58.8 | 0 | 0 | 0 | 6.7603
交流220kV | 1994-12-28 | 2013-12-10 | 18.9644 | 2.09 | 208.65 | 1043.33 | 11.32 | 0.5 | 3.25 | 0 | 15.07 | 0 | 0 | 0 | 5.0004
交流220kV | 1994-12-28 | 2013-12-10 | 18.9644 | 2.18 | 833.73 | 4395.74 | 8.38 | 20.4 | 1.39 | 0 | 30.17 | 0 | 0 | 0 | 5.2724
交流220kV | 1994-05-01 | 2013-04-13 | 18.9644 | 9.2 | 704.8 | 4718.5 | 13.2 | 7.5 | 3.5 | 0 | 24.2 | 0.003 | 0.05 | 54.8 | 6.6948
交流220kV | 1993-04-16 | 2012-04-01 | 18.9726 | 7.89 | 946.13 | 2966.52 | 25.46 | 13.63 | 4.92 | 0 | 44.01 | 0.009 | 2.75 | 51 | 3.1354
交流220kV | 1993-12-03 | 2012-12-07 | 19.0247 | 4.73 | 227.02 | 2806.19 | 2.72 | 6.79 | 0.84 | 0.1 | 10.45 | 0.001 | 0.1 | 40 | 12.361
交流220kV | 1993-12-01 | 2012-12-10 | 19.0384 | 3.32 | 202.37 | 2182.66 | 3.47 | 2.71 | 0.67 | 0 | 6.85 | 0 | 0 | 0 | 10.7855
交流220kV | 1991-03-01 | 2010-03-10 | 19.0384 | 20 | 1143 | 8935 | 27.88 | 18.79 | 10.62 | 0 | 57.29 | 0.001 | 0.001 | 50 | 7.8171
交流220kV | 1992-09-27 | 2011-10-12 | 19.0521 | 32 | 1489 | 8737 | 31 | 42 | 18 | 0 | 91 | 0.005 | 0.001 | 46 | 5.8677
交流220kV | 1994-10-21 | 2013-11-21 | 19.0986 | 5.38 | 534.32 | 6323.35 | 26.28 | 10.35 | 9.25 | 0 | 45.88 | 0.003 | 0.25 | 51 | 11.8344
交流220kV | 1990-12-25 | 2010-01-25 | 19.0986 | 4 | 586 | 889 | 22.4 | 2 | 4.1 | 0 | 28.5 | 0.011 | 0.003 | 53 | 1.5171
交流220kV | 1995-02-16 | 2014-03-20 | 19.1014 | 5.47 | 411.16 | 1909.1 | 10.21 | 15.66 | 3.75 | 0 | 29.62 | 0.014 | 0.45 | 68 | 4.6432
交流220kV | 1995-02-16 | 2014-03-20 | 19.1014 | 6.18 | 612.16 | 2338.02 | 4.72 | 5.85 | 1.37 | 0 | 11.94 | 0.016 | 0.84 | 64 | 3.8193
交流220kV | 1994-03-20 | 2013-04-22 | 19.1041 | 2.2 | 128 | 1270.4 | 2.4 | 21.4 | 0 | 0 | 23.8 | 0.035 | 0.114 | 45 | 9.925
交流220kV | 1995-01-25 | 2014-03-20 | 19.1616 | 8 | 338 | 1560 | 20.89 | 7.36 | 2.21 | 0 | 30.46 | 0.001 | 0.136 | 50 | 4.6154
交流220kV | 1993-03-29 | 2012-06-02 | 19.1918 | 23 | 283 | 2891 | 6.3 | 2.3 | 1.5 | 0 | 10.1 | 0.011 | 0.242 | 53.6 | 10.2155
交流220kV | 1993-09-30 | 2012-12-05 | 19.1945 | 10.5 | 757.8 | 3811.7 | 8.5 | 31.2 | 3.3 | 0 | 43 | 0 | 0 | 0 | 5.03
交流220kV | 1993-05-11 | 2012-08-06 | 19.2521 | 14.82 | 1113.78 | 6797.7 | 29.51 | 47.82 | 11.93 | 0 | 89.26 | 0.002 | 0.2 | 46 | 6.1033
交流220kV | 1994-02-01 | 2013-05-24 | 19.3205 | 11.64 | 621.9 | 5584.99 | 11.61 | 13.52 | 5.95 | 0 | 31.08 | 0.05 | 0.001 | 58 | 8.9805
交流220kV | 1993-11-12 | 2013-03-06 | 19.326 | 5.53 | 1387.34 | 5090.93 | 69.31 | 71.9 | 24.79 | 0 | 166 | 0.008 | 0.002 | 52 | 3.6696
交流220kV | 1993-11-14 | 2013-03-14 | 19.3425 | 9.9 | 1121.9 | 3133.7 | 15.1 | 3.6 | 9 | 0.3 | 28 | 0.014 | 0.1 | 53.1 | 2.7932
交流220kV | 1993-12-09 | 2013-05-31 | 19.4877 | 11.04 | 199.56 | 2402.43 | 12.62 | 10.11 | 2.66 | 0 | 25.39 | 0.01 | 0.024 | 53 | 12.0386
交流220kV | 1994-10-01 | 2014-03-26 | 19.4959 | 2.03 | 172.48 | 2112.25 | 3.59 | 20.78 | 1.32 | 0 | 25.69 | 0.012 | 0.001 | 60 | 12.2463
交流220kV | 1993-12-03 | 2013-05-29 | 19.4986 | 2.46 | 273.42 | 3133.39 | 3.72 | 7.57 | 1.26 | 0.14 | 12.69 | 0.003 | 0.1 | 43 | 11.46
交流220kV | 1993-10-29 | 2013-04-25 | 19.5014 | 22.3 | 950.55 | 9126.86 | 25.11 | 30.37 | 6.7 | 0.97 | 63.15 | 0 | 0.007 | 48.6 | 9.6017
交流220kV | 1990-11-02 | 2010-05-06 | 19.5205 | 1.83 | 1028.51 | 8775 | 53.96 | 75.79 | 19.64 | 0 | 149.39 | 0.018 | 0.04 | 68.4 | 8.5318
交流220kV | 1993-12-01 | 2013-06-06 | 19.526 | 4 | 229.28 | 2775.5 | 3.77 | 3.13 | 0.49 | 0 | 7.39 | 0.003 | 0.174 | 67.5 | 12.1053
交流220kV | 1992-11-26 | 2012-06-19 | 19.5753 | 15.13 | 981.97 | 5320 | 15.26 | 27.16 | 5.16 | 0 | 47.58 | 0.48 | 0.18 | 47 | 5.4177
交流220kV | 1993-12-23 | 2013-07-18 | 19.5808 | 7 | 1513.2 | 7866.6 | 28.4 | 14.5 | 8.8 | 0 | 51.7 | 0.008 | 0.04 | 58 | 5.1987
220 | 1994-04-01 | 2013-11-28 | 19.674 | 6.08 | 595.11 | 2471.65 | 4.93 | 15.86 | 1.92 | 0 | 22.71 | 0.009 | 0.092 | 63.6 | 4.1533
交流220kV | 1993-09-30 | 2013-06-06 | 19.6959 | 14.7 | 901.9 | 6656.6 | 9.5 | 49.2 | 4.5 | 0 | 63.2 | 0.037 | 0 | 65.1 | 7.3806
交流220kV | 1993-12-23 | 2013-09-24 | 19.7671 | 5.9 | 1364.8 | 7224.2 | 25.3 | 10.4 | 9.3 | 0 | 45 | 0 | 0 | 0 | 5.2932
交流220kV | 1992-04-01 | 2012-01-16 | 19.8055 | 6.2 | 1242 | 3603.03 | 30.89 | 5.65 | 4.05 | 0 | 40.59 | 0.011 | 0.005 | 52.8 | 2.901
交流220kV | 1993-06-14 | 2013-04-27 | 19.8822 | 34 | 229 | 2607 | 13.56 | 5.08 | 2.27 | 0 | 20.91 | 0.014 | 0.057 | 54 | 11.3843
交流220kV | 1993-05-11 | 2013-04-10 | 19.9288 | 19.51 | 998.5 | 6675.97 | 28.9 | 40.7 | 8.3 | 0 | 77.9 | 0.001 | 0.1 | 42 | 6.686
交流220kV | 1991-08-01 | 2011-07-07 | 19.9452 | 76 | 479.9 | 19312.4 | 18.7 | 8.8 | 4.7 | 0 | 32.2 | 0 | 0 | 0 | 40.2426
交流220kV | 1993-04-09 | 2013-03-21 | 19.9616 | 16 | 797 | 3722 | 25.9 | 42.05 | 5.22 | 0.06 | 73.23 | 0.004 | 0.32 | 50 | 4.67
交流220kV | 1993-11-14 | 2013-10-28 | 19.9671 | 10.5 | 1075.9 | 3831 | 15 | 8 | 4.1 | 0.1 | 27.2 | 0 | 0 | 0 | 3.5607
交流220kV | 1993-12-03 | 2013-11-20 | 19.9781 | 13.63 | 323.74 | 3068.87 | 3.83 | 9.76 | 0 | 0.11 | 13.7 | 0.002 | 0.1 | 45 | 9.4794
交流220kV | 1993-12-23 | 2013-12-13 | 19.9863 | 4.6 | 1318.3 | 6370.9 | 23.7 | 7.7 | 7.8 | 0 | 39.2 | 0 | 0 | 0 | 4.8327
交流220kV | 1991-03-01 | 2011-02-23 | 19.9973 | 12 | 1099 | 10846 | 30.54 | 20.79 | 11.76 | 0 | 63.09 | 0.001 | 0.001 | 50 | 9.869
交流220kV | 1992-01-01 | 2011-12-27 | 20 | 13 | 343 | 1869 | 17 | 13 | 4 | 0 | 34 | 0 | 0 | 0 | 5.449
交流220kV | 1993-04-16 | 2013-04-11 | 20 | 7.98 | 477.92 | 2412.41 | 14.25 | 7.07 | 2.62 | 0 | 23.94 | 0.008 | 0.097 | 59 | 5.0477
交流220kV | 1990-11-02 | 2010-11-08 | 20.0301 | 30.66 | 1031.33 | 7824.48 | 54.22 | 67.3 | 15.53 | 0 | 137.05 | 0.018 | 0.04 | 68.4 | 7.5868
交流220kV | 1993-12-01 | 2013-12-10 | 20.0384 | 3.54 | 273.15 | 2766.39 | 4.61 | 3.25 | 0.75 | 0 | 8.61 | 0 | 0 | 0 | 10.1277
交流220kV | 1991-12-01 | 2011-12-21 | 20.0685 | 3.47 | 869.51 | 3444.34 | 27.82 | 32.56 | 7.57 | 0 | 67.95 | 0 | 0 | 0 | 3.9612
交流220kV | 1993-11-14 | 2013-12-13 | 20.0932 | 6.8 | 845.5 | 3227.1 | 12 | 6.6 | 2.7 | 0 | 21.3 | 0 | 0 | 0 | 3.8168
交流220kV | 1991-12-01 | 2012-01-26 | 20.1671 | 4.61 | 669.76 | 2199.86 | 26.09 | 29.65 | 7.06 | 0 | 62.8 | 0.031 | 0 | 45 | 3.2845
交流220kV | 1993-09-30 | 2013-12-05 | 20.1945 | 9.1 | 804.8 | 4460.9 | 8.1 | 37.6 | 2.5 | 0 | 48.2 | 0 | 0 | 0 | 5.5429
交流220kV | 1992-12-24 | 2013-03-14 | 20.2329 | 7.87 | 644.58 | 4906.22 | 12.56 | 9.48 | 2.71 | 0 | 24.75 | 0.011 | 0.015 | 61.6 | 7.6115
交流220kV | 1991-09-13 | 2011-12-16 | 20.2712 | 7.5 | 689.7 | 4570 | 11.3 | 1.5 | 3.5 | 0 | 16.3 | 0 | 0 | 0 | 6.6261
交流220kV | 1992-04-27 | 2012-08-27 | 20.3479 | 6.43 | 556.36 | 3815.56 | 8.37 | 6.56 | 3.34 | 0 | 18.27 | 0.008 | 0.005 | 60 | 6.8581
交流220kV | 1993-10-29 | 2014-03-06 | 20.3644 | 25.08 | 1066.2 | 7041.88 | 27.65 | 26.09 | 5.56 | 0 | 59.3 | 0 | 0.069 | 52.2 | 6.6047
交流220kV | 1993-05-07 | 2013-09-12 | 20.3644 | 4.68 | 953.9 | 3821.25 | 15.8 | 15.63 | 1.97 | 0 | 33.4 | 0.014 | 0.22 | 59 | 4.0059
交流220kV | 1993-05-07 | 2013-09-12 | 20.3644 | 5.42 | 1029.14 | 5817.38 | 12.27 | 37.72 | 3.29 | 0 | 53.28 | 0.02 | 0.59 | 61 | 5.6527
220 | 1991-10-28 | 2012-03-07 | 20.3726 | 3.78 | 641.04 | 7802.19 | 7.86 | 28.33 | 4.26 | 0 | 40.45 | 0.021 | 0.063 | 59 | 12.1711
交流220kV | 1989-10-23 | 2010-03-04 | 20.3753 | 20 | 338 | 363 | 19.93 | 4.93 | 4.79 | 0.16 | 29.81 | 0.004 | 0.003 | 50 | 1.074
交流220kV | 1991-08-01 | 2011-12-22 | 20.4055 | 112.03 | 396.3 | 9863.81 | 18.62 | 3.71 | 7.26 | 0 | 29.59 | 0 | 0 | 39.5 | 24.8898
交流220kV | 1991-07-24 | 2011-12-16 | 20.411 | 8.5 | 603 | 3361.9 | 8.5 | 14.5 | 2.9 | 0 | 25.9 | 0 | 0 | 0 | 5.5753
交流220kV | 1993-10-20 | 2014-03-14 | 20.411 | 7.14 | 858.88 | 6040.8 | 19.85 | 46 | 12.03 | 0 | 77.88 | 0.023 | 0.103 | 65.8 | 7.0333
交流220kV | 1992-01-01 | 2012-06-05 | 20.4411 | 13 | 357 | 2172 | 19 | 15 | 5 | 0 | 39 | 0.087 | 0.9 | 52 | 6.084
220 | 1992-07-01 | 2012-12-25 | 20.4986 | 7.83 | 769.59 | 4322.72 | 8.81 | 81.74 | 6.83 | 0.4 | 97.78 | 0.019 | 0.159 | 56 | 5.6169
交流220kV | 1993-05-11 | 2013-11-27 | 20.5616 | 64.69 | 1108.35 | 12864.23 | 37.47 | 39.93 | 11.67 | 0 | 89.07 | 0.003 | 0.25 | 49 | 11.6066
交流220kV | 1991-04-01 | 2011-10-20 | 20.5671 | 27 | 1135 | 5458 | 13.5 | 11 | 3.9 | 0 | 28.4 | 0.003 | 0.001 | 60 | 4.8088
交流220kV | 1991-04-01 | 2011-10-20 | 20.5671 | 12 | 1216 | 4649 | 15.8 | 6.8 | 3.5 | 0 | 26.1 | 0.003 | 0.001 | 59 | 3.8232
交流220kV | 1991-12-01 | 2012-06-24 | 20.5781 | 4.05 | 710.35 | 3804.57 | 27.93 | 29.12 | 6.79 | 0 | 63.84 | 0.025 | 0.341 | 53 | 5.3559
交流220kV | 1991-08-01 | 2012-03-28 | 20.6712 | 101.06 | 640.44 | 14702.78 | 20.78 | 5.59 | 4.18 | 0 | 30.55 | 0 | 0 | 0 | 22.9573
220 | 1992-07-01 | 2013-03-06 | 20.6932 | 4.18 | 722.19 | 4516.28 | 8.47 | 84.5 | 6.88 | 0.47 | 100.32 | 0.022 | 0.12 | 60 | 6.2536
交流220kV | 1993-01-19 | 2013-09-25 | 20.6959 | 11 | 1102 | 5862 | 12.2 | 10.3 | 3.9 | 0.1 | 26.5 | 0.014 | 0.1 | 56 | 5.3194
交流220kV | 1990-08-05 | 2011-04-22 | 20.726 | 8.7 | 820.5 | 6336.8 | 17.2 | 27 | 5.5 | 0 | 49.7 | 0.01 | 0.001 | 51 | 7.7231
交流220kV | 1991-03-30 | 2011-12-20 | 20.7397 | 2.7 | 387.5 | 2757 | 3.6 | 10.3 | 1 | 0 | 14.9 | 0 | 0 | 0 | 7.1148
交流220kV | 1991-07-24 | 2012-05-07 | 20.8027 | 7.1 | 684 | 3674.4 | 8.7 | 15.6 | 3.2 | 0 | 27.5 | 0 | 0.06 | 60 | 5.3719
交流220kV | 1991-07-24 | 2012-05-07 | 20.8027 | 19.5 | 821 | 1849.1 | 17.6 | 1.8 | 2 | 1.4 | 22.8 | 0 | 0.07 | 60 | 2.2523
交流220kV | 1990-08-05 | 2011-06-22 | 20.8932 | 6.1 | 1296.8 | 7403.4 | 21.6 | 57.2 | 7.1 | 0.1 | 86 | 0.01 | 0.001 | 49 | 5.709
交流220kV | 1990-11-03 | 2011-09-27 | 20.9123 | 19 | 1015 | 10183 | 8.3 | 120.9 | 5.7 | 0 | 134.9 | 0 | 0 | 0 | 10.0325
交流220kV | 1992-01-01 | 2012-12-05 | 20.9425 | 12 | 340 | 1965 | 19 | 11 | 5 | 0 | 35 | 0 | 0 | 0 | 5.7794
交流220kV | 1991-08-01 | 2012-07-05 | 20.9425 | 70.46 | 396.81 | 11096.35 | 16.35 | 3.76 | 3.79 | 0 | 23.9 | 0.002 | 0 | 51.2 | 27.9639
交流220kV | 1993-04-09 | 2014-03-24 | 20.9699 | 23 | 842 | 3874 | 27.27 | 45.8 | 6.96 | 0.09 | 80.12 | 0.003 | 0.23 | 50 | 4.601
交流220kV | 1992-06-01 | 2013-05-18 | 20.9753 | 13.5 | 1139.3 | 10485.5 | 13 | 45.3 | 2.2 | 0 | 60.5 | 0.016 | 0.393 | 0 | 9.2035
交流220kV | 1991-03-01 | 2012-02-21 | 20.9918 | 32 | 1290 | 13670 | 35.62 | 24.67 | 12.36 | 0 | 72.65 | 0.001 | 0.001 | 60.8 | 10.5969
交流220kV | 1990-12-20 | 2011-12-21 | 21.0164 | 5.27 | 499.37 | 2449.92 | 4.46 | 0.31 | 2.92 | 0 | 7.69 | 0 | 0.009 | 50 | 4.906
交流220kV | 1991-12-01 | 2012-12-18 | 21.063 | 2.02 | 708 | 3768.5 | 24.28 | 24.41 | 5.34 | 0 | 54.03 | 0.032 | 0.36 | 60 | 5.3227
交流220kV | 1992-04-01 | 2013-04-24 | 21.0767 | 14.39 | 1113.24 | 5182.72 | 17.83 | 26.51 | 7.83 | 0 | 52.17 | 0.012 | 0.24 | 57.3 | 4.6555
220 | 1991-03-01 | 2012-04-23 | 21.1616 | 9.17 | 180.24 | 1986.78 | 3.87 | 4.99 | 2.87 | 0.47 | 12.2 | 0.005 | 0.81 | 51 | 11.023
交流220kV | 1992-12-24 | 2014-02-20 | 21.1726 | 8.33 | 726.71 | 4837.14 | 14.43 | 10.81 | 3.5 | 0 | 28.74 | 0.004 | 0.025 | 61.6 | 6.6562
交流220kV | 1992-06-01 | 2013-08-13 | 21.2137 | 52.3 | 913.5 | 6958.45 | 10.9 | 0 | 1.8 | 0 | 12.7 | 0 | 0 | 0 | 7.6174
交流220kV | 1991-09-13 | 2012-12-05 | 21.2438 | 9.7 | 909.1 | 5671.8 | 15.1 | 9.2 | 4.8 | 0 | 29.1 | 0 | 0 | 0 | 6.2389
交流220kV | 1990-01-20 | 2011-04-14 | 21.2438 | 4 | 738 | 2459 | 14.39 | 3.14 | 3.78 | 0 | 21.31 | 0.01 | 0.39 | 50 | 3.332
交流220kV | 1991-01-11 | 2012-04-09 | 21.2575 | 15.8 | 344.3 | 6629.5 | 26.9 | 39.7 | 8.5 | 0.3 | 75.4 | 0.006 | 0.27 | 52 | 19.255
交流220kV | 1991-12-01 | 2013-04-02 | 21.3507 | 1.86 | 257.37 | 1011.63 | 18.02 | 16.6 | 3.62 | 0 | 38.24 | 0 | 0 | 0 | 3.9306
交流220kV | 1990-11-03 | 2012-03-07 | 21.3562 | 10 | 707 | 8619 | 10 | 104 | 4.8 | 0 | 118.8 | 0 | 0 | 0 | 12.1909
220 | 1991-10-28 | 2013-03-14 | 21.3918 | 3.22 | 511.15 | 7661.21 | 7.19 | 27.43 | 4.52 | 0 | 39.14 | 0.024 | 0.078 | 55 | 14.9882
交流220kV | 1991-08-01 | 2012-12-20 | 21.4027 | 128.74 | 151 | 5471.6 | 19.34 | 5.82 | 4.79 | 0 | 29.95 | 0 | 0 | 0 | 36.2358
交流220kV | 1991-07-24 | 2012-12-13 | 21.4055 | 10.3 | 764.2 | 3623.7 | 8.2 | 18.6 | 2.5 | 0 | 29.3 | 0 | 0 | 0 | 4.7418
交流220kV | 1992-04-27 | 2013-10-12 | 21.474 | 8 | 725.47 | 3070.21 | 10.72 | 8.27 | 3.61 | 0.59 | 23.19 | 0.009 | 0.056 | 67 | 4.232
交流220kV | 1989-10-23 | 2011-04-14 | 21.4877 | 7 | 196 | 297 | 29.28 | 38.68 | 12.84 | 0 | 80.8 | 0.001 | 0.001 | 50 | 1.5153
交流220kV | 1992-01-01 | 2013-06-27 | 21.5014 | 12 | 383 | 3376 | 25 | 16 | 8 | 0 | 49 | 0.006 | 1.196 | 50 | 8.8146
交流220kV | 1990-12-20 | 2012-06-21 | 21.5178 | 1.52 | 103.06 | 2686.04 | 1.57 | 2.99 | 0.59 | 0 | 5.15 | 0 | 0 | 0 | 26.0629
交流220kV | 1992-06-01 | 2013-12-11 | 21.5425 | 3.04 | 674.18 | 8417.58 | 11.07 | 28.27 | 0 | 0 | 39.34 | 0 | 0 | 0 | 12.4857
交流220kV | 1990-11-03 | 2012-05-18 | 21.5534 | 10.32 | 1426.49 | 10003.92 | 34.24 | 75.06 | 11.95 | 0 | 121.25 | 0.021 | 0.437 | 0 | 7.013
交流220kV | 1990-05-24 | 2011-12-13 | 21.5699 | 13.57 | 454.02 | 5181.8 | 3.74 | 24.11 | 1.44 | 0 | 29.29 | 0.003 | 0.02 | 51 | 11.4132
交流220kV | 1991-09-14 | 2013-04-10 | 21.5863 | 9 | 893 | 6841 | 12.51 | 18.54 | 5.75 | 0 | 36.8 | 0.011 | 0.2 | 59 | 7.6607
交流220kV | 1991-07-24 | 2013-03-11 | 21.6466 | 7.6 | 757.4 | 3525.3 | 6.5 | 16.8 | 2.6 | 0 | 25.9 | 0.01 | 0.04 | 51.3 | 4.6545
交流220kV | 1991-07-24 | 2013-03-11 | 21.6466 | 21.7 | 826.9 | 1916.2 | 18.2 | 1.9 | 1.8 | 1.5 | 23.4 | 0 | 0.08 | 50.2 | 2.3173
交流220kV | 1992-06-30 | 2014-02-26 | 21.674 | 1.8 | 666.6 | 6106 | 15.1 | 17.6 | 6.3 | 0 | 39 | 0.004 | 0.19 | 54.8 | 9.1599
交流220kV | 1989-12-31 | 2011-08-30 | 21.6767 | 12.1 | 353.2 | 1386.5 | 25.4 | 49.6 | 6.8 | 0 | 81.8 | 0 | 0 | 0 | 3.9255
交流220kV | 1991-03-30 | 2012-12-05 | 21.7014 | 3.7 | 453.4 | 2742.6 | 3.9 | 11.6 | 1.2 | 0 | 16.7 | 0 | 0 | 0 | 6.049
交流220kV | 1991-09-13 | 2013-05-28 | 21.7205 | 8.7 | 1115.8 | 7558 | 17 | 10.5 | 5.9 | 0 | 33.4 | 0.012 | 0 | 56.6 | 6.7736
交流220kV | 1991-12-01 | 2013-08-16 | 21.7233 | 4.15 | 930.67 | 2617.65 | 29.03 | 25.64 | 4.12 | 0 | 58.79 | 0.029 | 0.36 | 42 | 2.8127
交流220kV | 1991-08-01 | 2013-06-06 | 21.863 | 86.84 | 340.46 | 10666.6 | 22.04 | 4.76 | 4.72 | 0 | 31.52 | 0 | 0 | 0 | 31.33
交流220kV | 1990-12-13 | 2012-10-28 | 21.8904 | 0.32 | 4.8 | 155.08 | 0.21 | 0.07 | 0.07 | 0 | 0.35 | 0.008 | 0.17 | 64 | 32.3083
交流220kV | 1990-01-20 | 2011-12-27 | 21.9479 | 4 | 353 | 2844 | 7 | 4 | 1 | 0 | 12 | 0 | 0 | 0 | 8.0567
交流220kV | 1992-01-01 | 2013-12-18 | 21.9781 | 12 | 376 | 2461 | 21 | 14 | 5 | 0 | 40 | 0 | 0 | 0 | 6.5452
交流220kV | 1990-12-20 | 2012-12-20 | 22.0164 | 1.5 | 82.12 | 2190.86 | 1.9 | 16.79 | 0.62 | 0 | 19.31 | 0 | 0.211 | 48 | 26.6788
交流220kV | 1989-12-24 | 2011-12-27 | 22.0219 | 13 | 867 | 3184 | 8 | 25 | 2 | 0 | 35 | 0 | 0 | 0 | 3.6724
交流220kV | 1991-12-11 | 2013-12-17 | 22.0329 | 7 | 245.7 | 3137.7 | 11.9 | 8.5 | 1.8 | 0 | 22.2 | 0.06 | 1.95 | 44 | 12.7705
220 | 1991-03-01 | 2013-03-18 | 22.063 | 3.76 | 121.54 | 979.07 | 1.96 | 3.63 | 0.78 | 0.1 | 6.47 | 0.003 | 1.97 | 54.9 | 8.0555
交流220kV | 1992-01-28 | 2014-02-17 | 22.0712 | 7.6 | 233.2 | 6170.6 | 8.9 | 1.9 | 2.3 | 0.2 | 13.3 | 0.006 | 0.001 | 41.6 | 26.4605
交流220kV | 1991-03-01 | 2013-03-22 | 22.074 | 16 | 1220 | 9753 | 39.4 | 14.53 | 27.67 | 0 | 81.6 | 0.001 | 0.12 | 49.3 | 7.9943
交流220kV | 1989-04-29 | 2011-05-24 | 22.0822 | 12.58 | 1255 | 3731 | 21.35 | 6.71 | 7.27 | 0 | 35.33 | 0.029 | 0.031 | 60 | 2.9729
交流220kV | 1990-11-03 | 2012-12-07 | 22.1096 | 8.65 | 809.62 | 8971.74 | 7.01 | 98.05 | 4.29 | 0 | 109.35 | 0 | 0 | 0 | 11.0814
交流220kV | 1989-11-04 | 2011-12-20 | 22.1397 | 4.6 | 828.1 | 5730 | 18.8 | 80.7 | 3.5 | 0 | 103 | 0 | 0 | 0 | 6.9195
交流220kV | 1989-07-30 | 2011-09-20 | 22.1562 | 8.11 | 383.64 | 3010.7 | 12.38 | 3.73 | 2.02 | 0.16 | 18.29 | 0.01 | 0.027 | 57.4 | 7.8477
交流220kV | 1991-03-30 | 2013-06-20 | 22.2411 | 4.7 | 478.4 | 4593.4 | 4.9 | 15.2 | 1.9 | 0 | 22 | 0.028 | 0 | 59.7 | 9.6016
交流220kV | 1991-09-13 | 2013-12-04 | 22.2411 | 6.3 | 978.4 | 6364.2 | 15.9 | 9.9 | 5.8 | 0 | 31.6 | 0 | 0 | 0 | 6.5047
交流220kV | 1989-12-31 | 2012-03-28 | 22.2548 | 8.2 | 377.7 | 1683.9 | 25.8 | 53.4 | 7.6 | 0 | 86.8 | 0 | 0 | 0 | 4.4583
交流220kV | 1989-09-14 | 2011-12-16 | 22.2685 | 8 | 543.8 | 5881 | 9.9 | 4.5 | 3.9 | 0 | 18.3 | 0 | 0 | 0 | 10.8146
交流220kV | 1989-12-11 | 2012-03-20 | 22.2877 | 80.89 | 1501.89 | 11554.12 | 26.14 | 70.34 | 6.97 | 0 | 103.45 | 0.017 | 0.001 | 55 | 7.6931
交流220kV | 1989-07-30 | 2011-11-10 | 22.2959 | 14.31 | 614.85 | 5281.85 | 21.44 | 6.58 | 3.5 | 0.13 | 31.65 | 0.01 | 0.048 | 60.4 | 8.5905
交流220kV | 1989-10-23 | 2012-02-22 | 22.3479 | 7 | 334 | 398 | 34.77 | 41.64 | 14.59 | 0 | 91 | 0.001 | 0.001 | 65.5 | 1.1916
交流220kV | 1987-12-28 | 2010-05-06 | 22.3699 | 24.05 | 942.55 | 4943.56 | 13.04 | 26.33 | 6.26 | 0 | 45.63 | 0.022 | 0.16 | 65.6 | 5.2449
交流220kV | 1990-01-20 | 2012-06-05 | 22.389 | 5 | 337 | 2897 | 7 | 4 | 2 | 0 | 13 | 0.09 | 0.1 | 50 | 8.5964
交流220kV | 1991-08-01 | 2013-12-20 | 22.4027 | 128.3 | 156.88 | 4375.08 | 25.2 | 0 | 5.42 | 0 | 30.62 | 0 | 0 | 65.4 | 27.8881
交流220kV | 1990-08-02 | 2012-12-27 | 22.4192 | 16.09 | 648.84 | 8081.57 | 20.69 | 45.28 | 4.1 | 0.62 | 70.69 | 0.012 | 0.003 | 59 | 12.4554
交流220kV | 1989-12-24 | 2012-05-31 | 22.4493 | 17 | 852 | 3422 | 8.8 | 29.1 | 2.6 | 0 | 40.5 | 0.051 | 0.085 | 47 | 4.0164
交流220kV | 1989-04-29 | 2011-10-18 | 22.4849 | 14.02 | 1375 | 5152 | 23.71 | 9.38 | 8.45 | 0 | 41.54 | 0.027 | 0.047 | 56.2 | 3.7469
交流220kV | 1989-12-31 | 2012-07-09 | 22.537 | 9.9 | 533.6 | 2638.3 | 27.7 | 51.3 | 7.3 | 0 | 86.3 | 0.027 | 0 | 50 | 4.9443
交流220kV | 1990-11-03 | 2013-05-18 | 22.5534 | 7 | 1369.4 | 8593.9 | 27.5 | 73.3 | 12.1 | 0 | 112.9 | 0.023 | 0.227 | 0 | 6.2757
交流220kV | 1990-06-29 | 2013-01-18 | 22.5726 | 10.54 | 1053.87 | 5358.62 | 28.03 | 7.13 | 7.01 | 0 | 42.17 | 0.013 | 0.05 | 41.8 | 5.0847
交流220kV | 1991-08-01 | 2014-02-21 | 22.5753 | 134.27 | 502.68 | 11873.53 | 26.96 | 3.37 | 5.29 | 0 | 35.62 | 0 | 0 | 0 | 23.6205
交流220kV | 1989-09-06 | 2012-04-01 | 22.5836 | 0.92 | 266.2 | 1476.75 | 11.63 | 9.01 | 3.27 | 0 | 23.91 | 0.007 | 0.024 | 57 | 5.5475
交流220kV | 1989-07-30 | 2012-02-29 | 22.6 | 7.52 | 344.85 | 3028.56 | 14.63 | 4.63 | 2.68 | 0.15 | 22.09 | 0.012 | 0.057 | 56.7 | 8.7823
交流220kV | 1989-05-13 | 2011-12-20 | 22.6192 | 11.7 | 191.9 | 5763.9 | 23.1 | 4.6 | 20.2 | 0 | 47.9 | 0 | 0 | 0 | 30.036
交流220kV | 1990-12-12 | 2013-07-24 | 22.6301 | 2.29 | 25.03 | 239.7 | 0.45 | 0.07 | 0 | 0 | 0.52 | 0.007 | 0.11 | 68 | 9.5765
交流220kV | 1991-08-01 | 2014-04-03 | 22.6877 | 178.23 | 480.15 | 12257.35 | 29.94 | 3.47 | 5.29 | 0 | 38.7 | 0 | 0 | 0 | 25.5282
交流220kV | 1991-03-30 | 2013-12-11 | 22.7178 | 5.5 | 578.7 | 3361.9 | 5 | 13.6 | 1.3 | 0 | 19.9 | 0 | 0 | 0 | 5.8094
交流220kV | 1989-06-12 | 2012-03-05 | 22.7452 | 7.2 | 228.3 | 4945.5 | 57.3 | 6.4 | 98.1 | 0 | 161.8 | 0 | 0 | 0 | 21.6623
交流220kV | 1988-12-22 | 2011-09-15 | 22.7452 | 6.36 | 906.8 | 6905.06 | 13.3 | 3.19 | 5.85 | 0 | 22.34 | 0.011 | 0.02 | 56.7 | 7.6148
交流220kV | 1990-11-03 | 2013-08-13 | 22.7918 | 10.3 | 822.6 | 9754.9 | 7.3 | 95.7 | 4.5 | 0 | 107.5 | 0 | 0 | 0 | 11.8586
交流220kV | 1990-01-20 | 2012-12-05 | 22.8904 | 4 | 338 | 2573 | 7 | 3 | 1 | 0 | 11 | 0 | 0 | 0 | 7.6124
交流220kV | 1989-04-29 | 2012-03-20 | 22.9068 | 14.38 | 1367 | 3462 | 24.9 | 7.34 | 8.83 | 0.19 | 41.26 | 0.023 | 0.03 | 54 | 2.5326
交流220kV | 1988-07-24 | 2011-07-05 | 22.9616 | 8.74 | 1047.93 | 6061.02 | 9.79 | 10.45 | 1.86 | 0.23 | 22.33 | 0 | 0 | 0 | 5.7838
交流220kV | 1989-12-24 | 2012-12-05 | 22.9644 | 27 | 857 | 3583 | 9 | 26 | 2 | 0 | 37 | 0 | 0 | 0 | 4.1809
交流220kV | 1989-05-13 | 2012-05-08 | 23.0027 | 8.2 | 146.7 | 5284.1 | 21.3 | 4.3 | 21 | 0 | 46.6 | 0.004 | 0 | 72.6 | 36.0198
交流220kV | 1989-01-18 | 2012-01-19 | 23.0164 | 14 | 29 | 1598 | 20.1 | 39.4 | 10.8 | 0 | 70.3 | 0.037 | 0.45 | 45 | 55.1034
交流220kV | 1989-06-20 | 2012-07-04 | 23.0548 | 20.47 | 553.38 | 2693 | 15.55 | 16.49 | 5.18 | 0 | 37.22 | 0.46 | 0.17 | 45 | 4.8665
交流220kV | 1990-03-23 | 2013-04-08 | 23.0603 | 3.76 | 296.29 | 2649.73 | 3.35 | 9.6 | 1.01 | 0 | 13.96 | 0.016 | 0.013 | 46 | 8.943
交流220kV | 1991-03-01 | 2014-03-19 | 23.0658 | 9 | 1016 | 7920 | 35.97 | 23.14 | 12.52 | 0 | 71.63 | 0.001 | 0.079 | 50 | 7.7953
交流220kV | 1989-06-17 | 2012-07-05 | 23.0658 | 22.07 | 1184.46 | 8699.97 | 39.73 | 67.92 | 12.12 | 0.67 | 120.44 | 0.009 | 0.12 | 50 | 7.3451
交流220kV | 1988-11-30 | 2011-12-21 | 23.0712 | 0.91 | 719.54 | 4367.27 | 19.99 | 8.61 | 4.79 | 0 | 33.39 | 0 | 0 | 0 | 6.0695
交流220kV | 1990-01-20 | 2013-02-20 | 23.1014 | 4 | 360 | 2676 | 8 | 4 | 2 | 0 | 14 | 0 | 0 | 0 | 7.4333
交流220kV | 1990-11-03 | 2013-12-11 | 23.1205 | 5.66 | 783.91 | 8831.33 | 7.81 | 86.83 | 3.58 | 0 | 98.22 | 0 | 0 | 0 | 11.2657
交流220kV | 1988-11-10 | 2011-12-20 | 23.1233 | 14.9 | 334.6 | 9250.6 | 17.4 | 2.3 | 7.5 | 0 | 27.2 | 0 | 0 | 0 | 27.6467
交流220kV | 1991-01-11 | 2014-02-26 | 23.1425 | 5.8 | 212.6 | 5786.8 | 25.6 | 41.1 | 9.2 | 0.1 | 76 | 0.003 | 0.29 | 47.6 | 27.2192
交流220kV | 1988-12-25 | 2012-02-17 | 23.1616 | 9.8 | 82 | 2482 | 2.9 | 1.2 | 0.5 | 0 | 4.6 | 0.016 | 0.001 | 44 | 30.2683
交流220kV | 1988-12-22 | 2012-02-22 | 23.1836 | 5.81 | 1018.07 | 7746.26 | 17.42 | 4.13 | 8.08 | 0 | 29.63 | 0.01 | 0.201 | 52.5 | 7.6088
交流220kV | 1989-09-14 | 2012-12-05 | 23.2411 | 8 | 686.2 | 6395.8 | 12 | 12.2 | 5.8 | 0 | 30 | 0 | 0 | 0 | 9.3206
交流220kV | 1990-08-02 | 2013-11-01 | 23.2658 | 2.49 | 171.2 | 4079.03 | 10.17 | 35.73 | 3.66 | 0.44 | 50 | 0.012 | 0.171 | 61 | 23.8261
交流220kV | 1987-12-28 | 2011-04-06 | 23.2877 | 29.32 | 950.49 | 9596.65 | 20.64 | 33.42 | 9.18 | 0 | 63.24 | 0.022 | 0.16 | 65.6 | 10.0965
交流220kV | 1988-10-24 | 2012-02-17 | 23.3315 | 11.6 | 171 | 2901 | 3.8 | 4.8 | 1 | 0 | 9.6 | 0.022 | 0.007 | 46 | 16.9649
交流220kV | 1988-12-02 | 2012-03-29 | 23.337 | 21.46 | 818.68 | 4415.82 | 26.47 | 22.63 | 9.53 | 0 | 58.63 | 0.013 | 0.076 | 53 | 5.3938
交流220kV | 1988-11-30 | 2012-03-31 | 23.3479 | 1.68 | 1668.2 | 11258.02 | 21.68 | 7.75 | 4.48 | 0 | 33.91 | 0.02 | 0.33 | 57 | 6.7486
交流220kV | 1987-12-29 | 2011-05-13 | 23.3863 | 3 | 560 | 2425 | 12.89 | 8.77 | 4.22 | 0 | 25.88 | 0.014 | 0.078 | 53 | 4.3304
交流220kV | 1989-10-23 | 2013-03-07 | 23.3863 | 4 | 392 | 899 | 33.6 | 37.37 | 14.11 | 0 | 85.08 | 0.001 | 0.052 | 50 | 2.2934
交流220kV | 1988-07-24 | 2011-12-17 | 23.4137 | 16.02 | 835.41 | 4585.2 | 7.12 | 13.04 | 2.38 | 0.38 | 22.92 | 0 | 0 | 0 | 5.4886
交流220kV | 1989-12-31 | 2013-05-29 | 23.4247 | 9 | 398 | 2150.7 | 24.5 | 45.5 | 6.9 | 0 | 76.9 | 0 | 0 | 0 | 5.4038
交流220kV | 1990-01-20 | 2013-06-27 | 23.4493 | 4 | 410 | 3428 | 8 | 4 | 2 | 0 | 14 | 0.089 | 0.069 | 45 | 8.361
交流220kV | 1988-11-10 | 2012-05-08 | 23.5068 | 16.1 | 361 | 9359.9 | 16.5 | 1.9 | 6.7 | 0 | 25.1 | 0.003 | 0 | 54.6 | 25.9277
交流220kV | 1989-12-24 | 2013-06-27 | 23.5233 | 20 | 459 | 2562 | 6 | 5 | 2 | 0 | 13 | 0.003 | 0.127 | 52 | 5.5817
交流220kV | 1989-05-13 | 2012-12-05 | 23.5808 | 131 | 209.2 | 6225.9 | 31.1 | 5 | 26.8 | 0 | 62.9 | 0 | 0 | 0 | 29.7605
交流220kV | 1988-11-30 | 2012-06-24 | 23.5808 | 2.1 | 732.22 | 4609.49 | 20.7 | 7.78 | 4.95 | 0 | 33.43 | 0.025 | 0.315 | 60 | 6.2952
220 | 1988-08-08 | 2012-03-07 | 23.5945 | 7.35 | 1028.99 | 7694.13 | 23.47 | 21.7 | 11.29 | 0 | 56.46 | 0.026 | 0.053 | 56 | 7.4774
交流220kV | 1988-12-25 | 2012-08-22 | 23.674 | 8 | 44 | 2096 | 2 | 1 | 0.7 | 0 | 3.7 | 0.016 | 0 | 40.3 | 47.6364
交流220kV | 1989-09-14 | 2013-05-28 | 23.7178 | 5.5 | 590.2 | 6200.7 | 9.1 | 12.1 | 5.5 | 0 | 26.7 | 0.011 | 0 | 60.4 | 10.5061
交流220kV | 1988-10-24 | 2012-08-22 | 23.8438 | 10 | 149 | 3381 | 4 | 5 | 1 | 0 | 10 | 0.021 | 0.001 | 47 | 22.6913
交流220kV | 1989-06-17 | 2013-04-16 | 23.8466 | 26.34 | 1417.99 | 9438.27 | 49.73 | 72.42 | 14.29 | 0.28 | 136.72 | 0.009 | 0.05 | 52 | 6.6561
交流220kV | 1990-01-20 | 2013-12-18 | 23.926 | 3 | 410 | 3676 | 9 | 6 | 2 | 0 | 17 | 0 | 0 | 0 | 8.9659
交流220kV | 1989-12-31 | 2013-12-17 | 23.9781 | 8.9 | 504.7 | 2516.7 | 26.7 | 44.2 | 6.5 | 0 | 77.4 | 0.07 | 2.8 | 45 | 4.9865
交流220kV | 1988-07-24 | 2012-07-17 | 23.9973 | 10.51 | 1057.8 | 5233 | 11.54 | 14.46 | 2.59 | 0.28 | 28.87 | 0.009 | 0.154 | 45 | 4.9471
交流220kV | 1989-12-24 | 2013-12-17 | 23.9973 | 46 | 799 | 3843 | 12 | 28 | 4 | 0 | 44 | 0 | 0 | 0 | 4.8098
交流220kV | 1988-12-22 | 2013-01-14 | 24.0795 | 4.22 | 595.12 | 5841.15 | 13.89 | 3.53 | 7.33 | 0 | 24.75 | 0.013 | 0.084 | 52.6 | 9.8151
交流220kV | 1988-11-10 | 2012-12-05 | 24.0849 | 47.1 | 336.1 | 8681.5 | 33 | 8.9 | 8.4 | 0 | 50.3 | 0 | 0 | 0 | 25.8301
交流220kV | 1988-11-30 | 2013-01-07 | 24.1205 | 1.77 | 727.67 | 5179.4 | 19.32 | 6.3 | 3.59 | 0 | 29.21 | 0.011 | 0.35 | 60 | 7.1178
交流220kV | 1987-06-29 | 2011-09-15 | 24.2301 | 0.87 | 57.79 | 1230.14 | 35.55 | 79.18 | 26.67 | 0.13 | 141.53 | 0.01 | 0.856 | 59.7 | 21.2864
交流220kV | 1989-09-14 | 2013-12-04 | 24.2384 | 6.7 | 662.7 | 6053.2 | 9.3 | 14.4 | 5.8 | 0 | 29.5 | 0 | 0 | 0 | 9.1341
交流220kV | 1987-12-17 | 2012-04-01 | 24.3068 | 1.01 | 165.6 | 1380.94 | 6.86 | 1.07 | 1.97 | 0 | 9.9 | 0.014 | 0.045 | 57 | 8.339
交流220kV | 1988-12-25 | 2013-04-29 | 24.3589 | 12 | 30 | 1766 | 3 | 1.5 | 1 | 0 | 5.5 | 0.016 | 0.001 | 46 | 58.8667
交流220kV | 1988-10-13 | 2013-03-06 | 24.411 | 8 | 208 | 1113 | 7.8 | 2.98 | 0.4 | 0.12 | 11.3 | 0.015 | 0.115 | 52.4 | 5.351
交流220kV | 1987-11-11 | 2012-04-06 | 24.4192 | 7.59 | 358 | 2076 | 3.19 | 3.68 | 0.47 | 0.07 | 7.41 | 0.015 | 0.27 | 57 | 5.7989
交流220kV | 1988-07-24 | 2012-12-31 | 24.4548 | 11.78 | 797.47 | 3411.13 | 5.66 | 10.85 | 1.92 | 0.18 | 18.61 | 0 | 0 | 0 | 4.2774
交流220kV | 1987-03-03 | 2011-08-13 | 24.463 | 16.5 | 584.3 | 7685.8 | 34.2 | 33.7 | 10.9 | 0 | 78.8 | 0.018 | 0.07 | 53.8 | 13.1539
220 | 1988-10-01 | 2013-03-18 | 24.4767 | 5.05 | 369.15 | 2027.8 | 5.35 | 7.46 | 1.76 | 0.14 | 14.71 | 0.003 | 1.88 | 57.8 | 5.4932
交流220kV | 1988-10-24 | 2013-04-29 | 24.5288 | 12 | 94 | 3562 | 4 | 6 | 1.7 | 0 | 11.7 | 0.021 | 0.001 | 48.2 | 37.8936
交流220kV | 1987-11-10 | 2012-05-15 | 24.5288 | 13.84 | 184.8 | 2429.23 | 13.17 | 7.58 | 6.71 | 0 | 27.46 | 0.03 | 0 | 60 | 13.1452
220 | 1988-08-08 | 2013-03-14 | 24.6137 | 4.21 | 950.02 | 7761.21 | 23.56 | 17.84 | 10.2 | 0 | 51.6 | 0.016 | 0.095 | 58 | 8.1695
交流220kV | 1987-06-29 | 2012-02-22 | 24.6685 | 7.25 | 314.69 | 1518.54 | 100.57 | 141.49 | 40.08 | 0 | 282.14 | 0.01 | 0.394 | 53.1 | 4.8255
交流220kV | 1987-06-29 | 2012-03-08 | 24.7096 | 5.11 | 236.83 | 1414.43 | 83.51 | 116.6 | 32.99 | 0 | 233.1 | 0.011 | 0.578 | 49.8 | 5.9723
交流220kV | 1988-11-30 | 2013-08-16 | 24.726 | 3.38 | 775.3 | 2724.39 | 24.28 | 5.24 | 4.25 | 0 | 33.77 | 0.037 | 0.35 | 40 | 3.514
交流220kV | 1988-05-31 | 2013-03-06 | 24.7808 | 12.1 | 159.85 | 1980.78 | 15.63 | 24.28 | 16.34 | 0 | 56.25 | 0.008 | 0.07 | 46.4 | 12.3915
交流220kV | 1988-07-24 | 2013-06-08 | 24.8904 | 11.68 | 837.62 | 4125.04 | 7.93 | 2.4 | 13.12 | 0.2 | 23.65 | 0 | 0 | 0 | 4.9247
交流220kV | 1988-12-25 | 2014-03-16 | 25.2384 | 8.5 | 39.5 | 2506 | 3.1 | 4.2 | 0.5 | 0 | 7.8 | 0.016 | 0 | 47 | 63.443
交流220kV | 1988-10-24 | 2014-03-16 | 25.4082 | 12.8 | 57 | 2750 | 4 | 1.4 | 1 | 0 | 6.4 | 0.021 | 0.001 | 49 | 48.2456
交流220kV | 1987-11-11 | 2013-04-08 | 25.4247 | 6.15 | 489.98 | 2783.1 | 4.28 | 3.62 | 0.33 | 0.06 | 8.29 | 0.018 | 0.12 | 45 | 5.68
交流220kV | 1988-07-24 | 2013-12-30 | 25.4521 | 12.03 | 1141.03 | 5388.33 | 10.27 | 19.78 | 3.33 | 0.19 | 33.57 | 0 | 0 | 0 | 4.7223
交流220kV | 1987-11-10 | 2013-05-21 | 25.5452 | 3.39 | 134.28 | 2622.04 | 15.36 | 7.87 | 15.36 | 0 | 38.59 | 0.04 | 0.001 | 60 | 19.5267
交流220kV | 1987-06-29 | 2013-01-11 | 25.5562 | 4.81 | 221.51 | 1659.93 | 91.15 | 137.39 | 48.75 | 0 | 277.29 | 0.013 | 0.116 | 47.1 | 7.4937
交流220kV | 1986-08-25 | 2012-05-16 | 25.7425 | 113.08 | 1325.29 | 14850.11 | 135.43 | 229.5 | 37.83 | 0.35 | 403.11 | 0.019 | 0.001 | 53.08 | 11.2052
交流220kV | 1987-05-28 | 2013-03-06 | 25.7918 | 11.24 | 181.9 | 2112.07 | 16.29 | 15.73 | 16.06 | 0 | 48.08 | 0.008 | 0.06 | 42 | 11.6112
交流220kV | 1985-07-23 | 2011-05-17 | 25.8329 | 20.78 | 1195 | 3610 | 28.96 | 24.44 | 16.58 | 0.25 | 70.23 | 0.032 | 0.126 | 57.6 | 3.0209
交流220kV | 1987-06-30 | 2013-06-05 | 25.9507 | 3.6 | 248 | 3187.7 | 3.4 | 7.4 | 0 | 0 | 10.8 | 0.023 | 0.323 | 0 | 12.8536
220 | 1986-08-12 | 2012-09-20 | 26.126 | 7.41 | 1004.09 | 6052.4 | 18.16 | 31.94 | 4.58 | 0.19 | 54.87 | 0.075 | 0.188 | 56 | 6.0277
交流220kV | 1986-04-05 | 2012-05-30 | 26.1699 | 6.5 | 529 | 6108 | 10.9 | 3.5 | 3.6 | 0 | 18 | 0.009 | 0 | 64.5 | 11.5463
交流220kV | 1986-04-05 | 2012-06-15 | 26.2137 | 6.5 | 529 | 6108 | 10.9 | 3.5 | 3.6 | 0 | 18 | 0.008 | 0 | 64.5 | 11.5463
交流220kV | 1985-07-23 | 2011-10-18 | 26.2548 | 18.49 | 1172 | 4258 | 30.19 | 29.85 | 20.44 | 0.31 | 80.79 | 0.026 | 0.129 | 54.3 | 3.6331
220 | 1985-12-15 | 2012-03-13 | 26.2603 | 28.84 | 13.32 | 468.94 | 20.08 | 1.03 | 2.52 | 0 | 23.63 | 0.008 | 0 | 60 | 35.2057
220 | 1985-07-01 | 2011-11-03 | 26.3589 | 33.72 | 1025.46 | 5665.65 | 11.95 | 15.57 | 2.52 | 0 | 30.04 | 0.008 | 0.068 | 67.2 | 5.525
交流220kV | 1987-06-30 | 2013-12-12 | 26.4712 | 4.5 | 355.6 | 3619.1 | 4.3 | 7.5 | 0 | 0 | 11.8 | 0 | 0 | 0 | 10.1774
交流220kV | 1984-12-29 | 2011-07-07 | 26.537 | 19.1 | 467.7 | 13188.5 | 20.3 | 2.6 | 4.7 | 0 | 27.6 | 0 | 0 | 0 | 28.1986
220 | 1986-08-12 | 2013-03-06 | 26.5836 | 4.74 | 976.32 | 5314.04 | 18.94 | 32.74 | 5.43 | 0.21 | 57.32 | 0.031 | 0.168 | 55 | 5.4429
交流220kV | 1985-12-02 | 2012-07-02 | 26.6 | 0.81 | 0.9 | 103.09 | 0.37 | 0.08 | 0.14 | 0 | 0.59 | 0.007 | 0.01 | 70.5 | 114.5444
交流220kV | 1985-07-23 | 2012-03-20 | 26.6767 | 15.6 | 1075 | 3299 | 27.57 | 27.02 | 18.31 | 0.25 | 73.15 | 0.021 | 0.095 | 54 | 3.0688
交流220kV | 1986-04-05 | 2012-12-05 | 26.6877 | 5.9 | 458.2 | 5479.2 | 11.6 | 3.1 | 3.4 | 0 | 18.1 | 0 | 0 | 0 | 11.9581
交流220kV | 1985-07-23 | 2012-05-31 | 26.874 | 16.01 | 1133 | 3822 | 29.26 | 27.8 | 18.44 | 0.25 | 75.75 | 0.024 | 0.087 | 61.2 | 3.3733
交流220kV | 1984-12-29 | 2011-12-22 | 26.9973 | 20.48 | 533.96 | 8051.92 | 19.82 | 2.43 | 1.57 | 0.22 | 24.04 | 0 | 0 | 47.2 | 15.0796
交流220kV | 1985-07-01 | 2012-07-04 | 27.0274 | 12.34 | 1166.4 | 6164.63 | 15.98 | 7.29 | 3.47 | 0 | 26.74 | 0.004 | 0.061 | 51.5 | 5.2852
交流220kV | 1984-01-28 | 2011-02-20 | 27.0822 | 20.11 | 549.03 | 6839.11 | 21.03 | 25.12 | 4.6 | 0 | 50.75 | 0.002 | 0.03 | 46 | 12.4567
交流220kV | 1986-04-05 | 2013-06-04 | 27.1836 | 11.1 | 563 | 8866.1 | 16.5 | 4.2 | 6.6 | 0 | 27.3 | 0.011 | 0 | 47.3 | 15.748
交流220kV | 1984-12-29 | 2012-03-28 | 27.263 | 17.48 | 723.31 | 12341.03 | 22.18 | 1.88 | 2.98 | 0 | 27.04 | 0 | 0 | 0 | 17.0619
交流220kV | 1984-05-09 | 2011-08-13 | 27.2795 | 6.1 | 13.5 | 659.2 | 20.5 | 109.8 | 6.5 | 0.3 | 137.1 | 0.021 | 0.09 | 51.3 | 48.8296
交流220kV | 1985-07-01 | 2012-12-10 | 27.463 | 3.88 | 871.8 | 5140.91 | 13.65 | 6.32 | 3.04 | 0 | 23.01 | 0 | 0 | 0 | 5.8969
交流220kV | 1984-12-29 | 2012-07-05 | 27.5342 | 17.79 | 759.15 | 11319.72 | 0 | 1.61 | 2.78 | 0 | 0 | 0.024 | 0 | 50.2 | 14.911
交流220kV | 1984-01-28 | 2011-08-20 | 27.5781 | 20.36 | 549.51 | 6860.91 | 21.09 | 25.13 | 4.6 | 0 | 50.82 | 0.002 | 0.02 | 48 | 12.4855
交流220kV | 1986-04-05 | 2013-12-11 | 27.7041 | 11.5 | 670 | 7620.9 | 19.2 | 4.9 | 4.8 | 0 | 28.9 | 0 | 0 | 0 | 11.3745
交流220kV | 1984-01-28 | 2011-12-19 | 27.9096 | 20.97 | 938.85 | 10362.89 | 26.78 | 32.13 | 7.3 | 0.12 | 66.33 | 0.002 | 0.03 | 43 | 11.0379
交流220kV | 1985-07-01 | 2013-06-06 | 27.9507 | 3.64 | 868.16 | 5177.09 | 13.46 | 6.23 | 2.89 | 0 | 22.58 | 0.006 | 0.123 | 62.4 | 5.9633
交流220kV | 1984-12-29 | 2012-12-20 | 27.9945 | 9 | 178.6 | 3915.85 | 16.57 | 2.77 | 2.72 | 0.2 | 22.26 | 0 | 0 | 0 | 21.9253
交流220kV | 1984-01-28 | 2012-03-09 | 28.1315 | 19.48 | 821.34 | 9811.75 | 25.58 | 30.88 | 8.07 | 0 | 64.53 | 0.003 | 0.25 | 48 | 11.946
交流220kV | 1983-06-28 | 2011-08-20 | 28.1644 | 7.79 | 565.98 | 8156.23 | 21.03 | 29.36 | 6.19 | 0 | 56.58 | 0.003 | 0.03 | 46 | 14.4108
220 | 1985-07-01 | 2013-11-28 | 28.4301 | 6.11 | 1396.05 | 6503.42 | 16.1 | 18.95 | 3.76 | 0 | 38.81 | 0.016 | 0.063 | 60.4 | 4.6584
交流220kV | 1982-12-01 | 2011-05-03 | 28.4384 | 2 | 12.6 | 763 | 0.5 | 1.9 | 0 | 0 | 2.4 | 0 | 0 | 0 | 60.5556
交流220kV | 1982-12-01 | 2011-05-09 | 28.4548 | 2.4 | 20 | 776 | 0.6 | 2.2 | 0 | 0 | 2.8 | 0 | 0 | 0 | 38.8
交流220kV | 1984-12-29 | 2013-06-06 | 28.4548 | 14.1 | 486.63 | 9459.97 | 20.59 | 3.39 | 2.81 | 0.27 | 27.06 | 0 | 0 | 0 | 19.4398
交流220kV | 1985-07-01 | 2013-12-10 | 28.463 | 3.98 | 1027.46 | 6072.12 | 14.86 | 6.46 | 3.39 | 0 | 24.71 | 0 | 0 | 0 | 5.9098
交流220kV | 1982-12-01 | 2011-05-15 | 28.4712 | 2.3 | 19 | 789 | 0.7 | 2.4 | 0 | 0 | 3.1 | 0 | 0 | 0 | 41.5263
交流220kV | 1983-06-28 | 2011-12-19 | 28.4959 | 4.1 | 886.27 | 9013.06 | 24.57 | 34.32 | 8.37 | 0.13 | 67.39 | 0.001 | 0.03 | 43 | 10.1697
交流220kV | 1982-12-01 | 2011-06-05 | 28.5288 | 2.3 | 22 | 778 | 1.3 | 2.9 | 0 | 0 | 4.2 | 0 | 0 | 0 | 35.3636
交流220kV | 1983-06-28 | 2012-03-09 | 28.7178 | 8.42 | 855.93 | 9048.32 | 25.71 | 34.67 | 8.81 | 0 | 69.19 | 0.002 | 0.25 | 49 | 10.5713
交流220kV | 1984-01-28 | 2012-12-07 | 28.8795 | 28.77 | 948.69 | 10747.48 | 28.27 | 32.42 | 7.23 | 0 | 67.92 | 0.001 | 0.2 | 42 | 11.3288
交流220kV | 1984-12-29 | 2013-12-20 | 28.9945 | 12.23 | 223.03 | 3448.93 | 20.79 | 1.33 | 2.68 | 0 | 24.8 | 0 | 0 | 66.2 | 15.464
交流220kV | 1982-12-01 | 2011-12-13 | 29.0521 | 2 | 156 | 1620 | 2.3 | 3.6 | 0 | 0 | 5.9 | 0.056 | 0 | 0 | 10.3846
交流220kV | 1984-11-01 | 2013-12-05 | 29.1123 | 16.9 | 212.7 | 2846.4 | 14 | 21.8 | 3.5 | 0 | 39.3 | 0 | 0 | 0 | 13.3822
交流220kV | 1984-01-28 | 2013-05-20 | 29.3288 | 24.64 | 957.89 | 11469.59 | 29.39 | 33.77 | 6.93 | 0 | 70.09 | 0.003 | 0.2 | 42 | 11.9738
交流220kV | 1982-12-01 | 2012-04-20 | 29.4055 | 7.47 | 381.4 | 3196.6 | 4.67 | 7.1 | 1.54 | 0 | 13.31 | 0.012 | 0 | 0 | 8.3812
交流220kV | 1983-06-28 | 2012-12-07 | 29.4658 | 8.67 | 975.53 | 10201.2 | 28.05 | 36.07 | 8.95 | 0 | 73.07 | 0.002 | 0.1 | 41 | 10.4571
交流220kV | 1984-01-28 | 2013-11-26 | 29.8493 | 44.76 | 948.88 | 11452.29 | 29.81 | 33.61 | 5.51 | 0 | 68.93 | 0.002 | 0.1 | 41 | 12.0693
交流220kV | 1983-06-28 | 2013-05-20 | 29.9151 | 4.57 | 831.81 | 10282.73 | 27.63 | 35.82 | 8.19 | 0 | 71.64 | 0.002 | 0.2 | 43 | 12.3619
交流220kV | 1981-07-01 | 2011-06-21 | 29.9918 | 32.5 | 658.4 | 15054 | 24.4 | 60.2 | 8.3 | 0 | 92.9 | 0.03 | 0 | 63.2 | 22.8645
交流220kV | 1982-12-01 | 2012-12-14 | 30.0575 | 14.3 | 828.41 | 7989.19 | 15.43 | 37.11 | 3.37 | 0 | 55.91 | 0 | 0 | 0 | 9.644
交流220kV | 1984-01-28 | 2014-03-10 | 30.1342 | 45.41 | 975.76 | 11275.71 | 30.59 | 33.58 | 4.94 | 0 | 69.11 | 0.003 | 0.025 | 51 | 11.5558
交流220kV | 1981-07-01 | 2011-09-01 | 30.189 | 9.8 | 612.7 | 4586.7 | 11.5 | 35.3 | 3.2 | 0 | 50 | 0 | 0 | 0 | 7.486
交流220kV | 1981-07-01 | 2011-09-01 | 30.189 | 8.9 | 570.2 | 4142.3 | 10.5 | 32.7 | 2.9 | 0 | 46.1 | 0 | 0 | 0 | 7.2646
交流220kV | 1983-06-28 | 2013-11-26 | 30.4356 | 5.03 | 833.31 | 9984.15 | 26.85 | 35.35 | 6.97 | 0 | 69.17 | 0.002 | 0.1 | 41 | 11.9813
交流220kV | 1981-07-01 | 2011-12-16 | 30.4795 | 4.8 | 459.9 | 4836 | 11.9 | 44.4 | 3.4 | 0 | 59.7 | 0 | 0 | 0 | 10.5153
交流220kV | 1982-12-01 | 2013-05-18 | 30.4822 | 8.7 | 874.2 | 7118.2 | 10.5 | 14.4 | 0 | 0 | 24.9 | 0.015 | 0.225 | 0 | 8.1425
交流220kV | 1983-06-28 | 2014-03-10 | 30.7205 | 11.46 | 625.67 | 7734.18 | 20.26 | 29.89 | 5.04 | 0 | 55.19 | 0.002 | 0.025 | 53 | 12.3614
交流220kV | 1982-12-01 | 2013-08-13 | 30.7205 | 46 | 72.58 | 6822.7 | 10.8 | 12.4 | 0 | 0 | 23.2 | 0 | 0 | 0 | 94.0025
220 | 1980-04-10 | 2012-05-09 | 32.1014 | 3.5 | 284.23 | 3670.16 | 10.47 | 12.7 | 3.32 | 1.13 | 27.62 | 0.009 | 0.001 | 56 | 12.9126
220 | 1979-04-01 | 2014-03-10 | 34.9644 | 2.78 | 649.97 | 6364.25 | 38.9 | 81.98 | 11.47 | 1.7 | 134.05 | 0.093 | 0.396 | 54.2 | 9.7916

## 1-330kV
Voltage | Inservice time | Test time | Year-of-test | H2(μL/L) | CO(μL/L) | CO2(μL/L) | CH4(μL/L) | C2H4(μL/L) | C2H6(μL/L) | C2H2(μL/L) | total consub(μL/L) | Acid (mgKOH/g) | PF(90℃)(%) | Breakdown voltage(kV) | CO/CO2
交流330kV | 1994-12-30 | 1994-12-30 | 0 | 3.51 | 35.6 | 124.2 | 0.26 | 0 | 0 | 0 | 0.26 | 0.012 | 0.049 | 62 | 3.4888
交流330kV | 1994-12-30 | 1994-12-30 | 0 | 2.88 | 51.3 | 154.2 | 0.46 | 0 | 0 | 0 | 0.46 | 0.018 | 0.056 | 64.8 | 3.0058
交流330kV | 2010-09-30 | 2010-10-09 | 0.024658 | 0.88 | 20.04 | 363.98 | 0.65 | 0.33 | 0 | 0 | 0.98 | 0.02 | 0.078 | 60.8 | 18.1627
交流330kV | 2005-12-30 | 2006-01-11 | 0.032877 | 6.17 | 10.31 | 66.03 | 0.26 | 0 | 2.08 | 0 | 2.34 | 0.005 | 0.108 | 58.6 | 6.4045
交流330kV | 2005-12-30 | 2006-01-11 | 0.032877 | 2.89 | 6.98 | 71.35 | 0.19 | 0 | 0 | 0 | 0.19 | 0.005 | 0.107 | 60.5 | 10.2221
交流330kV | 2004-12-26 | 2005-01-13 | 0.049315 | 1.82 | 19.37 | 124.69 | 0.69 | 0 | 0 | 0 | 0.69 | 0.014 | 0.128 | 62.8 | 6.4373
交流330kV | 2005-03-03 | 2005-03-29 | 0.071233 | 2.49 | 12.23 | 131.55 | 0.48 | 0.62 | 1.55 | 0 | 2.65 | 0.02 | 0.124 | 55.1 | 10.7563
交流330kV | 2006-12-18 | 2007-01-22 | 0.09589 | 3.8 | 19.91 | 201.85 | 0.45 | 0 | 0 | 0 | 0.45 | 0.02 | 0.125 | 53.2 | 10.1381
交流330kV | 2010-09-30 | 2010-11-05 | 0.09863 | 0.21 | 35.2 | 183.14 | 0.28 | 0.35 | 0 | 0 | 0.63 | 0.028 | 0.223 | 65.9 | 5.2028
交流330kV | 2008-09-05 | 2009-01-05 | 0.33425 | 4.22 | 73.42 | 222.18 | 1.25 | 0 | 0 | 0 | 1.25 | 0.026 | 0.268 | 56.1 | 3.0262
交流330kV | 2008-09-05 | 2009-01-05 | 0.33425 | 4.71 | 83.86 | 137.59 | 1.6 | 0.14 | 0 | 0 | 1.74 | 0.019 | 0.165 | 53.6 | 1.6407
交流330kV | 2010-04-08 | 2010-08-12 | 0.34521 | 16.39 | 150.55 | 362.39 | 1.55 | 0.32 | 0.22 | 0 | 2.09 | 0.007 | 0.07 | 65.3 | 2.4071
交流330kV | 2010-04-08 | 2010-08-12 | 0.34521 | 24.58 | 160.79 | 325.01 | 1.59 | 0.28 | 0.25 | 0 | 2.12 | 0.009 | 0.084 | 66.3 | 2.0213
交流330kV | 2010-04-08 | 2010-08-13 | 0.34795 | 16.39 | 150.55 | 362.39 | 1.55 | 0.32 | 0.22 | 0 | 2.09 | 0.007 | 0.07 | 65.3 | 2.4071
交流330kV | 2010-04-08 | 2010-08-13 | 0.34795 | 24.58 | 160.79 | 325.01 | 1.59 | 0.28 | 0.25 | 0 | 2.12 | 0.009 | 0.084 | 66.3 | 2.0213
交流330kV | 2005-12-30 | 2006-06-05 | 0.43014 | 24.92 | 63.1 | 171.06 | 0.87 | 0 | 0 | 0 | 0.87 | 0.005 | 0.136 | 52.2 | 2.7109
交流330kV | 2005-12-30 | 2006-06-07 | 0.43562 | 30.53 | 60.46 | 158.88 | 1.7 | 0 | 0 | 0 | 1.7 | 0.005 | 0.198 | 51.2 | 2.6279
交流330kV | 2008-09-05 | 2009-03-04 | 0.49315 | 4.71 | 83.86 | 237.59 | 1.6 | 0.01 | 0.14 | 0 | 1.75 | 0.019 | 0.165 | 53.6 | 2.8332
交流330kV | 2009-11-06 | 2010-08-25 | 0.8 | 9.52 | 136.76 | 374.77 | 2.58 | 0.54 | 1.43 | 0 | 4.55 | 0.013 | 0.172 | 61.3 | 2.7403
交流330kV | 2013-04-21 | 2014-04-02 | 0.94795 | 4.33 | 61.59 | 159.34 | 0.95 | 0 | 0.2 | 0 | 1.15 | 0.034 | 0.199 | 60.4 | 2.5871
交流330kV | 2006-12-18 | 2008-02-28 | 1.1973 | 10.42 | 101.65 | 415.23 | 1.6 | 1.26 | 1.57 | 0 | 4.43 | 0.027 | 0.093 | 50.4 | 4.0849
交流330kV | 2012-06-22 | 2013-09-02 | 1.1973 | 5.1 | 110.63 | 367.23 | 1.64 | 0.28 | 0.2 | 0 | 2.12 | 0.018 | 0.001 | 59.6 | 3.3194
交流330kV | 2012-06-22 | 2013-09-02 | 1.1973 | 4.77 | 98.12 | 374.75 | 1.51 | 0.29 | 0.45 | 0 | 2.25 | 0.018 | 0.001 | 58.4 | 3.8193
交流330kV | 2004-12-26 | 2006-03-31 | 1.2603 | 9.98 | 197.52 | 397.97 | 2.48 | 0 | 0 | 0 | 2.48 | 0.02 | 0.125 | 53.2 | 2.0148
交流330kV | 2010-11-12 | 2012-03-16 | 1.3425 | 10 | 119 | 350 | 0.7 | 0.6 | 0 | 0 | 1.3 | 0.004 | 0.001 | 59 | 2.9412
交流330kV | 2011-07-25 | 2012-12-06 | 1.3699 | 2.44 | 25.67 | 260.21 | 1.97 | 0.93 | 0.9 | 0 | 3.8 | 0.005 | 0.048 | 60.2 | 10.1367
交流330kV | 2011-07-25 | 2012-12-06 | 1.3699 | 2.88 | 28.47 | 89.32 | 1.58 | 0.31 | 0.65 | 0 | 2.54 | 0.002 | 0.043 | 60.8 | 3.1373
交流330kV | 2010-09-30 | 2012-02-29 | 1.4164 | 8.44 | 328.88 | 907.91 | 4.62 | 12.15 | 0.6 | 0 | 17.37 | 0.029 | 0.359 | 61.2 | 2.7606
交流330kV | 2010-09-30 | 2012-02-29 | 1.4164 | 5.83 | 505.13 | 869.34 | 3.46 | 8.58 | 0.48 | 0 | 12.52 | 0.024 | 0.169 | 57.9 | 1.721
交流330kV | 2010-09-30 | 2012-03-01 | 1.4192 | 5.83 | 505.13 | 869.34 | 3.46 | 8.58 | 0.48 | 0 | 12.52 | 0.024 | 0.169 | 57.9 | 1.721
交流330kV | 2010-09-30 | 2012-03-01 | 1.4192 | 8.44 | 328.88 | 907.91 | 4.62 | 12.15 | 0.6 | 0 | 17.37 | 0.042 | 0.359 | 61.2 | 2.7606
交流330kV | 2008-09-05 | 2010-03-16 | 1.526 | 9.43 | 84.28 | 152.13 | 2.02 | 0.41 | 0.38 | 0 | 2.81 | 0.017 | 0.185 | 57.6 | 1.8051
交流330kV | 2008-09-05 | 2010-03-16 | 1.526 | 10.64 | 130.81 | 189.88 | 2.5 | 6.2 | 2.61 | 0 | 11.31 | 0.029 | 0.166 | 47.6 | 1.4516
交流330kV | 2010-08-03 | 2012-03-16 | 1.6192 | 14 | 86 | 262 | 1.9 | 0 | 0 | 0 | 1.9 | 0.005 | 0.001 | 60 | 3.0465
交流330kV | 2011-09-12 01:01 | 2013-05-17 | 1.6793 | 13 | 40.88 | 135.88 | 0.88 | 0.07 | 0.1 | 0 | 1.05 | 0.008 | 0.004 | 56.8 | 3.3239
交流330kV | 2012-06-06 | 2014-03-04 | 1.7425 | 2.8 | 154.62 | 1190.65 | 2.2 | 0.28 | 1.46 | 0 | 3.94 | 0 | 0.003 | 55.5 | 7.7005
交流330kV | 2012-06-06 | 2014-03-04 | 1.7425 | 2.08 | 108.54 | 768.24 | 1.48 | 0.21 | 0.94 | 0 | 2.63 | 0.002 | 0 | 55.1 | 7.0779
交流330kV | 2011-07-13 | 2013-05-23 | 1.863 | 11.8 | 94.32 | 194.73 | 2.14 | 0.18 | 0.41 | 0 | 2.73 | 0.009 | 0.067 | 59.6 | 2.0646
交流330kV | 2008-09-05 | 2010-07-22 | 1.8767 | 19.5 | 118.39 | 246.67 | 2.29 | 0.32 | 0.49 | 0 | 3.1 | 0.011 | 0.134 | 63.6 | 2.0835
交流330kV | 2008-09-05 | 2010-07-22 | 1.8767 | 24.15 | 214.3 | 336.08 | 2.65 | 0.72 | 0.78 | 0 | 4.15 | 0.015 | 0.139 | 69 | 1.5683
交流330kV | 2011-07-25 | 2013-06-19 | 1.9041 | 1.83 | 25.38 | 70.48 | 1.88 | 0.82 | 0.6 | 0 | 3.3 | 0.008 | 0.003 | 59.2 | 2.777
交流330kV | 2011-07-25 | 2013-06-19 | 1.9041 | 1.98 | 23.52 | 65.63 | 1.49 | 0.25 | 0.6 | 0 | 2.34 | 0.007 | 0.005 | 58 | 2.7904
交流330kV | 2011-06-27 | 2013-05-23 | 1.9068 | 9.84 | 153.73 | 327.41 | 2.58 | 0.26 | 0.38 | 0 | 3.22 | 0.006 | 0.048 | 58 | 2.1298
交流330kV | 2004-12-26 | 2007-01-09 | 2.0384 | 10.66 | 270.63 | 605.66 | 3.35 | 1.07 | 1.25 | 0 | 5.67 | 0.028 | 0.165 | 55.4 | 2.238
交流330kV | 2011-08-06 | 2013-09-06 | 2.0877 | 11.98 | 155.43 | 205.9 | 3.92 | 0.28 | 0.69 | 0.31 | 5.2 | 0.021 | 0.031 | 60.86 | 1.3247
交流330kV | 2010-12-07 | 2013-04-19 | 2.3671 | 3.41 | 37.63 | 341.98 | 1.41 | 0.21 | 1.18 | 0.91 | 3.71 | 0.008 | 0 | 55 | 9.088
交流330kV | 2009-12-29 00:31 | 2012-07-31 | 2.589 | 1.58 | 50.78 | 203.64 | 1.6 | 0.16 | 0.26 | 0 | 2.02 | 0.009 | 0 | 72.6 | 4.0102
交流330kV | 2010-07-14 | 2013-04-19 | 2.7671 | 11.61 | 117.43 | 470.13 | 2.69 | 0.33 | 1.55 | 0 | 4.57 | 0.008 | 0 | 55.6 | 4.0035
交流330kV | 2010-08-03 00:28 | 2013-05-17 | 2.789 | 15.42 | 58 | 980.2 | 9.12 | 4.3 | 1.3 | 0 | 14.72 | 0.012 | 0.001 | 51.2 | 16.9
交流330kV | 2010-11-12 | 2013-09-24 | 2.8685 | 10.15 | 209.38 | 578.33 | 2.96 | 0.25 | 0.33 | 0 | 3.54 | 0.001 | 0.001 | 60.2 | 2.7621
交流330kV | 2009-03-31 | 2012-03-14 | 2.9562 | 20 | 147 | 344 | 4.51 | 0.25 | 0.57 | 0 | 5.33 | 0.001 | 0.001 | 60.4 | 2.3401
交流330kV | 2009-08-03 | 2012-08-07 | 3.0137 | 12.04 | 73.28 | 265.76 | 1.89 | 0.22 | 0.3 | 0 | 2.41 | 0.009 | 0 | 56.8 | 3.6266
交流330kV | 2009-08-01 | 2012-08-07 | 3.0192 | 7.3 | 336.43 | 860.82 | 3.61 | 0.36 | 0.6 | 0 | 4.57 | 0.009 | 0 | 58.3 | 2.5587
交流330kV | 2010-08-03 | 2013-09-24 | 3.1452 | 25.57 | 109.97 | 352.73 | 3.14 | 0.45 | 0.55 | 0 | 4.14 | 0.003 | 0.001 | 61.4 | 3.2075
交流330kV | 2004-12-26 | 2008-02-28 | 3.1753 | 5.83 | 282.81 | 491.59 | 3.36 | 0.72 | 0.42 | 0 | 4.5 | 0.021 | 0.072 | 52.8 | 1.7382
交流330kV | 2006-12-18 | 2010-03-16 | 3.2438 | 9.71 | 340.86 | 1101.87 | 4.41 | 0.8 | 0.05 | 0 | 5.26 | 0.027 | 0.168 | 55.2 | 3.2326
交流330kV | 2008-12-03 | 2012-03-14 | 3.2795 | 18 | 449 | 394 | 3.23 | 0 | 0.68 | 0 | 3.91 | 0.001 | 0.001 | 60 | 0.87751
交流330kV | 2010-08-03 00:28 | 2013-12-06 | 3.3452 | 0 | 1.15 | 31.42 | 0 | 0 | 0.1 | 0 | 0.1 | 0.002 | 0.057 | 65.36 | 27.3217
交流330kV | 2008-09-05 | 2012-02-29 | 3.4849 | 18.75 | 133.23 | 315.04 | 4.9 | 0.57 | 2.87 | 0 | 8.34 | 0.024 | 0.247 | 56.8 | 2.3646
交流330kV | 2008-09-05 | 2012-02-29 | 3.4849 | 24.23 | 437.91 | 708.35 | 4.69 | 1.18 | 0.84 | 0 | 6.71 | 0.022 | 1.047 | 53.3 | 1.6176
交流330kV | 2008-09-05 | 2012-03-01 | 3.4877 | 24.23 | 437.91 | 708.35 | 4.69 | 1.18 | 0.84 | 0 | 6.71 | 0.022 | 1.047 | 53.3 | 1.6176
交流330kV | 2008-09-05 | 2012-03-01 | 3.4877 | 18.75 | 133.23 | 315.04 | 4.9 | 0.57 | 2.87 | 0 | 8.34 | 0.024 | 0.247 | 56.8 | 2.3646
交流330kV | 2009-12-29 00:31 | 2013-08-15 | 3.6301 | 10.13 | 466.23 | 737.08 | 2.44 | 0 | 1.08 | 0 | 3.52 | 0.021 | 0.06 | 31.65 | 1.5809
交流330kV | 2009-08-03 | 2013-08-16 | 4.0384 | 12.83 | 116.96 | 423.56 | 2.65 | 0.2 | 17.64 | 0 | 20.49 | 0.022 | 0.02 | 55.34 | 3.6214
交流330kV | 2009-08-01 | 2013-08-16 | 4.0438 | 6.39 | 564.09 | 1635.23 | 4.39 | 0.34 | 44.76 | 0 | 49.49 | 0.018 | 0.057 | 53.37 | 2.8989
交流330kV | 2009-03-22 | 2013-04-11 | 4.0575 | 13.22 | 115.41 | 260.74 | 1.49 | 0.24 | 0.24 | 0 | 1.97 | 0.017 | 0.01 | 56 | 2.2592
交流330kV | 2009-03-22 | 2013-04-11 | 4.0575 | 9.07 | 110.18 | 187.05 | 3.53 | 0.4 | 7.27 | 0 | 11.2 | 0.015 | 0.07 | 59.6 | 1.6977
交流330kV | 2008-10-30 00:54 | 2012-12-18 | 4.1369 | 13 | 363.91 | 1139.83 | 7.53 | 0.36 | 1.73 | 0 | 9.62 | 0.019 | 0.11 | 59.2 | 3.1322
交流330kV | 2008-10-30 00:35 | 2012-12-18 | 4.1369 | 18.19 | 182.76 | 461.42 | 3.86 | 0.32 | 0.72 | 0 | 4.9 | 0.021 | 0.07 | 57.8 | 2.5247
交流330kV | 2008-09-28 01:04 | 2012-12-14 | 4.2136 | 13.74 | 192.32 | 518.65 | 3.12 | 0.41 | 0.24 | 0 | 3.77 | 0.02 | 0.03 | 56.7 | 2.6968
交流330kV | 2008-09-28 00:43 | 2012-12-14 | 4.2136 | 16.55 | 188.28 | 499.01 | 2.99 | 0.38 | 0.24 | 0 | 3.61 | 0.017 | 0.06 | 58.9 | 2.6504
交流330kV | 2008-01-04 | 2012-05-11 | 4.3534 | 14.87 | 443.46 | 1050.97 | 4.59 | 0.99 | 0.64 | 0 | 6.22 | 0.033 | 0.059 | 70.2 | 2.3699
交流330kV | 2009-03-31 | 2013-09-24 | 4.4877 | 41.83 | 142.88 | 604.18 | 9.13 | 0.3 | 1.16 | 0 | 10.59 | 0.003 | 0.001 | 55.8 | 4.2286
交流330kV | 2008-10-30 00:54 | 2013-06-05 | 4.5999 | 5.49 | 242.28 | 1295.11 | 6.34 | 0.37 | 1.81 | 0 | 8.52 | 0.012 | 0.02 | 57.6 | 5.3455
交流330kV | 2008-10-30 00:35 | 2013-06-05 | 4.5999 | 8.66 | 120.25 | 602.04 | 3.73 | 0.24 | 0.7 | 0 | 4.67 | 0.011 | 0.06 | 58 | 5.0066
交流330kV | 2007-12-31 00:23 | 2012-09-05 | 4.6849 | 0.93 | 21.09 | 175.9 | 0.23 | 0 | 0 | 0 | 0.23 | 0.007 | 0 | 72.8 | 8.3404
交流330kV | 2007-12-26 00:43 | 2012-09-05 | 4.6985 | 4.07 | 187.25 | 287.17 | 1.46 | 0.19 | 0.34 | 0 | 1.99 | 0.009 | 0 | 74.9 | 1.5336
交流330kV | 2008-07-18 00:24 | 2013-04-17 | 4.7506 | 11.2 | 159.3 | 284 | 4.1 | 0 | 0 | 0 | 4.1 | 0.06 | 0.07 | 58.4 | 1.7828
交流330kV | 2008-12-03 | 2013-09-24 | 4.811 | 23.57 | 558.06 | 790.66 | 8.67 | 0.35 | 1.12 | 0 | 10.14 | 0.003 | 0.002 | 55.4 | 1.4168
交流330kV | 2009-03-22 | 2014-04-02 | 5.0329 | 9.96 | 163.37 | 394.92 | 1.88 | 0.34 | 0.33 | 0 | 2.55 | 0.019 | 0.033 | 59.6 | 2.4173
交流330kV | 2009-03-22 | 2014-04-02 | 5.0329 | 8.97 | 123.32 | 178.48 | 1.54 | 0.18 | 0.38 | 0 | 2.1 | 0.001 | 0.06 | 54.4 | 1.4473
交流330kV | 2005-03-03 | 2010-03-16 | 5.0384 | 12.88 | 424.07 | 470.14 | 9.46 | 2.18 | 2.18 | 0 | 13.82 | 0.043 | 0.039 | 58.4 | 1.1086
交流330kV | 2008-01-04 | 2013-01-24 | 5.0603 | 13 | 626 | 1930 | 7.36 | 1.55 | 1.75 | 0 | 10.66 | 0.023 | 0.001 | 58.4 | 3.0831
交流330kV | 2008-01-04 | 2013-01-24 | 5.0603 | 20 | 503 | 2317 | 7.09 | 1.37 | 1.5 | 0 | 9.96 | 0.02 | 0.001 | 57.6 | 4.6064
交流330kV | 2004-12-26 | 2010-03-16 | 5.2219 | 5.92 | 355.21 | 647.88 | 4.84 | 0.65 | 0.1 | 0 | 5.59 | 0.028 | 0.315 | 55.2 | 1.8239
交流330kV | 2007-12-15 01:04 | 2013-04-11 | 5.3259 | 24.07 | 299.01 | 532.45 | 8.61 | 0.62 | 1.5 | 0 | 10.73 | 0.043 | 0.09 | 54.8 | 1.7807
交流330kV | 2007-12-11 00:15 | 2013-04-11 | 5.337 | 18.84 | 297.57 | 504.72 | 6.6 | 0.43 | 1.08 | 0 | 8.11 | 0.098 | 0.2 | 60.4 | 1.6961
交流330kV | 2005-03-03 | 2010-07-15 | 5.3699 | 9.59 | 387.44 | 738.66 | 12.49 | 2.73 | 5.42 | 0 | 20.64 | 0.009 | 1.336 | 69.9 | 1.9065
交流330kV | 2007-07-03 00:49 | 2012-12-04 | 5.4273 | 8.56 | 144.84 | 158.58 | 5.54 | 0.25 | 0.47 | 0 | 6.26 | 0.013 | 0.029 | 58.9 | 1.0949
交流330kV | 2007-06-30 00:41 | 2012-12-04 | 5.4355 | 12.06 | 192.96 | 173.18 | 5.63 | 0.34 | 0.41 | 0 | 6.38 | 0.013 | 0.024 | 56.7 | 0.89749
交流330kV | 2007-12-31 00:23 | 2013-08-15 | 5.6274 | 4.03 | 145.65 | 911.37 | 0.46 | 0 | 1.08 | 0 | 1.54 | 0.078 | 0.023 | 59.72 | 6.2573
交流330kV | 2006-12-27 00:47 | 2012-08-15 | 5.6383 | 262.54 | 329.81 | 1678.55 | 20.53 | 0.51 | 2.4 | 0 | 23.44 | 0.009 | 0 | 63.4 | 5.0894
交流330kV | 2006-12-27 | 2012-08-15 | 5.6384 | 16.64 | 271.48 | 1400.18 | 3.62 | 0.38 | 0.52 | 0 | 4.52 | 0.007 | 0.001 | 60 | 5.1576
交流330kV | 2007-12-26 00:43 | 2013-08-15 | 5.641 | 10.13 | 466.23 | 737.08 | 1.21 | 0 | 1.18 | 0 | 3.57 | 0.058 | 0.015 | 45.37 | 1.5809
交流330kV | 2008-01-04 | 2013-09-24 | 5.726 | 9.19 | 431.26 | 1857.25 | 8.96 | 2.05 | 1.39 | 0 | 12.4 | 0.003 | 0.001 | 54 | 4.3066
交流330kV | 2008-01-04 | 2013-09-24 | 5.726 | 14.04 | 643.54 | 2114 | 9.44 | 1.76 | 1.45 | 0 | 12.65 | 0.004 | 0.001 | 62 | 3.285
交流330kV | 2007-07-03 00:49 | 2013-06-14 | 5.9533 | 7.79 | 118.86 | 125.14 | 6.04 | 0.27 | 0.85 | 0 | 7.16 | 0.008 | 0.001 | 56.4 | 1.0528
交流330kV | 2007-06-30 00:41 | 2013-06-14 | 5.9616 | 11.61 | 183.13 | 163.35 | 6.68 | 0.43 | 0.39 | 0 | 7.5 | 0.008 | 0 | 52.4 | 0.89199
交流330kV | 2007-07-25 | 2013-09-06 | 6.1233 | 16.91 | 166.56 | 252.07 | 1.98 | 0.22 | 0.38 | 0 | 2.58 | 0.042 | 0.451 | 53.51 | 1.5134
交流330kV | 2007-07-25 | 2013-09-06 | 6.1233 | 16.04 | 224.24 | 267.48 | 2.05 | 0.25 | 4.14 | 0 | 6.44 | 0.005 | 0.054 | 49.45 | 1.1928
交流330kV | 2006-12-04 00:30 | 2013-04-11 | 6.3561 | 56.25 | 52.1 | 105.37 | 3.72 | 0.24 | 0.76 | 0 | 4.72 | 0.022 | 0.004 | 54.6 | 2.0225
交流330kV | 2006-03-08 00:30 | 2012-08-30 | 6.4849 | 1.35 | 162.05 | 596.99 | 3.66 | 0.54 | 0.99 | 0 | 5.19 | 0.011 | 0.017 | 72 | 3.684
交流330kV | 2005-03-03 | 2011-08-30 | 6.4959 | 10.85 | 443.19 | 1058.37 | 19.99 | 2.87 | 15.28 | 0 | 38.14 | 0.007 | 1.344 | 68.5 | 2.3881
交流330kV | 2006-12-27 00:47 | 2013-07-27 | 6.5862 | 265.35 | 401.07 | 1222.33 | 10.35 | 0.78 | 21.25 | 0 | 32.38 | 0.006 | 0.033 | 47.16 | 3.0477
交流330kV | 2006-12-27 00:47 | 2013-07-31 | 6.5972 | 196.52 | 339.4 | 1551.93 | 10.47 | 0.83 | 17.8 | 0 | 29.1 | 0.028 | 0.095 | 47.08 | 4.5726
交流330kV | 2006-12-27 00:47 | 2013-08-02 | 6.6027 | 145.78 | 282.33 | 1253.64 | 12.23 | 0.81 | 26.96 | 0 | 40 | 0.021 | 0.06 | 46.52 | 4.4403
交流330kV | 2006-12-27 00:47 | 2013-08-05 | 6.6109 | 129.44 | 264.33 | 1583.57 | 14.82 | 0.71 | 37.12 | 0 | 52.65 | 0.021 | 0.064 | 53.09 | 5.9909
交流330kV | 2006-12-27 00:47 | 2013-08-08 | 6.6191 | 97.6 | 238.2 | 1328 | 3.51 | 0.53 | 16.64 | 0 | 20.68 | 0.002 | 0.052 | 46.53 | 5.5751
交流330kV | 2006-12-27 00:47 | 2013-08-11 | 6.6273 | 89.99 | 222.02 | 1487.71 | 4.5 | 0.54 | 15.74 | 0 | 20.78 | 0.029 | 0.055 | 51.03 | 6.7008
交流330kV | 2006-12-27 00:47 | 2013-08-15 | 6.6383 | 70.17 | 213.6 | 1408.25 | 4.21 | 0.74 | 2.23 | 0 | 7.18 | 0.036 | 0.033 | 51.4 | 6.5929
交流330kV | 2006-12-27 00:47 | 2013-08-17 | 6.6437 | 85.05 | 206.3 | 1472.48 | 3.74 | 0.68 | 20.34 | 0 | 24.76 | 0.03 | 0.047 | 60.19 | 7.1376
交流330kV | 2006-12-27 00:47 | 2013-08-21 | 6.6547 | 66.05 | 184.94 | 1189.03 | 6.2 | 0.62 | 14.06 | 0 | 20.88 | 0.041 | 0.044 | 51.67 | 6.4293
交流330kV | 2006-12-27 | 2013-08-21 | 6.6548 | 12.59 | 336.6 | 1139.73 | 3.78 | 0.4 | 30.18 | 0 | 34.36 | 0.052 | 0.027 | 47.48 | 3.386
交流330kV | 2006-12-27 00:47 | 2013-08-23 | 6.6602 | 61.25 | 176.22 | 1277.82 | 14.43 | 0.78 | 10.39 | 0 | 25.6 | 0.039 | 0.038 | 51.2 | 7.2513
交流330kV | 2006-12-27 00:47 | 2013-08-26 | 6.6684 | 65.28 | 195.65 | 1344.29 | 15.22 | 0.67 | 11.66 | 0 | 27.55 | 0.042 | 0.061 | 48.05 | 6.8709
交流330kV | 2006-12-27 00:47 | 2013-08-29 | 6.6766 | 67.66 | 198.12 | 1313.98 | 13.21 | 0.61 | 13.71 | 0 | 27.53 | 0.031 | 0.044 | 57.19 | 6.6322
交流330kV | 2006-12-27 00:47 | 2013-09-01 | 6.6848 | 67.09 | 199.06 | 1401.18 | 11.71 | 0.79 | 14.19 | 0 | 26.69 | 0.012 | 0.059 | 53.23 | 7.039
交流330kV | 2006-12-27 00:47 | 2013-09-04 | 6.6931 | 65.73 | 182.31 | 1341.2 | 10.37 | 0.62 | 13.08 | 0 | 24.07 | 0.021 | 0.044 | 59.68 | 7.3567
交流330kV | 2006-12-27 00:47 | 2013-09-07 | 6.7013 | 63.55 | 193.91 | 1374.81 | 9.21 | 0.77 | 10.73 | 0 | 20.71 | 0.026 | 0.03 | 63.35 | 7.0899
交流330kV | 2006-12-27 00:47 | 2013-09-10 | 6.7095 | 66.34 | 196.6 | 1408.21 | 7.43 | 0.94 | 12.64 | 0 | 21.01 | 0.016 | 0.035 | 62.65 | 7.1628
交流330kV | 2006-12-27 00:47 | 2013-09-13 | 6.7177 | 68.72 | 188.44 | 1255.92 | 4.22 | 0.77 | 11.21 | 0 | 16.2 | 0.005 | 0.044 | 59.26 | 6.6648
交流330kV | 2006-12-27 00:47 | 2013-09-16 | 6.7259 | 61.79 | 184.59 | 1230.24 | 8.87 | 0.74 | 12.58 | 0 | 22.19 | 0.043 | 0.056 | 62.73 | 6.6647
交流330kV | 2006-12-27 00:47 | 2013-09-19 | 6.7342 | 51.66 | 197.43 | 1310.49 | 4.96 | 0.64 | 5.33 | 0 | 10.93 | 0.048 | 0.097 | 57.62 | 6.6377
交流330kV | 2006-12-27 00:47 | 2013-09-22 | 6.7424 | 42.89 | 188.53 | 1293.53 | 3.3 | 0.69 | 2.13 | 0 | 6.12 | 0.027 | 0.107 | 56.28 | 6.8611
交流330kV | 2005-03-03 | 2012-02-10 | 6.9452 | 10.86 | 446.73 | 654.49 | 17.71 | 2.62 | 10.89 | 0 | 31.22 | 0.013 | 0.794 | 52.8 | 1.4651
交流330kV | 2006-03-08 00:30 | 2013-08-09 | 7.4273 | 15.1 | 368.26 | 1418.74 | 58.55 | 0.96 | 1.42 | 0 | 60.93 | 0.009 | 0.082 | 55.77 | 3.8525
交流330kV | 2005-10-27 00:37 | 2013-04-17 | 7.4766 | 78.8 | 77.7 | 176.4 | 3.2 | 0 | 0 | 0 | 3.2 | 0.08 | 0.08 | 59.2 | 2.2703
交流330kV | 2005-06-24 01:00 | 2013-04-11 | 7.8026 | 291.52 | 181.44 | 1174.25 | 40.94 | 0.6 | 5 | 0 | 46.54 | 0.009 | 0.04 | 59.3 | 6.4718
交流330kV | 2005-07-24 01:15 | 2013-05-17 | 7.819 | 9.5 | 214.96 | 1205.08 | 8.86 | 1.24 | 3 | 0 | 13.1 | 0.009 | 0.003 | 59.6 | 5.6061
交流330kV | 2005-04-20 00:52 | 2013-04-11 | 7.9807 | 12.77 | 342.94 | 1153.83 | 5.96 | 1.01 | 0.78 | 0 | 7.75 | 0.008 | 0.04 | 56.1 | 3.3645
交流330kV | 2005-06-24 01:00 | 2013-09-03 | 8.1999 | 359.76 | 192.91 | 1522.06 | 29.62 | 0.47 | 34.67 | 0 | 64.76 | 0.051 | 0.034 | 55.91 | 7.89
交流330kV | 2005-06-24 01:00 | 2013-09-10 | 8.2191 | 323.62 | 164.51 | 1296.29 | 10.74 | 0.55 | 2.19 | 0 | 13.48 | 0.018 | 0.03 | 58.28 | 7.8797
交流330kV | 2005-06-24 01:00 | 2013-09-17 | 8.2382 | 324.34 | 177.14 | 1301.32 | 26.12 | 0.49 | 22.59 | 0 | 49.2 | 0.012 | 0.044 | 58.4 | 7.3463
交流330kV | 2005-06-24 01:00 | 2013-09-24 | 8.2574 | 357.78 | 185.4 | 1376.47 | 48.87 | 0.58 | 19.07 | 0 | 68.52 | 0.025 | 0.036 | 65.96 | 7.4243
交流330kV | 2005-06-24 01:00 | 2013-09-30 | 8.2739 | 261.77 | 99.9 | 1327.44 | 37.55 | 0.35 | 1.3 | 0 | 39.2 | 0.06 | 0.184 | 59.84 | 13.2877
交流330kV | 2005-06-24 01:00 | 2013-10-08 | 8.2958 | 221.61 | 95.79 | 1329.02 | 45.11 | 0.54 | 2.02 | 0 | 47.67 | 0.035 | 0.034 | 64.32 | 13.8743
交流330kV | 2005-06-24 01:00 | 2013-10-14 | 8.3122 | 344.86 | 198.33 | 1108.44 | 37.65 | 0.49 | 11.99 | 0 | 50.13 | 0.035 | 0.034 | 64.32 | 5.5889
交流330kV | 2005-06-24 01:00 | 2013-10-21 | 8.3314 | 343.96 | 191.68 | 1271.14 | 34.41 | 0.53 | 16.22 | 0 | 51.16 | 0.004 | 0.03 | 65.74 | 6.6316
交流330kV | 2005-06-24 01:00 | 2013-10-28 | 8.3506 | 311.59 | 179.58 | 1180.83 | 6.28 | 0.57 | 22.64 | 0 | 29.49 | 0.038 | 0.098 | 61.42 | 6.5755
交流330kV | 2004-03-27 00:05 | 2013-05-17 | 9.1452 | 40.8 | 260.44 | 895.15 | 13 | 1.5 | 6.55 | 0 | 21.05 | 0.013 | 0.001 | 60 | 3.4371
交流330kV | 2003-12-31 00:46 | 2013-05-17 | 9.3835 | 10 | 650 | 1900 | 8.74 | 2.05 | 1.9 | 0 | 12.69 | 0.009 | 0.001 | 54.4 | 2.9231
交流330kV | 2002-12-27 00:09 | 2013-04-17 | 10.3123 | 33.8 | 258.4 | 851.8 | 6.6 | 0 | 0 | 0 | 6.6 | 0.023 | 0.04 | 59.3 | 3.2964
交流330kV | 2000-05-26 | 2012-03-13 | 11.8055 | 10 | 510 | 1971 | 18.7 | 5.79 | 4.86 | 0 | 29.35 | 0.004 | 0.007 | 55.8 | 3.8647
交流330kV | 1999-08-16 | 2012-03-29 | 12.6274 | 6 | 1277 | 2561 | 17.26 | 5.57 | 4.63 | 0 | 27.46 | 0.006 | 0.002 | 51 | 2.0055
交流330kV | 2000-05-26 | 2013-01-23 | 12.6712 | 11 | 443 | 2514 | 23.79 | 6.01 | 5.99 | 0 | 35.79 | 0.036 | 0.002 | 60.2 | 5.6749
交流330kV | 1999-11-25 | 2012-09-08 | 12.7973 | 7.2 | 241.58 | 751.43 | 2.7 | 0.31 | 0.52 | 0 | 3.53 | 0.009 | 0 | 67 | 3.1105
交流330kV | 2000-05-26 | 2013-09-24 | 13.3397 | 10.72 | 551.34 | 2638.1 | 29.33 | 7.42 | 9.12 | 0 | 45.87 | 0.007 | 0.004 | 62 | 4.7849
交流330kV | 1999-08-16 | 2013-01-23 | 13.4493 | 7 | 1064 | 4199 | 22.6 | 5.96 | 5.83 | 0 | 34.39 | 0.035 | 0.001 | 60.3 | 3.9464
交流330kV | 1999-11-25 | 2013-09-06 | 13.7918 | 7.33 | 243.24 | 733.74 | 3.33 | 0.37 | 1.18 | 0 | 4.88 | 0.028 | 0.034 | 62.07 | 3.0165
交流330kV | 1999-08-16 | 2013-09-24 | 14.1178 | 8.62 | 1381.4 | 4346.22 | 30.33 | 6.95 | 9.06 | 0 | 46.34 | 0.015 | 0.008 | 60.8 | 3.1462
交流330kV | 1996-01-01 00:44 | 2012-08-30 | 16.6739 | 1.52 | 220.02 | 822.31 | 6.92 | 1.6 | 2.22 | 0 | 10.74 | 0.01 | 0.001 | 72.5 | 3.7374
交流330kV | 1993-12-30 00:47 | 2011-05-16 | 17.3862 | 19.6 | 565.3 | 1712.8 | 15 | 0.9 | 2.6 | 0 | 18.5 | 0.02 | 0.09 | 60.4 | 3.0299
交流330kV | 1996-01-01 00:44 | 2013-08-09 | 17.6164 | 13.36 | 248.78 | 1008.87 | 11.62 | 0.5 | 1.44 | 0 | 13.56 | 0.017 | 0.019 | 54.98 | 4.0553
交流330kV | 1993-12-30 00:47 | 2012-08-30 | 18.6794 | 11.95 | 477.37 | 1230.28 | 10.67 | 2.25 | 2.56 | 0 | 15.48 | 0.001 | 0.001 | 69.5 | 2.5772
交流330kV | 1994-07-13 00:44 | 2013-04-11 | 18.7588 | 4.01 | 115.64 | 348.24 | 3.67 | 1.01 | 2.77 | 0 | 7.45 | 0.018 | 0.004 | 58.3 | 3.0114
交流330kV | 1993-12-30 00:47 | 2013-08-09 | 19.6218 | 8.68 | 764.23 | 2475.28 | 17.71 | 1.78 | 17.9 | 0 | 37.39 | 0.021 | 0.099 | 54.93 | 3.2389
交流330kV | 1991-11-24 00:43 | 2013-04-11 | 21.3944 | 4.98 | 170.07 | 451 | 4.44 | 1.96 | 1.69 | 1.23 | 9.32 | 0.047 | 0.002 | 45.5 | 2.6518
交流330kV | 1990-04-20 00:30 | 2012-10-06 | 22.4794 | 1.03 | 2.25 | 60.2 | 0.26 | 0 | 0 | 0 | 0.26 | 0.009 | 0 | 63.8 | 26.7556
交流330kV | 1990-04-20 00:30 | 2013-07-11 | 23.241 | 2.36 | 45.66 | 219.48 | 0 | 0 | 0.35 | 0 | 0.35 | 0.013 | 0.019 | 69.8 | 4.8068
交流330kV | 1987-09-20 00:45 | 2012-09-12 | 24.9972 | 2.82 | 1.19 | 166.1 | 0.47 | 0 | 0 | 0 | 0.47 | 0.001 | 0 | 69.2 | 139.5798
交流330kV | 1987-09-20 00:45 | 2013-05-17 | 25.6739 | 2.4 | 11.4 | 59.6 | 0.36 | 0.3 | 0 | 0 | 0.66 | 0.008 | 0.002 | 60.8 | 5.2281
交流330kV | 1987-09-20 00:45 | 2013-07-19 | 25.8465 | 2.96 | 53.64 | 156.97 | 12.52 | 0.63 | 6.42 | 0 | 19.57 | 0.006 | 0.034 | 54.1 | 2.9264

## 2-330kV
VOLTAGE | YOM | Age | TCG | TEMPERATURE | CO | CO2 | H2 | CH4 | C2H4 | C2H6 | C2H2 | water | ACIDITY | BREAKDOWN | FURFURAL | RESISTIVITY | DDF | COMMENTS
33000 | 2012 | -1 | 140.3 | 20 | 78.2 | 218.2 | 60.8 | 0.8 | 0.1 | 0.4 | 0 | 6 | 0.002 | 67 |  | 555 | 0.003 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 2011 | 0 | 122.2 | 41 | 113.9 | 227.5 | 6.9 | 1.1 | 0.2 | 0.1 | 0 | 7 | 0.004 | 84 |  | 630 | 0.004 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 2011 | 0 | 137.5 | 33 | 115 | 264.5 | 21 | 1.3 | 0.1 | 0.1 | 0 | 3 | 0 | 92 |  | 933 | 0.001 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 2011 | 0 | 154.5 | 25 | 136.3 | 312.7 | 16.7 | 1.4 | 0.1 | 0 | 0 | 5 | 0 | 81 |  | 1700 | 0.001 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 2011 | 0 | 159.9 | 34 | 150.6 | 199.7 | 7.9 | 1.3 | 0.1 | 0 | 0 | 2 | 0 | 72 |  | 84 | 0.011 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 2011 | 0 | 310.3 | 79 | 290.3 | 1030.2 | 10.1 | 7.8 | 1.2 | 0.8 | 0.1 | 5 | 0.004 | 87 |  | 179 | 0.007 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 2011 | 0 | 187.1 | 15 | 103 | 169.5 | 82.3 | 0.8 | 1 | 0 | 0 | 5 | 0 | 84 |  | 227 | 0.005 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable. Non-corrosive IEC. Non-corrosive ASTM 3A.
33000 | 2011 | 0 | 153.6 | 42 | 110.9 | 260.4 | 41.7 | 0.9 | 0.1 | 0 | 0 | 3 | 0.001 | 85 |  | 116 | 0.005 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable. Non-corrosive IEC. Non-corrosive ASTM 3A.
33000 | 2011 | 0 | 155 | 37 | 120.6 | 331.6 | 26 | 8.4 | 0 | 0 | 0 | 10 | 0 | 78 |  | 136 | 0.007 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
330000 | 2004 | 1 | 84.6 | 22 | 83.7 | 163.6 | 0 | 0.6 | 0.1 | 0.2 | 0 | 6 | 0 | 62 | 0 | 299 | 0.002 | DGA is assessed as acceptable. Oil quality is assessed as acceptable. Insulation is assessed as acceptable.
330000 | 2004 | 1 | 90.3 | 41.81 | 88.9 | 221.3 | 0 | 1 | 0.2 | 0.2 | 0 | 6 | 0.01 | 66 | 0 | 140 | 0.002 | DGA is assessed as acceptable. Oil quality is assessed as acceptable. Tested to be uncontaminated by PCB. Insulation is assessed as acceptable.
33000 | 2010 | 1 | 216.9 | 39 | 197.1 | 352.2 | 16.9 | 2.6 | 0.1 | 0.2 | 0 | 7 | 0.001 | 78 |  | 246 | 0.006 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 2010 | 1 | 311.8 | 29 | 296.2 | 559.7 | 11.1 | 2.7 | 1.4 | 0.4 | 0 | 4 | 0 | 86 |  | 147 | 0.008 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 2010 | 1 | 36.3 | 37 | 27.1 | 104.6 | 8.9 | 0.3 | 0 | 0 | 0 | 4 | 0.01 | 72 |  | 60 | 0.01 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 2010 | 1 | 127 | 41 | 111.4 | 326.1 | 13.8 | 1.6 | 0 | 0.2 | 0 | 8 | 0.001 | 78 |  | 107 | 0.011 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 2010 | 1 | 276.3 | 41.81 | 155 | 586.1 | 78.9 | 11.4 | 1.2 | 29.8 | 0 | 14 | 0.003 | 46 |  | 86 | 0.008 | Dissolved gas levels are increased. | Oil quality is assessed as acceptable.
33000 | 2010 | 1 | 166.5 | 38 | 144.3 | 251.2 | 20.5 | 1.7 | 0 | 0 | 0 | 11 | 0.001 | 55 |  | 90 | 0.011 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 2010 | 1 | 175.4 | 41.81 | 163.2 | 303.3 | 10 | 1.8 | 0.2 | 0.2 | 0 | 3 | 0.003 | 70 |  | 138 | 0.008 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 2010 | 1 | 180.2 | 41.81 | 168.5 | 271.5 | 9.5 | 1.9 | 0.2 | 0.1 | 0 | 4 | 0.001 | 74 |  | 134 | 0.01 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 2010 | 1 | 358 | 34 | 340.2 | 600 | 5.6 | 11.1 | 0.8 | 0.3 | 0 | 22 | 0 | 41 |  | 354 | 0.003 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 2010 | 1 | 391.3 | 41.81 | 82.7 | 789.9 | 285.7 | 7.6 | 0.9 | 14.4 | 0 | 28 | 0.003 | 22 |  | 163 | 0.006 | DGA is assessed as acceptable at present. | Breakdown voltage is low. Other oil quality results are assessed as acceptable.
33000 | 2010 | 1 | 128.3 | 40 | 112.9 | 201.9 | 14.2 | 1.2 | 0 | 0 | 0 | 2 | 0.001 | 77 |  | 516 | 0.005 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 2010 | 1 | 572.4 | 29 | 141.3 | 831.1 | 404.7 | 10.9 | 1.2 | 14.3 | 0 | 16 | 0.006 | 35 |  | 176 | 0.003 | Dissolved gas levels are increasing. Dissolved gases consistent with May 2011 sample. | Breakdown voltage is low. Other oil quality results are assessed as acceptable.
33000 | 2010 | 1 | 285.5 | 31 | 266.4 | 453 | 7.2 | 10.2 | 0.9 | 0.8 | 0 | 4 | 0 | 88 |  | 155 | 0.009 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 2010 | 1 | 204.7 | 41.81 | 103.1 | 570 | 87.1 | 4.4 | 0.4 | 9.7 | 0 | 23 | 0.002 | 50 |  | 156 | 0.005 | DGA is assessed as acceptable at present. | Oil quality is assessed as acceptable.
33000 | 2010 | 1 | 120 | 38 | 112.3 | 253.2 | 6.4 | 1.3 | 0 | 0 | 0 | 15 | 0.002 | 88 |  | 294 | 0.006 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 2010 | 1 | 293.9 | 42 | 164.9 | 575.6 | 110.8 | 6.9 | 0.8 | 10.5 | 0 | 20 | 0.003 | 33 |  | 196 | 0.005 | DGA is assessed as acceptable. Dissolved gas levels consistent with May 2011 sample. | Breakdown voltage is low. Other oil quality results are assessed as acceptable.
33000 | 2010 | 1 | 232.1 | 40 | 220.2 | 381.7 | 8.8 | 2.5 | 0.5 | 0.1 | 0 | 3 | 0.003 | 84 |  | 270 | 0.006 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 2010 | 1 | 399.4 | 33 | 357.9 | 676.8 | 27.9 | 12.2 | 1.1 | 0.3 | 0 | 5 | 0 | 72 |  | 60 | 0.021 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 2010 | 1 | 4438.3 | 41 | 470.8 | 174.1 | 1305.6 | 427.2 | 674.3 | 48.8 | 1511.6 | 6 | 0.01 | 74 |  | 235 | 0.011 | DGA suggests arcing has occurred. | Oil quality is assessed as acceptable.
33000 | 2010 | 1 | 157.7 | 45 | 133.1 | 264.5 | 23 | 1 | 0.1 | 0 | 0.5 | 7 | 0 | 90 |  | 122 | 0.008 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 2010 | 1 | 134 | 40 | 120.6 | 223.9 | 12.2 | 1.2 | 0 | 0 | 0 | 7 | 0.002 | 80 |  | 195 | 0.004 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 2010 | 1 | 184.5 | 41 | 163.5 | 268.4 | 18.8 | 1.8 | 0.1 | 0.3 | 0 | 5 | 0.001 | 78 |  | 418 | 0.004 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 2010 | 1 | 298.1 | 29 | 273.7 | 397.8 | 14.4 | 3.2 | 2.4 | 4.4 | 0 | 5 | 0 | 82 |  | 266 | 0.006 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 2010 | 1 | 182.1 | 27 | 170.3 | 94.4 | 9.6 | 1.9 | 0.1 | 0.2 | 0 | 6 | 0.001 | 79 |  | 267 | 0.006 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 2010 | 1 | 71 | 37 | 61 | 138 | 9 | 1 | 0 | 0 | 0 | 8 | 0.01 | 75 |  | 153 | 0.007 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 2010 | 1 | 224.6 | 46 | 190.1 | 388.8 | 31.8 | 1.8 | 0.9 | 0 | 0 | 4 | 0.001 | 86 |  | 34 | 0.027 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 2010 | 1 | 366.5 | 50 | 322.2 | 596.6 | 32 | 8.5 | 2 | 0.9 | 0.9 | 8 | 0 | 84 |  | 156 | 0.008 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 2010 | 1 | 293.3 | 45 | 241.8 | 446.9 | 48.4 | 2.6 | 0.3 | 0.2 | 0 | 5 | 0.002 | 82 |  | 161 | 0.01 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 2010 | 1 | 377.8 | 40 | 341.6 | 717.2 | 32.1 | 3.3 | 0.6 | 0.2 | 0 | 4 | 0.003 | 56 |  | 265 | 0.006 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 2010 | 1 | 352.7 | 38 | 323.3 | 496.5 | 25.1 | 3.1 | 0.4 | 0.8 | 0 | 4 | 0.003 | 68 |  | 181 | 0.006 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable. Non-corrosive IEC. Non-corrosive ASTM 3A.
33000 | 2010 | 1 | 603.6 | 40 | 551.7 | 975.2 | 31.5 | 8 | 1.7 | 10.7 | 0 | 4 | 0 | 84 |  | 169 | 0.008 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 2010 | 1 | 383.7 | 49 | 343.6 | 646.4 | 28.3 | 5.6 | 0.7 | 5.5 | 0 | 3 | 0.002 | 91 |  | 194 | 0.007 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable. Non-corrosive IEC. Non-corrosive ASTM 3A.
33000 | 2010 | 1 | 470.3 | 42 | 436 | 868.6 | 16.5 | 7.6 | 1.9 | 8.3 | 0 | 6 | 0 | 80 |  | 154 | 0.007 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 2010 | 1 | 231.9 | 33 | 214.5 | 269.6 | 14 | 2 | 0.7 | 0.7 | 0 | 5 | 0.003 | 78 |  | 325 | 0.005 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 2010 | 1 | 322.2 | 30 | 291.9 | 411.5 | 21.3 | 8 | 0.8 | 0.2 | 0 | 5 | 0.001 | 74 |  | 212 | 0.006 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 2010 | 1 | 88 | 27 | 77.3 | 163.1 | 9.6 | 0.7 | 0.2 | 0.2 | 0 | 3 | 0.004 | 77 |  | 396 | 0.003 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 2010 | 1 | 250.1 | 30 | 232 | 351 | 15 | 2 | 0.9 | 0.2 | 0 | 3 | 0 | 77 |  | 155 | 0.006 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 2010 | 1 | 345 | 48 | 314.4 | 536.4 | 25.7 | 3.6 | 0.8 | 0.5 | 0 | 4 | 0.004 | 86 |  | 118 | 0.008 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 2010 | 1 | 475 | 43 | 407 | 1074 | 37 | 21 | 4 | 6 | 0 | 5 | 0 | 75 |  | 122 | 0.009 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 2010 | 1 | 83.7 | 23 | 69.4 | 128.9 | 9.8 | 1.4 | 1.8 | 0 | 1.3 | 4 | 0 | 56 |  | 324 | 0.006 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 2010 | 1 | 265.7 | 50 | 220.1 | 358.5 | 41.3 | 2.6 | 0.3 | 1.2 | 0.2 | 2 | 0.004 | 80 |  | 110 | 0.011 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 2010 | 1 | 353.6 | 42 | 243.8 | 494.3 | 16.8 | 45.5 | 3.6 | 43.9 | 0 | 4 | 0 | 74 |  | 41 | 0.015 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 2010 | 1 | 174.8 | 32 | 160.3 | 296.6 | 10.9 | 1.7 | 1 | 0.6 | 0.3 | 3 | 0.001 | 81 |  | 200 | 0.004 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 2010 | 1 | 127.7 | 27 | 100.9 | 216 | 26.4 | 0.4 | 0 | 0 | 0 | 4 | 0.01 | 75 |  | 83 | 0.007 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 2010 | 1 | 183.8 | 16 | 171.7 | 261.8 | 9 | 1.5 | 0.9 | 0.7 | 0 | 6 | 0 | 81 |  | 527 | 0.003 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable. Non-corrosive IEC. Non-corrosive ASTM 1B.
33000 | 2010 | 1 | 238.4 | 32 | 225.1 | 432.2 | 11.6 | 1.7 | 0 | 0 | 0 | 8 | 0.005 | 70 |  | 227 | 0.004 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 2010 | 1 | 153.2 | 30 | 143.2 | 223.3 | 7.9 | 1.7 | 0.2 | 0.2 | 0 | 4 | 0.001 | 86 |  | 553 | 0.003 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 2010 | 1 | 182.3 | 30 | 171.4 | 273.4 | 8.4 | 1.7 | 0.3 | 0.5 | 0 | 3 | 0.001 | 91 |  | 526 | 0.003 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 2010 | 1 | 262.4 | 42 | 248.6 | 556.1 | 11.6 | 2.1 | 0.1 | 0 | 0 | 5 | 0.003 | 90 |  | 604 | 0.005 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 2010 | 1 | 151.9 | 20 | 130.9 | 234.2 | 18.4 | 1.3 | 1.2 | 0.1 | 0 | 5 | 0.01 | 75 |  | 425 | 0.006 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable. Non-corrosive IEC. Non-corrosive ASTM 3A.
33000 | 2010 | 1 | 216.3 | 38 | 203.9 | 308.4 | 9.7 | 2 | 0.4 | 0.3 | 0 | 3 | 0.001 | 76 |  | 251 | 0.005 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 2010 | 1 | 118.2 | 21 | 88.9 | 163 | 27.3 | 0.8 | 1 | 0.2 | 0 | 4 | 0 | 72 |  | 254 | 0.004 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 2010 | 1 | 157.9 | 41.81 | 146.4 | 585.1 | 8.2 | 2.9 | 0.2 | 0.1 | 0.1 | 7 | 0.003 | 49 |  | 252 | 0.003 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
330000 | 2004 | 2 | 180.3 | 41 | 166.9 | 416.7 | 6.2 | 4.6 | 0.7 | 1.9 | 0 | 5 | 0.01 | 75 | 0 | 23 | 0.02 | DGA is assessed as acceptable. Oil quality is assessed as acceptable. Insulation is assessed as acceptable.
33000 | 2009 | 2 | 520.9 | 38 | 461.6 | 845.8 | 42.9 | 8.7 | 2.2 | 5.5 | 0 | 3 | 0.002 | 91 |  | 124 | 0.008 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 2009 | 2 | 101.4 | 51 | 92.5 | 514.9 | 7.6 | 1.1 | 0 | 0.2 | 0 | 4 | 0.01 | 71 |  | 146 | 0.009 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 2009 | 2 | 79.3 | 41 | 70.8 | 700.2 | 6.1 | 1.9 | 0.2 | 0.3 | 0 | 4 | 0.001 | 96 |  | 41 | 0.023 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 2009 | 2 | 63.8 | 38 | 62.6 | 745 | 0 | 1.2 | 0 | 0 | 0 | 6 | 0.003 | 86 |  | 116 | 0.01 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 2009 | 2 | 540.1 | 56 | 467.5 | 1024.5 | 54.5 | 13.4 | 1.4 | 3.3 | 0 | 4 | 0.002 | 61 |  | 86 | 0.009 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 2009 | 2 | 6570.6 | 40 | 140.4 | 688.1 | 6396.8 | 15 | 0.8 | 17.6 | 0 | 22 | 0 | 39 |  | 163 | 0.006 | Hydrogen level is high. | Breakdown voltage is slightly low. Other oil quality results are assessed as acceptable.
33000 | 2009 | 2 | 1225.3 | 44 | 171 | 525.4 | 1022.9 | 10.6 | 0.7 | 20.1 | 0 | 50 | 0.01 | 18 |  | 197 | 0.004 | Hydrogen level is high. Other dissolved gas levels are assessed as acceptable at present. | Breakdown voltage is low. Other oil quality results are assessed as acceptable.
33000 | 2009 | 2 | 655 | 44 | 169.4 | 420.8 | 470.7 | 5.7 | 0.3 | 8.9 | 0 | 32 | 0.01 | 32 |  | 167 | 0.004 | DGA is assessed as acceptable at present. | Breakdown voltage is low. Other oil quality results are assessed as acceptable.
33000 | 2009 | 2 | 3001.1 | 41.81 | 204.4 | 877.6 | 2753.8 | 16.5 | 1.3 | 25.1 | 0 | 48 | 0.003 | 13 |  | 112 | 0.005 | DGA suggests partial discharge has occurred. | Breakdown voltage is low. Other oil quality results are assessed as acceptable.
33000 | 2009 | 2 | 708 | 41.81 | 333 | 615.4 | 362.5 | 7.2 | 0.4 | 4.9 | 0 | 22 | 0.002 | 40 |  | 109 | 0.009 | Dissolved gas levels are reduced. DGA is assessed as acceptable at present. | Oil quality is assessed as acceptable.
33000 | 2009 | 2 | 359.3 | 41.81 | 325.6 | 939 | 22.5 | 3.6 | 4.6 | 3 | 0 | 4 | 0.002 | 65 |  | 96 | 0.013 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 2009 | 2 | 361.5 | 44 | 338.3 | 613.1 | 17.4 | 4.2 | 1 | 0.6 | 0 | 4 | 0.002 | 84 |  | 137 | 0.008 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 2009 | 2 | 382.7 | 48 | 357.4 | 659 | 18.7 | 4.8 | 1 | 0.8 | 0 | 14 | 0 | 47 |  | 70 | 0.012 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 2009 | 2 | 555.6 | 36 | 145.6 | 444.1 | 240.3 | 21.4 | 15.4 | 3.8 | 129.1 | 12 | 0 | 67 |  | 227 | 0.003 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable. Particle contamination load is within normal limits.
33000 | 2009 | 2 | 162.6 | 32 | 143.7 | 251.4 | 16.4 | 2.2 | 0.1 | 0.2 | 0 | 8 | 0.01 | 75 |  | 86 | 0.013 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable. Non-corrosive IEC. Non-corrosive ASTM 3A.
33000 | 2009 | 2 | 281.9 | 32 | 268.3 | 479.5 | 9.6 | 3.7 | 0.1 | 0.2 | 0 | 3 | 0.002 | 84 |  | 102 | 0.013 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 2009 | 2 | 420.9 | 43 | 349 | 761.9 | 66.4 | 4.5 | 0.4 | 0.6 | 0 | 4 | 0.002 | 91 |  | 76 | 0.02 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable. Non-corrosive IEC. Non-corrosive ASTM 1B.
33000 | 2009 | 2 | 364.6 | 38 | 339.2 | 885.3 | 19 | 4.7 | 1 | 0.7 | 0 | 6 | 0.001 | 63 |  | 81 | 0.013 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 2009 | 2 | 509 | 34 | 481.9 | 974.4 | 18.6 | 6.5 | 2 | 0 | 0 | 7 | 0 | 75 |  | 116 | 0.007 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 2009 | 2 | 181.1 | 36 | 154.1 | 311.2 | 25.4 | 1.6 | 0 | 0 | 0 | 5 | 0.002 | 82 |  | 262 | 0.008 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 2009 | 2 | 351.3 | 27 | 321.5 | 477.4 | 24.1 | 4.8 | 0.5 | 0.4 | 0 | 2 | 0.002 | 75 |  | 86 | 0.01 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 2009 | 2 | 148.6 | 27 | 131.3 | 297.7 | 15.4 | 1.5 | 0.2 | 0.2 | 0 | 2 | 0.003 | 81 |  | 393 | 0.004 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable. Non-corrosive IEC. Non-corrosive ASTM 3A.
33000 | 2009 | 2 | 423.2 | 28 | 369.9 | 744.6 | 48.9 | 3.6 | 0.8 | 0 | 0 | 3 | 0 | 68 |  | 42 | 0.027 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable. Non-corrosive IEC. Non-corrosive ASTM 3A.
33000 | 2009 | 2 | 294 | 31 | 264.5 | 351.2 | 19.1 | 7.1 | 1 | 1.5 | 0.8 | 3 | 0.003 | 79 |  | 196 | 0.009 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable. Non-corrosive IEC. Non-corrosive ASTM 3A.
33000 | 2009 | 2 | 181.7 | 26 | 165.9 | 291.6 | 12.7 | 2.3 | 0.3 | 0.5 | 0 | 5 | 0.01 | 66 |  | 85 | 0.055 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable. Non-corrosive IEC. Non-corrosive ASTM 3A.
33000 | 2009 | 2 | 171.4 | 27 | 149.6 | 268.1 | 19.7 | 1.7 | 0.3 | 0.1 | 0 | 4 | 0.002 | 73 |  | 157 | 0.006 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 2009 | 2 | 448.6 | 41 | 414 | 664.9 | 28.8 | 5.1 | 0.7 | 0 | 0 | 7 | 0 | 95 |  | 158 | 0.008 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 2009 | 2 | 324.3 | 34 | 287.2 | 382.9 | 33.2 | 2.8 | 0.6 | 0.5 | 0 | 2 | 0.004 | 82 |  | 214 | 0.005 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 2009 | 2 | 391.8 | 30 | 358.4 | 522.1 | 27.5 | 4.8 | 0.8 | 0.3 | 0 | 3 | 0.002 | 85 |  | 144 | 0.007 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 2009 | 2 | 0 | 43 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0
33000 | 2009 | 2 | 208.8 | 36 | 197.9 | 283.6 | 8.5 | 2.1 | 0.1 | 0.2 | 0 | 2 | 0.006 | 80 |  | 311 | 0.008 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 2009 | 2 | 299.1 | 40 | 294.6 | 493.5 | 0 | 2.6 | 1.6 | 0.3 | 0 | 5 | 0 | 98 |  | 73 | 0.017 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 2009 | 2 | 190.3 | 43 | 177.5 | 275.5 | 10.1 | 1.8 | 0.3 | 0.6 | 0 | 4 | 0.002 | 92 |  | 279 | 0.004 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 2009 | 2 | 290.1 | 46 | 270.1 | 471.9 | 14.1 | 3.2 | 1.5 | 1.2 | 0 | 6 | 0.002 | 86 |  | 294 | 0.004 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 2009 | 2 | 191 | 35 | 179.8 | 262.8 | 9.8 | 1.3 | 0.1 | 0 | 0 | 2 | 0.002 | 81 |  | 123 | 0.007 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 2009 | 2 | 252.7 | 15 | 241.7 | 343.1 | 8.1 | 1.7 | 1 | 0.2 | 0 | 5 | 0.002 | 77 |  | 175 | 0.009 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 2009 | 2 | 366.8 | 15 | 218.2 | 460.1 | 117.5 | 11.1 | 5.8 | 14.2 | 0 | 10 | 0.01 | 84 |  | 189 | 0.007 | DGA suggests partial discharge has occurred. | Oil quality is assessed as acceptable.
33000 | 2009 | 2 | 213 | 36 | 199.2 | 310.7 | 10.5 | 1.4 | 0.6 | 0.7 | 0.6 | 7 | 0.001 | 95 |  | 183 | 0.005 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 2009 | 2 | 197.2 | 30 | 182.4 | 299.6 | 12.5 | 1.8 | 0.1 | 0.4 | 0 | 4 | 0 | 84 |  | 238 | 0.007 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 2009 | 2 | 398.4 | 47 | 378.6 | 652.5 | 14.7 | 3.4 | 0.9 | 0.8 | 0 | 5 | 0.01 | 81 |  | 299 | 0.006 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 2009 | 2 | 176.1 | 33 | 163.8 | 283.7 | 10.6 | 1.7 | 0 | 0 | 0 | 7 | 0.005 | 93 |  | 536 | 0.005 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 2009 | 2 | 105.8 | 44 | 92.3 | 242.3 | 11.7 | 1 | 0.4 | 0.4 | 0 | 11 | 0 | 70 |  | 87 | 0.015 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 2009 | 2 | 102.3 | 31 | 96.2 | 185 | 5.1 | 1 | 0 | 0 | 0 | 4 | 0.003 | 76 |  | 211 | 0.008 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable. Non-corrosive IEC. Non-corrosive ASTM 3A.
33000 | 2009 | 2 | 191.5 | 20 | 182.6 | 322.4 | 7.1 | 1.5 | 0.1 | 0.2 | 0 | 2 | 0.004 | 80 |  | 522 | 0.004 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable. Non-corrosive IEC. Non-corrosive ASTM 3A.
33000 | 2009 | 2 | 165.7 | 30 | 151.3 | 207.9 | 11.8 | 2.6 | 0 | 0 | 0 | 2 | 0 | 90 |  | 200 | 0.004 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 2009 | 2 | 195.7 | 33 | 186.5 | 306.4 | 7.5 | 1.7 | 0 | 0 | 0 | 5 | 0 | 79 |  | 370 | 0.004 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 2009 | 2 | 254.8 | 35 | 243.4 | 393.6 | 8.8 | 2.1 | 0.2 | 0.3 | 0 | 5 | 0.002 | 86 |  | 682 | 0.003 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable. Non-corrosive IEC. Non-corrosive ASTM 3A.
330000 | 2004 | 3 | 149.7 | 41.81 | 131 | 295.7 | 6.5 | 7.1 | 0.5 | 4.6 | 0 | 10 | 0.01 | 69 | 0 | 166 | 0.002 | DGA is assessed as acceptable. Oil quality is assessed as acceptable. Non-corrosive IEC. Insulation is assessed as acceptable.
33000 | 2008 | 3 | 43.5 | 41.81 | 41.3 | 139.3 | 0 | 1.4 | 0 | 0.8 | 0 | 3 | 0 | 71 |  | 303 | 0.005 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 2008 | 3 | 185.2 | 90 | 165.4 | 556.7 | 8 | 6 | 0.3 | 5.5 | 0 | 3 | 0.01 | 75 |  | 38 | 0.029 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable. Non-corrosive IEC. Non-corrosive ASTM 3A.
33000 | 2008 | 3 | 146 | 32 | 112.6 | 1221.1 | 19.2 | 3 | 1 | 10.2 | 0 | 2 | 0.007 | 53 |  | 14 | 0.044 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 2008 | 3 | 114.4 | 33 | 76.1 | 1228.4 | 25.2 | 3.6 | 1.7 | 7.8 | 0 | 1 | 0.007 | 86 |  | 22 | 0.025 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 2008 | 3 | 160.7 | 30 | 144.7 | 350.9 | 9.4 | 6 | 0 | 0.6 | 0 | 7 | 0.01 | 75 |  | 173 | 0.012 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable. Non-corrosive IEC. Non-corrosive ASTM 3A.
33000 | 2008 | 3 | 118.8 | 36 | 107.8 | 915.3 | 4.8 | 2.7 | 0.4 | 3.1 | 0 | 7 | 0.004 | 86 |  | 124 | 0.01 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable. Non-corrosive IEC. Non-corrosive ASTM 3A.
33000 | 2008 | 3 | 111.2 | 36 | 99.4 | 1134.6 | 2.8 | 2.5 | 1.9 | 4.6 | 0 | 6 | 0.001 | 91 |  | 68 | 0.009 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 2008 | 3 | 129.5 | 30 | 116.9 | 351.2 | 9.6 | 2.1 | 0.2 | 0.7 | 0 | 4 | 0.001 | 94 |  | 152 | 0.012 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable. Non-corrosive IEC. Non-corrosive ASTM 3A.
33000 | 2008 | 3 | 127.8 | 36 | 113 | 1014.9 | 5.4 | 3.1 | 1.2 | 5.1 | 0 | 5 | 0.003 | 76 |  | 67 | 0.021 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable. Non-corrosive IEC. Non-corrosive ASTM 3A.
33000 | 2008 | 3 | 135.7 | 34 | 97.2 | 1288.6 | 5.3 | 4.6 | 3.6 | 25 | 0 | 7 | 0.001 | 81 |  | 150 | 0.006 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 2008 | 3 | 183.9 | 56 | 137.7 | 613.5 | 42 | 1.1 | 1 | 2.1 | 0 | 6 | 0.01 | 71 |  | 226 | 0.003 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable. Non-corrosive IEC. Non-corrosive ASTM 3A.
33000 | 2008 | 3 | 152.8 | 34 | 104.3 | 674.9 | 34.9 | 4.4 | 1.3 | 7.4 | 0.5 | 4 | 0 | 75 |  | 57 | 0.01 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable. Non-corrosive IEC. Non-corrosive ASTM 3A.
33000 | 2008 | 3 | 129.5 | 34 | 94.6 | 941.6 | 21.5 | 2.9 | 0.6 | 9.9 | 0 | 3 | 0.001 | 79 |  | 160 | 0.004 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable. Non-corrosive IEC. Non-corrosive ASTM 3B.
33000 | 2008 | 3 | 111 | 29 | 76.9 | 917.6 | 22.6 | 2.6 | 0.5 | 8.4 | 0 | 1 | 0.005 | 85 |  | 348 | 0.002 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable. Non-corrosive IEC. Non-corrosive ASTM 3A.
33000 | 2008 | 3 | 164.4 | 30 | 103.4 | 1140.1 | 53 | 3.2 | 3.3 | 1.5 | 0 | 2 | 0.002 | 78 |  | 221 | 0.002 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 2008 | 3 | 112.6 | 29 | 93.4 | 834.6 | 4.7 | 3.1 | 2.4 | 9 | 0 | 4 | 0.002 | 73 |  | 69 | 0.012 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 2008 | 3 | 84 | 27 | 63.4 | 926.1 | 10.5 | 2.4 | 1.9 | 5.8 | 0 | 22 | 0.003 | 66 |  | 72 | 0.008 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 2008 | 3 | 175.4 | 48 | 156.3 | 572 | 12.8 | 2.5 | 1.7 | 1.3 | 0.8 | 4 | 0.01 | 75 |  | 54 | 0.017 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 2008 | 3 | 107.2 | 34 | 101 | 652 | 6 | 0.1 | 0.1 | 0 | 0 | 2 | 0.01 | 75 |  | 52 | 0.013 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable. Non-corrosive IEC. Non-corrosive ASTM 2C.
33000 | 2008 | 3 | 116.1 | 37 | 105.8 | 983.5 | 4.8 | 2.8 | 0.6 | 1.9 | 0.2 | 6 | 0.003 | 92 |  | 149 | 0.01 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 2008 | 3 | 96.7 | 36 | 93.8 | 967.8 | 0 | 1.7 | 1.2 | 0 | 0 | 8 | 0.008 | 65 |  | 131 | 0.003 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 2008 | 3 | 551 | 35 | 442.4 | 476.7 | 77.1 | 21.1 | 1.1 | 9.3 | 0 | 4 | 0.002 | 98 |  | 164 | 0.01 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable. Non-corrosive IEC. Non-corrosive ASTM 3A.
33000 | 2008 | 3 | 473.6 | 34 | 319.1 | 702.2 | 21.8 | 29.6 | 9.1 | 94 | 0 | 55 | 0.002 | 21 |  | 273 | 0.003 | DGA is assessed as acceptable. | Breakdown voltage is low. Other oil quality results are assessed as acceptable. Possible sample contamination.
33000 | 2008 | 3 | 425.9 | 38 | 306.4 | 604.7 | 18.3 | 28.2 | 5.2 | 67.4 | 0.4 | 7 | 0.001 | 77 |  | 190 | 0.007 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 2008 | 3 | 316.2 | 72 | 262.2 | 442.5 | 41.1 | 4.7 | 0.8 | 7.4 | 0 | 5 | 0.001 | 77 |  | 215 | 0.007 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable. Non-corrosive IEC. Non-corrosive ASTM 3A.
33000 | 2008 | 3 | 422.6 | 37 | 354.5 | 843.6 | 28.4 | 13.6 | 4.2 | 21.9 | 0 | 4 | 0.005 | 73 |  | 99 | 0.009 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 2008 | 3 | 408.5 | 36 | 313.1 | 851.5 | 28.9 | 19.7 | 4 | 42.8 | 0 | 6 | 0.006 | 75 |  | 125 | 0.008 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 2008 | 3 | 279.9 | 37 | 222.2 | 405.5 | 49.4 | 3.4 | 0.8 | 4.1 | 0 | 6 | 0 | 75 |  | 136 | 0.008 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable. Non-corrosive IEC. Non-corrosive ASTM 3A.
33000 | 2008 | 3 | 397.6 | 41 | 284.4 | 601.2 | 38.3 | 25.2 | 2.7 | 47 | 0 | 4 | 0.004 | 89 |  | 110 | 0.009 | DGA is assessed as acceptable at present. | Oil quality is assessed as acceptable. Non-corrosive IEC. Non-corrosive ASTM 3B.
33000 | 2008 | 3 | 565.3 | 71 | 365.6 | 861.8 | 139.7 | 27.6 | 2.2 | 30.2 | 0 | 6 | 0.01 | 75 |  | 67 | 0.012 | DGA is assessed as acceptable at present. | Oil quality is assessed as acceptable. Non-corrosive IEC. Non-corrosive ASTM 3A.
33000 | 2008 | 3 | 336.6 | 78 | 196.5 | 952.9 | 19.9 | 40.4 | 3.3 | 76.5 | 0 | 13 | 0.01 | 71 |  | 53 | 0.015 | DGA suggests mild oil overheating (<300C) has occurred. | Oil quality is assessed as acceptable.
33000 | 2008 | 3 | 500.8 | 71 | 284 | 1071.5 | 68.6 | 59.9 | 3.4 | 84.9 | 0 | 7 | 0.01 | 75 |  | 81 | 0.011 | DGA suggests mild oil overheating (<300C) has occurred. | Oil quality is assessed as acceptable.
33000 | 2008 | 3 | 516.9 | 73 | 296.7 | 1105.5 | 33.7 | 71.2 | 3.4 | 111.8 | 0.1 | 2 | 0.01 | 75 |  | 24 | 0.028 | DGA suggests mild oil overheating (<300C) has occurred. | Oil quality is assessed as acceptable.
33000 | 2008 | 3 | 204.6 | 81 | 89 | 587.1 | 13.4 | 31.5 | 1.9 | 68.8 | 0 | 6 | 0.01 | 75 |  | 72 | 0.011 | Dissolved gas levels are reduced. | Oil quality is assessed as acceptable.
33000 | 2008 | 3 | 209 | 77 | 80 | 687.6 | 15 | 37 | 2 | 75 | 0 | 5 | 0.01 | 75 |  | 48 | 0.016 | DGA suggests mild oil overheating (<300C) has occurred. | Oil quality is assessed as acceptable.
33000 | 2008 | 3 | 221.2 | 77 | 95 | 697.4 | 10.1 | 34.9 | 2.1 | 79.1 | 0 | 3 | 0.01 | 75 |  | 82 | 0.012 | DGA suggests mild oil overheating (<300C) has occurred. | Oil quality is assessed as acceptable.
33000 | 2008 | 3 | 236.3 | 56 | 98.9 | 796.5 | 12.1 | 37.4 | 2.2 | 85.7 | 0 | 7 | 0.01 | 52 |  | 78 | 0.015 | DGA suggests mild oil overheating (<300C) has occurred. | Oil quality is assessed as acceptable.
33000 | 2008 | 3 | 218.5 | 75 | 82.3 | 809.6 | 12 | 32.7 | 2.5 | 88.4 | 0.6 | 8 | 0 | 86 |  | 59 | 0.012 | DGA suggests mild oil overheating (<300C) has occurred. | Oil quality is assessed as acceptable.
33000 | 2008 | 3 | 191.6 | 78 | 64.1 | 854 | 7.7 | 38.3 | 1.6 | 79.9 | 0 | 13 | 0.001 | 80 |  | 26 | 0.026 | Dissolved gas levels are relatively stable. | Oil quality is assessed as acceptable.
33000 | 2008 | 3 | 157.4 | 77 | 47.8 | 870.1 | 0 | 29.2 | 2.1 | 78.3 | 0 | 16 | 0.002 | 86 |  | 49 | 0.024 | Dissolved gas levels are relatively stable. | Oil quality is assessed as acceptable.
33000 | 2008 | 3 | 257.3 | 35 | 88.6 | 765.2 | 20 | 50.6 | 2.4 | 95.7 | 0 | 6 | 0.001 | 87 |  | 101 | 0.012 | Dissolved gas levels are relatively stable. | Oil quality is assessed as acceptable.
33000 | 2008 | 3 | 282.7 | 37 | 95.4 | 710.2 | 18.5 | 54.9 | 7.5 | 106.4 | 0 | 5 | 0 | 86 |  | 74 | 0.012 | DGA suggests mild oil overheating (<300C) has occurred. | Oil quality is assessed as acceptable.
33000 | 2008 | 3 | 327.5 | 34 | 267.2 | 522.9 | 44.5 | 4.4 | 1 | 10.4 | 0 | 5 | 0.003 | 86.5 |  | 91 | 0.008 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 2008 | 3 | 355.3 | 30 | 253.6 | 1040.5 | 47.8 | 14.5 | 3.4 | 36 | 0 | 6 | 0.002 | 100 |  | 65 | 0.011 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 2008 | 3 | 222.5 | 35 | 169.9 | 644.2 | 25.1 | 5.7 | 1.6 | 20.2 | 0 | 23 | 0.003 | 47 |  | 214 | 0.003 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 2008 | 3 | 257 | 38 | 183.4 | 565.9 | 34.2 | 11.8 | 2.4 | 25.2 | 0 | 6 | 0 | 76 |  | 65 | 0.009 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 2008 | 3 | 491.1 | 39 | 311.7 | 830.9 | 14.2 | 59.6 | 5.4 | 100.2 | 0 | 2 | 0.01 | 75 |  | 94 | 0.013 | DGA suggests mild oil overheating (<300C) has occurred. | Oil quality is assessed as acceptable.
33000 | 2008 | 3 | 510.2 | 65 | 300.3 | 920.6 | 9.7 | 69.3 | 6.9 | 124 | 0 | 5 | 0.01 | 70 |  | 78 | 0.01 | DGA suggests mild oil overheating (<300C) has occurred. | Oil quality is assessed as acceptable.
33000 | 2008 | 3 | 577.5 | 55 | 349.2 | 990.8 | 11.1 | 78 | 7.1 | 131.4 | 0.7 | 4 | 0.01 | 75 |  | 124 | 0.008 | DGA suggests mild oil overheating (<300C) has occurred. | Oil quality is assessed as acceptable.
33000 | 2008 | 3 | 513 | 48 | 301.4 | 930.1 | 9.8 | 71.4 | 5.7 | 124.7 | 0 | 6 | 0.01 | 75 |  | 136 | 0.008 | DGA suggests mild oil overheating (<300C) has occurred. | Oil quality is assessed as acceptable.
33000 | 2008 | 3 | 557 | 64 | 326.6 | 1011.3 | 10 | 81.5 | 5.9 | 133 | 0 | 6 | 0.005 | 92 |  | 87 | 0.01 | DGA suggests mild oil overheating (<300C) has occurred. | Oil quality is assessed as acceptable.
33000 | 2008 | 3 | 534.2 | 64 | 304.1 | 939.6 | 9.1 | 76.4 | 6.3 | 138.3 | 0 | 9 | 0.001 | 83 |  | 95 | 0.009 | DGA suggests mild oil overheating (<300C) has occurred. | Oil quality is assessed as acceptable.
33000 | 2008 | 3 | 732.7 | 58 | 328.7 | 946.3 | 12.3 | 99.8 | 115.2 | 173.8 | 2.9 | 7 | 0.001 | 77 |  | 88 | 0.01 | Dissolved gas levels are increased. DGA suggests mild oil overheating (<300C) has occurred. | Oil quality is assessed as acceptable.
33000 | 2008 | 3 | 210.5 | 52 | 172.7 | 346 | 36.1 | 1 | 0.3 | 0.4 | 0 | 3 | 0 | 75 |  | 87 | 0.013 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable. Non-corrosive IEC. Non-corrosive ASTM 3A.
33000 | 2008 | 3 | 522.9 | 41.81 | 419.3 | 754.7 | 86.5 | 9.5 | 1.3 | 6.3 | 0 | 4 | 0.002 | 86 |  | 139 | 0.009 | DGA is assessed as acceptable at present. | Oil quality is assessed as acceptable.
33000 | 2008 | 3 | 431.2 | 25 | 321.3 | 823.3 | 79.4 | 7.5 | 2.2 | 20.8 | 0 | 55 | 0 | 74 |  | 95 | 0.006 | DGA is assessed as acceptable at present. | Oil quality is assessed as acceptable. Non-corrosive IEC. Non-corrosive ASTM 3A.
33000 | 2008 | 3 | 440.3 | 36 | 341.4 | 488.3 | 82.9 | 5.7 | 0.9 | 9.4 | 0 | 4 | 0.01 | 75 |  | 48 | 0.017 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable. Non-corrosive IEC. Non-corrosive ASTM 3A.
33000 | 2008 | 3 | 449.4 | 39 | 341.1 | 665.9 | 89.8 | 6.9 | 1.1 | 10.5 | 0 | 4 | 0 | 75 |  | 58 | 0.013 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable. Non-corrosive IEC. Non-corrosive ASTM 3A.
33000 | 2008 | 3 | 377.3 | 37 | 302.4 | 692 | 45.8 | 11.6 | 1.5 | 16 | 0 | 6 | 0.004 | 87 |  | 59 | 0.01 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable. Non-corrosive IEC. Non-corrosive ASTM 3A.
33000 | 2008 | 3 | 362.3 | 28 | 290.1 | 701.1 | 33.9 | 17.4 | 1.4 | 19.5 | 0 | 5 | 0.002 | 90 |  | 88 | 0.007 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable. Non-corrosive IEC. Non-corrosive ASTM 3A.
33000 | 2008 | 3 | 254.1 | 32 | 221.4 | 342.5 | 29.1 | 3.2 | 0.2 | 0.2 | 0 | 3 | 0.01 | 75 |  | 39 | 0.05 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 2008 | 3 | 15.9 | 21 | 7.4 | 520.5 | 6.2 | 1.4 | 0.2 | 0.7 | 0 | 18 | 0.001 | 48 |  | 169 | 0.006 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable. Particle contamination load is marginal.
33000 | 2008 | 3 | 350.5 | 21 | 319.6 | 512.7 | 25.7 | 4 | 0.7 | 0.5 | 0 | 4 | 0.01 | 75 |  | 125 | 0.008 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 2008 | 3 | 12.6 | 18 | 10.6 | 182.7 | 1.5 | 0.3 | 0.1 | 0.1 | 0 | 5 | 0.007 | 69 |  | 91 | 0.007 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 2008 | 3 | 13.2 | 15 | 9 | 266.9 | 2.1 | 0.4 | 1.1 | 0.6 | 0 | 6 | 0 | 74 |  | 110 | 0.009 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable. Non-corrosive IEC.
33000 | 2008 | 3 | 233.8 | 58 | 220.9 | 397.2 | 10.6 | 2 | 0.1 | 0.2 | 0 | 3 | 0.002 | 95 |  | 290 | 0.003 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 2008 | 3 | 329 | 44 | 315.7 | 600.9 | 9.8 | 3.1 | 0.4 | 0 | 0 | 6 | 0 | 83 |  | 439 | 0.003 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 2008 | 3 | 186.7 | 52 | 125 | 454.1 | 54.2 | 3.8 | 0.5 | 3.2 | 0 | 3 | 0.01 | 75 |  | 953 | 0.001 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable. Non-corrosive IEC. Non-corrosive ASTM 3A.
33000 | 2008 | 3 | 228 | 56 | 157.6 | 821.3 | 59.6 | 4.5 | 0.5 | 5.8 | 0 | 7 | 0.01 | 75 |  | 935 | 0.002 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable. Non-corrosive IEC. Non-corrosive ASTM 3A.
33000 | 2008 | 3 | 116.4 | 48 | 85.2 | 948.8 | 21.3 | 3.3 | 0.5 | 6.1 | 0 | 14 | 0.01 | 26 |  | 229 | 0.002 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable. Non-corrosive IEC. Non-corrosive ASTM 3A.
33000 | 2008 | 3 | 136.5 | 52 | 94.4 | 1019.1 | 31.6 | 3.2 | 0.5 | 6.8 | 0 | 4 | 0.006 | 88 |  | 240 | 0.002 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable. Non-corrosive IEC. Non-corrosive ASTM 3A.
33000 | 2008 | 3 | 195.9 | 46 | 116 | 1202.2 | 64.1 | 8.5 | 0.6 | 6.7 | 0 | 0 | 0.003 | 94 |  | 122 | 0.004 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 2007 | 4 | 72.8 | 39 | 67.6 | 438.8 | 3.3 | 1.6 | 0.1 | 0.2 | 0 | 3 | 0.01 | 75 |  | 95 | 0.019 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 2007 | 4 | 88.7 | 40 | 79.5 | 881 | 2.8 | 2.4 | 0.1 | 3.9 | 0 | 4 | 0.01 | 75 |  | 124 | 0.011 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable. Corrosive IEC. Corrosive ASTM 4A.
33000 | 2007 | 4 | 64.9 | 42 | 58.3 | 857.4 | 1.4 | 2.1 | 0.7 | 2.4 | 0 | 2 | 0.002 | 89 |  | 97 | 0.009 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable. Corrosive IEC. Corrosive ASTM 4A.
33000 | 2007 | 4 | 64.2 | 22 | 57.9 | 580.9 | 0.4 | 1.5 | 0.2 | 4.2 | 0 | 8 | 0.01 | 75 |  | 38 | 0.02 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 2007 | 4 | 45 | 41.81 | 41.2 | 683.7 | 0 | 1.4 | 0.4 | 2 | 0 | 3 | 0.001 | 57 |  | 68 | 0.011 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 2007 | 4 | 71.2 | 41.81 | 51.6 | 2995.5 | 17.9 | 1.2 | 0.1 | 0.4 | 0 | 10 | 0.005 | 88 |  | 20 | 0.02 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 2007 | 4 | 181.2 | 42 | 157.1 | 945.2 | 12.9 | 4.2 | 0.8 | 6.2 | 0 | 10 | 0.003 | 49 |  | 38 | 0.016 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable. Corroisve IEC. Corrosive ASTM 4A.
33000 | 2007 | 4 | 197.6 | 63 | 158 | 1792.9 | 14.3 | 6.3 | 1.9 | 17.1 | 0 | 10 | 0.004 | 86 |  | 11 | 0.034 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 2007 | 4 | 223.8 | 40 | 149.5 | 1695.3 | 51.1 | 6.6 | 3.1 | 13.5 | 0 | 4 | 0.011 | 86 |  | 33 | 0.009 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 2007 | 4 | 265.3 | 54 | 146.9 | 1231.9 | 43.6 | 19.5 | 5.7 | 49.6 | 0 | 3 | 0.006 | 96 |  | 176 | 0.003 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable. Corrosive IEC. Corrosive ASTM 4A.
33000 | 2007 | 4 | 209.2 | 45 | 102.8 | 1247.7 | 43.5 | 10.9 | 5 | 47 | 0 | 4 | 0.006 | 96 |  | 89 | 0.004 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable. Corrosive IEC. Corrosive ASTM 4A.
33000 | 2007 | 4 | 358.7 | 48 | 159.3 | 1408.4 | 143.1 | 12 | 4.5 | 39.8 | 0 | 3 | 0.007 | 83 |  | 41 | 0.008 | DGA is assessed as acceptable at present. | Oil quality is assessed as acceptable.
33000 | 2007 | 4 | 106.9 | 32 | 98.6 | 588.8 | 4.9 | 2 | 0.5 | 0.9 | 0 | 3 | 0.01 | 75 |  | 105 | 0.014 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable. Corrosive IEC. Corrosive ASTM 4A.
33000 | 2007 | 4 | 1452.2 | 41.81 | 104 | 2125.3 | 1292.8 | 14.5 | 0.7 | 40.2 | 0 | 18 | 0.005 | 37 |  | 53 | 0.006 | DGA suggests partial discharge has occurred. | Breakdown voltage is low. Other oil quality results are assessed as acceptable.
33000 | 2007 | 4 | 76.5 | 41.81 | 67.5 | 808.8 | 1.5 | 2.8 | 2.3 | 2.4 | 0 | 4 | 0.003 | 59 |  | 42 | 0.02 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 2007 | 4 | 65.8 | 38 | 56.8 | 810.4 | 2.4 | 3.1 | 0.8 | 2.7 | 0 | 5 | 0.004 | 53 |  | 26 | 0.026 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 2007 | 4 | 81 | 24 | 77.4 | 558 | 0 | 2.1 | 0 | 1.5 | 0 | 4 | 0.01 | 75 |  | 66 | 0.014 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 2007 | 4 | 97.1 | 24 | 83.6 | 603.8 | 9.4 | 1.8 | 1 | 1.3 | 0 | 3 | 0.01 | 67 |  | 65 | 0.015 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 2007 | 4 | 76.4 | 25 | 67.6 | 880.2 | 5 | 2.1 | 1 | 0.7 | 0 | 6 | 0.002 | 88 |  | 78 | 0.013 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable. Corrosive IEC. Corrosive ASTM 4A.
33000 | 2007 | 4 | 124.4 | 32 | 108 | 439.1 | 13.1 | 2 | 0.4 | 0.9 | 0 | 4 | 0.01 | 71 |  | 35 | 0.019 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 2007 | 4 | 90 | 39 | 80.3 | 578.6 | 3.2 | 2.5 | 0.8 | 3.2 | 0 | 5 | 0.002 | 79 |  | 58 | 0.018 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable. Corrosive IEC. Corrosive ASTM 4A.
33000 | 2007 | 4 | 92.4 | 41 | 83.6 | 891.6 | 2.9 | 2.2 | 0.8 | 2.9 | 0 | 4 | 0.005 | 56 |  | 67 | 0.007 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable. Corrosive IEC. Corrosive ASTM 4A.
33000 | 2007 | 4 | 93 | 25.6 | 73.8 | 349.6 | 15.1 | 1.8 | 0.5 | 1.8 | 0 | 4 | 0.01 | 75 |  | 73 | 0.013 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 2007 | 4 | 114.7 | 24 | 59.3 | 798.7 | 12.9 | 2.7 | 2.5 | 37.3 | 0 | 65 | 0.01 | 13 |  | 31 | 0.022 | DGA is assessed as acceptable. | Breakdown voltage is low. Other oil quality results are assessed as acceptable.
33000 | 2007 | 4 | 71.3 | 24 | 53.5 | 736.7 | 4.6 | 2 | 1.4 | 9.8 | 0 | 31 | 0.005 | 23 |  | 113 | 0.006 | DGA is assessed as acceptable. | Breakdown voltage is low. Oil sample was cloudy in appearance. Other oil quality results are assessed as acceptable.
33000 | 2007 | 4 | 57 | 28 | 48.2 | 830.2 | 3.4 | 1.4 | 2.1 | 1.9 | 0 | 40 | 0.003 | 24 |  | 164 | 0.003 | DGA is assessed as acceptable. | Breakdown voltage is low. Other oil quality results are assessed as acceptable.
33000 | 2007 | 4 | 64.7 | 37 | 56.1 | 849.2 | 5.9 | 1.5 | 0.3 | 0.9 | 0 | 56 | 0.001 | 12 |  | 52 | 0.013 | DGA is assessed as acceptable. | Breakdown voltage is low. Other oil quality results are assessed as acceptable.
33000 | 2007 | 4 | 107.9 | 40 | 98.3 | 577.6 | 3.7 | 2.3 | 2.2 | 1.4 | 0 | 8 | 0.01 | 75 |  | 79 | 0.016 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable. Corrosive IEC. Corrosive ASTM 4A.
33000 | 2007 | 4 | 88.1 | 41.81 | 78.7 | 933.7 | 1.8 | 2.4 | 1.7 | 3.5 | 0 | 69 | 0.005 | 14 |  | 103 | 0.006 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 2007 | 4 | 63.4 | 44 | 56.7 | 903 | 2.1 | 2.8 | 0.6 | 1.2 | 0 | 56 | 0.003 | 19 |  | 147 | 0.005 | DGA is assessed as acceptable. | Breakdown voltage is low. Oil sample is cloudy in appearance. Other oil quality results are assessed as acceptable.
33000 | 2007 | 4 | 83.1 | 37 | 73.4 | 927.1 | 3.7 | 2.5 | 1.6 | 1.9 | 0 | 22 | 0.001 | 34 |  | 32 | 0.028 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 2007 | 4 | 157.8 | 33 | 146.8 | 578.3 | 7.4 | 2.7 | 0.4 | 0.5 | 0 | 12 | 0.01 | 74 |  | 28 | 0.018 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 2007 | 4 | 107.6 | 45 | 102 | 886.8 | 0 | 2.5 | 0 | 3.1 | 0 | 4 | 0.01 | 75 |  | 28 | 0.016 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 2007 | 4 | 92.8 | 36 | 84.2 | 1012 | 3.5 | 2.1 | 0.9 | 2.1 | 0 | 2 | 0.002 | 70 |  | 35 | 0.012 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 2007 | 4 | 87.7 | 32 | 68.8 | 914 | 1.8 | 7.9 | 4 | 5.2 | 0 | 3 | 0 | 79 |  | 38 | 0.01 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 2007 | 4 | 83.2 | 31 | 68.6 | 298.6 | 9.6 | 1.6 | 1.8 | 1.6 | 0 | 2 | 0.01 | 75 |  | 66 | 0.011 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 2007 | 4 | 74.2 | 40 | 65 | 658.1 | 4.9 | 1.7 | 0.2 | 2.4 | 0 | 3 | 0.003 | 92 |  | 44 | 0.019 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 2007 | 4 | 55.9 | 41.81 | 42 | 652.5 | 5.3 | 1.3 | 6.7 | 0.6 | 0 | 15 | 0.004 | 57 |  | 77 | 0.01 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 2007 | 4 | 194.5 | 29 | 160.4 | 654.4 | 23.8 | 4.1 | 0.7 | 5.4 | 0.1 | 3 | 0.01 | 75 |  | 58 | 0.012 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 2007 | 4 | 364.9 | 60 | 117.7 | 1301.5 | 115 | 35.3 | 30.9 | 66 | 0 | 11 | 0.007 | 80 |  | 24 | 0.02 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 2007 | 4 | 735.5 | 55 | 287 | 2328.6 | 410.3 | 10.1 | 6.5 | 21.6 | 0 | 67 | 0.026 | 27 |  | 23 | 0.009 | DGA is assessed as acceptable at present. | Breakdown voltage is low. Oil is cloudy in appearance. Other oil quality results are assessed as acceptable.
33000 | 2007 | 4 | 505.2 | 62 | 224 | 2227.2 | 250.2 | 8.4 | 4.4 | 18.2 | 0 | 15 | 0.025 | 77 |  | 9 | 0.028 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 2007 | 4 | 418.2 | 41 | 231.8 | 2253.7 | 167.8 | 5.1 | 4.2 | 9.3 | 0 | 13 | 0.037 | 79 |  | 17 | 0.015 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 2007 | 4 | 128.5 | 33 | 105.9 | 428 | 15.8 | 2.2 | 0.4 | 4.2 | 0 | 4 | 0.01 | 75 |  | 71 | 0.013 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 2007 | 4 | 141.9 | 37 | 121.3 | 920.2 | 9.4 | 4.3 | 0.6 | 6.3 | 0 | 3 | 0.01 | 75 |  | 76 | 0.01 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable. Corrosive IEC. Corrosive ASTM 4A.
33000 | 2007 | 4 | 125 | 39 | 95.9 | 918.6 | 13.1 | 4.1 | 0.6 | 11.3 | 0 | 5 | 0.01 | 75 |  | 163 | 0.003 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable. Corrosive IEC. Corrosive ASTM 4A
33000 | 2007 | 4 | 161.5 | 36 | 86.9 | 1069 | 27.9 | 7.9 | 2.1 | 36.7 | 0 | 8 | 0.004 | 76 |  | 43 | 0.018 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable. Non-corrosive IEC. Non-corrosive ASTM 3A.
330000 | 2004 | 5 | 200.4 | 41.81 | 151.1 | 402.6 | 12.3 | 16.4 | 0.9 | 19.7 | 0 | 6 | 0.001 | 59 | 0 | 392 | 0.002 | DGA is assessed as acceptable. Oil quality is assessed as acceptable. Insulation is assessed as acceptable.
33000 | 2006 | 5 | 126.2 | 35 | 81.1 | 571.6 | 5.1 | 4.4 | 3.4 | 32.2 | 0 | 2 | 0.003 | 96 |  | 194 | 0.008 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 2006 | 5 | 90.9 | 41 | 73.7 | 749.5 | 4.5 | 2.4 | 0.6 | 9.7 | 0 | 3 | 0.004 | 88 |  | 109 | 0.011 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 2006 | 5 | 89.3 | 42 | 72.9 | 834.2 | 8.6 | 2.3 | 0.3 | 5.2 | 0 | 5 | 0.004 | 84 |  | 103 | 0.006 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 2006 | 5 | 91.3 | 32 | 72.1 | 368.5 | 14.5 | 1.7 | 0.3 | 2.7 | 0 | 3 | 0.01 | 72 |  | 53 | 0.012 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 2006 | 5 | 143.6 | 45 | 120.4 | 909.7 | 12.4 | 2.9 | 0.5 | 7.4 | 0 | 3 | 0.01 | 66 |  | 30 | 0.024 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 2006 | 5 | 123.9 | 46 | 105.4 | 1110.4 | 8.2 | 3 | 0.6 | 6.7 | 0 | 3 | 0.005 | 95 |  | 49 | 0.012 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable. Corrosive IEC. Corrosive ASTM 4A.
33000 | 2006 | 5 | 68.7 | 37 | 58.4 | 857.4 | 0 | 2.4 | 1.1 | 6.8 | 0 | 17 | 0.015 | 48 |  | 55 | 0.01 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 2006 | 5 | 109.9 | 48 | 81.3 | 385.5 | 16.4 | 3.6 | 0 | 8.6 | 0 | 6 | 0.01 | 71 |  | 63 | 0.011 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 2006 | 5 | 92.2 | 32 | 80.1 | 719.4 | 0 | 2.4 | 0.5 | 9 | 0.2 | 2 | 0.01 | 75 |  | 78 | 0.01 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 2006 | 5 | 102.1 | 32 | 84.3 | 1035.7 | 4.7 | 2.4 | 0.2 | 10.4 | 0.1 | 7 | 0 | 75 |  | 56 | 0.012 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable. Corrosive IEC. Corrosive ASTM 4A.
33000 | 2006 | 5 | 93 | 46 | 76.8 | 1066 | 7.9 | 2.2 | 0.4 | 5.5 | 0.2 | 4 | 0.004 | 79 |  | 64 | 0.009 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 2006 | 5 | 78.1 | 43 | 59.8 | 368.5 | 11.7 | 2.6 | 0.8 | 3.2 | 0 | 5 | 0.01 | 75 |  | 70 | 0.009 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 2006 | 5 | 93.1 | 26 | 80.5 | 600 | 2 | 2.7 | 0.4 | 7.5 | 0 | 2 | 0.01 | 75 |  | 100 | 0.008 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 2006 | 5 | 120 | 27 | 68.6 | 808.6 | 0.6 | 7.8 | 5.5 | 37.5 | 0 | 8 | 0.01 | 75 |  | 75 | 0.008 | DGA is assessed as acceptable at present. | Oil quality is assessed as acceptable.
33000 | 2006 | 5 | 80.9 | 28 | 60.1 | 821 | 3.4 | 4 | 1.8 | 11.6 | 0 | 5 | 0.006 | 95 |  | 74 | 0.01 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 2006 | 5 | 64.8 | 42 | 49.9 | 347.4 | 7.2 | 2.6 | 0.4 | 4.7 | 0 | 8 | 0.01 | 75 |  | 62 | 0.009 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 2006 | 5 | 198.4 | 32 | 82.4 | 575.5 | 11.4 | 37.2 | 37.5 | 29.9 | 0 | 2 | 0.01 | 66 |  | 74 | 0.009 | DGA is assessed as acceptable at present. | Oil quality is assessed as acceptable.
33000 | 2006 | 5 | 102.1 | 24 | 71.3 | 648.9 | 0.9 | 4.7 | 9.6 | 15.6 | 0 | 3 | 0.01 | 75 |  | 85 | 0.008 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 2006 | 5 | 79.3 | 26 | 61.6 | 810.7 | 3.7 | 3.2 | 2.6 | 8.2 | 0 | 4 | 0.006 | 77 |  | 77 | 0.009 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 2006 | 5 | 135.8 | 50 | 107.3 | 426.6 | 22.4 | 2.6 | 0.5 | 3 | 0 | 4 | 0 | 75 |  | 81 | 0.009 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 2006 | 5 | 86.2 | 33 | 73.4 | 978.9 | 6.9 | 1.7 | 0.1 | 4.1 | 0 | 3 | 0.01 | 75 |  | 50 | 0.014 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable. Corrosive IEC. Corrosive ASTM 4B.
33000 | 2006 | 5 | 126.6 | 30 | 67.9 | 1014.4 | 53.8 | 2.2 | 0.4 | 2.3 | 0 | 0 | 0.009 | 68 |  | 21 | 0.015 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 2006 | 5 | 83.5 | 35 | 55 | 635.7 | 6 | 3.5 | 1.2 | 17.8 | 0 | 27 | 0 | 51 |  | 44 | 0.019 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 2006 | 5 | 63.4 | 42 | 42 | 703 | 12.2 | 1.6 | 5.3 | 2.3 | 0 | 14 | 0.005 | 67 |  | 111 | 0.006 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 2006 | 5 | 85 | 35 | 62 | 659.2 | 12.3 | 2.3 | 0.3 | 8.1 | 0 | 7 | 0.01 | 75 |  | 30 | 0.017 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 2006 | 5 | 71.3 | 42 | 50 | 711.8 | 11.7 | 1.7 | 3.7 | 4.2 | 0 | 12 | 0.007 | 80 |  | 80 | 0.006 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 2006 | 5 | 112.6 | 21 | 94.7 | 481.2 | 8.1 | 2.4 | 0.3 | 7.1 | 0 | 3 | 0.01 | 75 |  | 167 | 0.007 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 2006 | 5 | 122.6 | 30 | 83.6 | 645.6 | 14.5 | 5.5 | 1.8 | 17.2 | 0 | 7 | 0.006 | 58 |  | 99 | 0.007 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 2006 | 5 | 88.5 | 25 | 70.7 | 784.2 | 4.6 | 3.5 | 1.1 | 8.6 | 0 | 4 | 0.003 | 96 |  | 178 | 0.006 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 2006 | 5 | 105 | 36 | 90 | 932 | 8 | 2 | 0.3 | 4.7 | 0 | 4 | 0.004 | 46 |  | 72 | 0.008 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 2006 | 5 | 71.6 | 36 | 59.8 | 824.1 | 4.7 | 2.1 | 0.9 | 4.1 | 0 | 4 | 0.003 | 92 |  | 119 | 0.009
33000 | 2006 | 5 | 118.4 | 23 | 97.7 | 537.1 | 5.5 | 2.9 | 0.9 | 11.4 | 0 | 4 | 0.01 | 64 |  | 46 | 0.013 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 2006 | 5 | 95.4 | 32 | 82 | 656 | 3.6 | 2.5 | 0.2 | 7.1 | 0 | 7 | 0.008 | 71 |  | 47 | 0.015 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable. Corrosive IEC. Corrosive ASTM 4A.
33000 | 2006 | 5 | 80 | 22 | 68.7 | 840.8 | 3.3 | 1.9 | 1.1 | 5 | 0 | 23 | 0.004 | 76 |  | 47 | 0.016 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 2006 | 5 | 74.3 | 38 | 60.2 | 774.7 | 3.5 | 1.9 | 0.9 | 7.8 | 0 | 8 | 0.003 | 90 |  | 66 | 0.009
33000 | 2006 | 5 | 137.6 | 45 | 118.9 | 544.2 | 11.2 | 2.7 | 0.5 | 4.3 | 0 | 10 | 0.01 | 57 |  | 70 | 0.01 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 2006 | 5 | 115.8 | 43 | 105.6 | 944.7 | 6.3 | 1 | 0.3 | 2.6 | 0 | 7 | 0.003 | 82 |  | 129 | 0.006 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable. Corrosive IEC. Corrosive ASTM 4A.
33000 | 2006 | 5 | 105.4 | 40 | 90.3 | 972.5 | 8.6 | 2.5 | 0.3 | 3.6 | 0.1 | 4 | 0.001 | 68 |  | 132 | 0.006 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 2006 | 5 | 78.1 | 47 | 66.9 | 390.4 | 8.3 | 1.6 | 0.1 | 1.2 | 0 | 5 | 0.01 | 68 |  | 24 | 0.051 | DGA is assessed as acceptable. | DDF is high and Resistivity is low for new transformer. Other oil quality results are assessed as acceptable.
33000 | 2006 | 5 | 102.8 | 35 | 87.5 | 658.9 | 1.6 | 2.6 | 1.6 | 9.5 | 0 | 3 | 0.01 | 75 |  | 17 | 0.043 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 2006 | 5 | 105.3 | 35 | 84.6 | 987.4 | 6.2 | 3 | 0.8 | 10.6 | 0.1 | 7 | 0 | 74 |  | 19 | 0.036 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable. Corrosive IEC. Corrosive ASTM 4A.
33000 | 2006 | 5 | 88.5 | 48 | 69.6 | 1055.6 | 6.5 | 3.2 | 1.8 | 7.1 | 0.3 | 6 | 0.004 | 86 |  | 20 | 0.023 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 2006 | 5 | 195.7 | 46 | 166.9 | 518.7 | 14 | 4.6 | 1.8 | 5.9 | 2.5 | 4 | 0.01 | 75 |  | 42 | 0.02295 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 2006 | 5 | 13490.8 | 44 | 216 | 1242 | 275 | 3484 | 6221 | 3285 | 9.8 | 4 | 0.01 | 75 |  | 24 | 0.017 | DGA suggests abnormal heating has occurred. | Oil quality is assessed as acceptable. Corrosive IEC. Corrosive ASTM 4A.
33000 | 2006 | 5 | 11676.7 | 39 | 142.3 | 1111.6 | 168.5 | 3038.3 | 5216.9 | 3089.5 | 21.2 | 5 | 0.01 | 75 |  | 22 | 0.016 | DGA suggests abnormal heating has occurred. | Oil quality is assessed as acceptable.
33000 | 2006 | 5 | 11918 | 39 | 149.5 | 1124.2 | 182.5 | 3174.2 | 5315.6 | 3082.5 | 13.7 | 3 | 0.01 | 75 |  | 20 | 0.018 | DGA suggests abnormal heating has occurred. | Oil quality is assessed as acceptable.
33000 | 2006 | 5 | 518.3 | 44 | 378.9 | 809.9 | 120.1 | 9.5 | 1.7 | 8.1 | 0 | 3 | 0.01 | 75 |  | 48 | 0.019 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 2006 | 5 | 83.1 | 30 | 76.8 | 271.7 | 1.5 | 2 | 2.3 | 0.5 | 0 | 2 | 0.01 | 75 |  | 549 | 0.004 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 2006 | 5 | 124.1 | 31 | 113.3 | 520.8 | 4.5 | 2.5 | 2.6 | 1.2 | 0 | 4 | 0.004 | 85 |  | 111 | 0.011 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 2006 | 5 | 110.4 | 37 | 100.6 | 699.2 | 3.3 | 2.4 | 2.6 | 1.5 | 0 | 4 | 0.002 | 91 |  | 119 | 0.008 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 2006 | 5 | 93.3 | 30 | 89 | 816.7 | 0 | 2.5 | 1.8 | 0 | 0 | 4 | 0.002 | 66 |  | 75 | 0.013 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 2006 | 5 | 116.5 | 32 | 114.1 | 731.2 | 0 | 2 | 0.2 | 0.2 | 0 | 3 | 0.01 | 75 |  | 139 | 0.009 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 2006 | 5 | 86.8 | 40 | 79.5 | 880.5 | 0.9 | 2.2 | 2.1 | 2.1 | 0 | 4 | 0.004 | 86 |  | 99 | 0.012 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 2006 | 5 | 101.1 | 34 | 86.2 | 998.7 | 4.2 | 3.8 | 3.8 | 3.1 | 0 | 7 | 0.002 | 81 |  | 96 | 0.01 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 2006 | 5 | 124 | 29 | 97.4 | 403.9 | 19 | 2.4 | 0.3 | 4.9 | 0 | 4 | 0.01 | 75 |  | 39 | 0.02 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 2006 | 5 | 185 | 72 | 161.3 | 918.5 | 3.5 | 8.7 | 0.3 | 11.2 | 0 | 4 | 0.01 | 63 |  | 44 | 0.022 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable. Corrosive IEC. Corrosive ASTM 4A.
33000 | 2006 | 5 | 125.8 | 30 | 104.5 | 1181.5 | 5.6 | 3.3 | 0.9 | 11.5 | 0 | 5 | 0.006 | 66 |  | 31 | 0.013 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 2006 | 5 | 90.9 | 35 | 66.5 | 955.1 | 12.9 | 2.5 | 1 | 8 | 0 | 7 | 0.004 | 90 |  | 39 | 0.01 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 2006 | 5 | 83.7 | 36 | 73.9 | 489.2 | 3.4 | 1.9 | 0.1 | 4.4 | 0 | 3 | 0.003 | 92 |  | 127 | 0.021 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 2006 | 5 | 71.2 | 40 | 61.5 | 713.9 | 2.4 | 2.1 | 0.2 | 5 | 0 | 2 | 0.004 | 94 |  | 18 | 0.092 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 2006 | 5 | 71.5 | 46 | 60 | 837.1 | 5.2 | 2 | 0.5 | 3.8 | 0 | 4 | 0.003 | 80 |  | 94 | 0.013 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 2006 | 5 | 71.5 | 42 | 62 | 610.2 | 1.9 | 2.1 | 0.2 | 5.3 | 0 | 4 | 0.01 | 75 |  | 166 | 0.01 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 2006 | 5 | 61.5 | 46 | 54.5 | 795.1 | 1.7 | 2 | 0.2 | 3.1 | 0 | 6 | 0.01 | 75 |  | 60 | 0.017 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 2006 | 5 | 99.3 | 42 | 69.6 | 950.1 | 3.7 | 4.4 | 3.6 | 18 | 0 | 4 | 0.004 | 57 |  | 73 | 0.009 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 2006 | 5 | 116.9 | 30 | 100.3 | 751.5 | 3.3 | 2.7 | 0.4 | 10.2 | 0 | 9 | 0.01 | 75 |  | 40 | 0.019 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable. Corrosive IEC. Corrosive ASTM 4A.
33000 | 2006 | 5 | 97.4 | 26 | 84.1 | 827.7 | 2.3 | 2.4 | 0.4 | 8.2 | 0 | 6 | 0.01 | 75 |  | 51 | 0.021 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 2006 | 5 | 106.6 | 41.81 | 93.6 | 992.2 | 2.7 | 2.3 | 0.5 | 7.5 | 0 | 3 | 0.005 | 56 |  | 51 | 0.011 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 2006 | 5 | 79.2 | 42 | 59.9 | 940.4 | 4.5 | 3.3 | 3.1 | 8.4 | 0 | 7 | 0.003 | 79 |  | 42 | 0.013 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 2006 | 5 | 105.8 | 31 | 85.5 | 1058.2 | 6.2 | 3.2 | 3.2 | 7.7 | 0 | 6 | 0.003 | 80 |  | 42 | 0.009 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 2006 | 5 | 105 | 25 | 87.8 | 722.7 | 13.8 | 1.6 | 1 | 0.8 | 0 | 6 | 0.01 | 75 |  | 110 | 0.008 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable. Corrosive IEC. Non-corrosive ASTM 3B.
33000 | 2006 | 5 | 52.5 | 12.6 | 49 | 433.1 | 2.2 | 1 | 0.1 | 0.2 | 0 | 4 | 0.01 | 75 |  | 115 | 0.008 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 2006 | 5 | 99 | 56 | 85.6 | 1200 | 11.7 | 1.3 | 0.4 | 0 | 0 | 6 | 0.01 | 75 |  | 34 | 0.018 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable. Corrosive IEC. Non-corrosive ASTM 2E.
33000 | 2006 | 5 | 95 | 47 | 92.4 | 899.5 | 0 | 1.8 | 0.5 | 0.3 | 0 | 4 | 0.01 | 75 |  | 217 | 0.007 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable. Corrosive IEC. Non-corrosive ASTM 3A.
33000 | 2006 | 5 | 69.4 | 43 | 65.8 | 867.6 | 1.4 | 1 | 1.1 | 0.1 | 0 | 5 | 0.006 | 85 |  | 202 | 0.006 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable. Corrosive IEC. Non-corrosive ASTM 3A.
33000 | 2006 | 5 | 71.5 | 32 | 68.6 | 475.3 | 1.7 | 1.1 | 0.1 | 0 | 0 | 8 | 0 | 61 |  | 90 | 0.013 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 2006 | 5 | 94.4 | 37 | 90 | 865.4 | 1 | 1.7 | 1.5 | 0.2 | 0 | 2 | 0.004 | 88 |  | 334 | 0.004 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable. Corrosive IEC. Non-corrosive ASTM 3B.
33000 | 2006 | 5 | 90.2 | 36 | 84 | 830.8 | 2.1 | 1.3 | 2.6 | 0.2 | 0 | 9 | 0.002 | 78 |  | 442 | 0.003 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 2006 | 5 | 119.8 | 30 | 94.8 | 424.1 | 9.1 | 3.3 | 5.5 | 7.1 | 0 | 5 | 0.01 | 75 |  | 40 | 0.036 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable. Corrosive IEC. Corrosive ASTM 4A.
33000 | 2006 | 5 | 123.8 | 45 | 108.2 | 891.5 | 5 | 5.3 | 1.6 | 3.7 | 0 | 5 | 0.01 | 75 |  | 48 | 0.012 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable. Corrosive IEC. Corrosive ASTM 4A.
33000 | 2006 | 5 | 112 | 42 | 88.3 | 995.9 | 6.9 | 3.7 | 2.4 | 10.7 | 0 | 10 | 0.006 | 77 |  | 59 | 0.007 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 2006 | 5 | 113 | 30 | 99.6 | 412.9 | 8.2 | 2.1 | 0.2 | 2.9 | 0 | 7 | 0.002 | 86 |  | 71 | 0.018 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 2006 | 5 | 130.6 | 36 | 118.5 | 948.7 | 2.8 | 4.2 | 0.3 | 4.8 | 0 | 4 | 0.004 | 95 |  | 52 | 0.015 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable. Non-corrosive IEC. Non-corrosive ASTM 3B.
33000 | 2006 | 5 | 97.5 | 40 | 85.5 | 898.3 | 6.4 | 3.2 | 0.3 | 2.1 | 0 | 4 | 0.002 | 92 |  | 53 | 0.01 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 2005 | 6 | 131.1 | 31 | 115.4 | 604 | 5.7 | 3.4 | 0.5 | 6.1 | 0 | 2 | 0 | 75 |  | 176 | 0.018 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 2005 | 6 | 240.4 | 26 | 100 | 949.1 | 132.3 | 2.8 | 0.4 | 4.9 | 0 | 4 | 0.01 | 75 |  | 48 | 0.022 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 2005 | 6 | 107.2 | 33 | 98.6 | 1198.6 | 3.3 | 2.4 | 0.2 | 2.7 | 0 | 6 | 0.01 | 74 |  | 46 | 0.023 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable. Corrosive IEC. Corrosive ASTM 4A.
33000 | 2005 | 6 | 75.3 | 31 | 68.1 | 1128.1 | 3.4 | 2.1 | 0.3 | 1.4 | 0 | 6 | 0.005 | 99 |  | 41 | 0.021 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 2005 | 6 | 142.1 | 39 | 120.2 | 781.5 | 16.9 | 2.3 | 1.9 | 0.8 | 0 | 2 | 0.01 | 75 |  | 8 | 0.075 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 2005 | 6 | 147.8 | 34 | 122.3 | 1002.2 | 13.8 | 2.9 | 5.5 | 3.3 | 0 | 5 | 0.01 | 88 |  | 13 | 0.058 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 2005 | 6 | 148.9 | 47 | 114.6 | 1159.6 | 25.7 | 2.6 | 2.8 | 3.2 | 0 | 5 | 0.008 | 99 |  | 11 | 0.05 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 2005 | 6 | 141.7 | 40 | 99.4 | 1185.3 | 36.4 | 2.5 | 1 | 2.4 | 0 | 7 | 0.008 | 84 |  | 10 | 0.039 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 2005 | 6 | 163.7 | 44 | 139.5 | 679.4 | 15.4 | 3.8 | 0.4 | 4.6 | 0 | 2 | 0.01 | 75 |  | 158 | 0.017 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 2005 | 6 | 162.2 | 46 | 118 | 1290.1 | 29.1 | 4.2 | 1.3 | 9.6 | 0 | 4 | 0.01 | 75 |  | 38 | 0.017 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 2005 | 6 | 70.8 | 32 | 62.4 | 953.5 | 1.6 | 2 | 0.3 | 4.5 | 0 | 9 | 0.01 | 74 |  | 41 | 0.015 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable. Corrosive IEC. Corrosive ASTM 4A.
33000 | 2005 | 6 | 52.9 | 32 | 45.9 | 790.3 | 3.3 | 1.5 | 0.2 | 2 | 0 | 4 | 0.003 | 77 |  | 48 | 0.01 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable. Corrosive IEC. Corrosive ASTM 4B.
33000 | 2005 | 6 | 77.1 | 34 | 67.8 | 571.2 | 7.2 | 1.7 | 0.2 | 0.2 | 0 | 4 | 0 | 75 |  | 61 | 0.018 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 2005 | 6 | 74.2 | 48 | 68 | 1008.6 | 3.4 | 1.9 | 0.4 | 0.5 | 0 | 4 | 0.01 | 73 |  | 87 | 0.013 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 2005 | 6 | 67.3 | 30 | 63.9 | 1007.3 | 0.8 | 1.9 | 0.3 | 0.4 | 0 | 3 | 0.01 | 75 |  | 111 | 0.009 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 2005 | 6 | 71.4 | 36 | 66.7 | 1029.1 | 2.6 | 1.7 | 0.2 | 0.2 | 0 | 5 | 0.01 | 75 |  | 73 | 0.02 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable. Corrosive IEC. Corrosive ASTM 4A.
33000 | 2005 | 6 | 53.2 | 28 | 48.6 | 898.2 | 2.1 | 1.5 | 0.7 | 0.3 | 0 | 3 | 0.003 | 95 |  | 49 | 0.014 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 2005 | 6 | 682.8 | 46 | 593.3 | 2708 | 72.8 | 12.6 | 1.3 | 2.8 | 0 | 6 | 0.002 | 77 |  | 110 | 0.012 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 2005 | 6 | 609.4 | 35 | 523 | 3734.5 | 55.6 | 16.7 | 6.3 | 7.8 | 0 | 12 | 0.007 | 49 |  | 43 | 0.016 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 2005 | 6 | 772.2 | 35 | 508 | 3112.3 | 182.1 | 31.7 | 5.8 | 44.6 | 0 | 26 | 0.003 | 40 |  | 78 | 0.009 | DGA suggests mild oil overheating (<300C) has occurred. | Oil quality is assessed as acceptable.
33000 | 2005 | 6 | 445.8 | 38 | 388.8 | 3287.6 | 28.1 | 14.7 | 5.2 | 9 | 0 | 4 | 0.001 | 93 |  | 69 | 0.011 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 2005 | 6 | 186.6 | 30 | 110.8 | 597.1 | 58 | 8.4 | 2.5 | 2.1 | 4.8 | 10 | 0.01 | 75 |  | 74 | 0.007 | DGA is assessed as acceptable. Acetylene gas possibly communicating from tapchanger. | Oil quality is assessed as acceptable.
33000 | 2005 | 6 | 60.4 | 47 | 53 | 1035 | 0 | 2 | 0.4 | 5 | 0 | 4 | 0 | 75 |  | 68 | 0.008 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 2005 | 6 | 53.9 | 38 | 48.9 | 1066.4 | 2.4 | 1.8 | 0.2 | 0.6 | 0 | 3 | 0 | 72 |  | 99 | 0.009 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable. Corrosive IEC. Corrosive ASTM 4A.
33000 | 2005 | 6 | 141.3 | 25 | 115.4 | 423.2 | 20.6 | 2.3 | 1.2 | 1.8 | 0 | 2 | 0.01 | 75 |  | 16 | 0.046 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 2005 | 6 | 134.1 | 35 | 120.3 | 633.2 | 6.9 | 2.8 | 1.5 | 2.6 | 0 | 3 | 0.01 | 72 |  | 16 | 0.044 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 2005 | 6 | 133.4 | 30 | 111.2 | 899.3 | 9.9 | 1.8 | 2.4 | 8.1 | 0 | 3 | 0.01 | 75 |  | 13 | 0.043 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable. Corrosive IEC. Corrosive ASTM 4B.
33000 | 2005 | 6 | 133.7 | 40 | 106.2 | 1115.5 | 18.3 | 2.2 | 1.6 | 5.4 | 0 | 5 | 0.005 | 94 |  | 15 | 0.031 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 2005 | 6 | 141.7 | 38 | 96.6 | 1125.3 | 31.1 | 2.6 | 5.5 | 4.7 | 1.2 | 10 | 0.01 | 75 |  | 13 | 0.029 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 2005 | 6 | 141.1 | 30 | 121 | 765.7 | 10.1 | 4.5 | 0.3 | 5.2 | 0 | 4 | 0.01 | 75 |  | 54 | 0.024 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 2005 | 6 | 116.1 | 26 | 98.1 | 1040.6 | 8.2 | 3.2 | 0.4 | 6.2 | 0 | 4 | 0.01 | 75 |  | 56 | 0.023 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 2005 | 6 | 122.5 | 30 | 108.7 | 1372.5 | 6.5 | 3 | 0.5 | 3.8 | 0 | 7 | 0.01 | 75 |  | 55 | 0.023 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable. Corrosive IEC. Corrosive ASTM 4A.
33000 | 2005 | 6 | 98.7 | 31 | 80.4 | 1315.3 | 11.9 | 2.8 | 0.7 | 2.9 | 0 | 4 | 0.003 | 94 |  | 38 | 0.019 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 2005 | 6 | 165.9 | 41 | 141.1 | 771.3 | 15.6 | 4.8 | 0.4 | 4 | 0 | 1 | 0.01 | 75 |  | 68 | 0.044 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 2005 | 6 | 164.6 | 39 | 84 | 1027.1 | 29.7 | 12.4 | 2.2 | 36.3 | 0 | 2 | 0.01 | 75 |  | 11 | 0.056 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 2005 | 6 | 311.3 | 40 | 146.9 | 1481.9 | 137.7 | 5.9 | 1.6 | 19.2 | 0 | 8 | 0.028 | 75 |  | 15 | 0.018 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable. Corrosive IEC. Corrosive ASTM 4B.
33000 | 2005 | 6 | 201.7 | 34 | 139.5 | 1600.1 | 51.9 | 3.8 | 1.3 | 5.2 | 0 | 7 | 0.039 | 72 |  | 14 | 0.017 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable. Corrosive IEC. Corrosive ASTM 4B
33000 | 2005 | 6 | 114.1 | 41.81 | 79.8 | 581.7 | 4.6 | 4.1 | 4.1 | 21.5 | 0 | 4 | 0.01 | 54 |  | 19 | 0.056 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 2005 | 6 | 152.2 | 61 | 99.7 | 1027.6 | 26.4 | 6.5 | 3.1 | 16.5 | 0 | 2 | 0.01 | 75 |  | 13.5 | 0.057 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable. Corrosive IEC. Non-corrosive ASTM 3B.
33000 | 2005 | 6 | 335.6 | 33 | 126.2 | 1455.1 | 148.4 | 8.7 | 5.2 | 47.1 | 0 | 1 | 0.016 | 89 |  | 12 | 0.023 | DGA suggests partial discharge has occurred. | Oil quality is assessed as acceptable.
33000 | 2005 | 6 | 360.2 | 29 | 143.4 | 1543.2 | 171.7 | 7 | 3.9 | 34.2 | 0 | 2 | 0.017 | 43 |  | 11 | 0.023 | DGA suggests partial discharge has occurred. | Oil quality is assessed as acceptable.
33000 | 2005 | 6 | 362 | 44 | 159.9 | 1878.5 | 139.5 | 11 | 7.7 | 43.9 | 0 | 14 | 0.027 | 67 |  | 8 | 0.032 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 2005 | 6 | 270 | 30 | 156.1 | 1813.1 | 92.3 | 5.9 | 3 | 12.7 | 0 | 6 | 0.031 | 94 |  | 9 | 0.026 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 2005 | 6 | 71.5 | 32 | 62.6 | 503 | 7 | 1.5 | 0.1 | 0.3 | 0 | 3 | 0.01 | 75 |  | 33 | 0.018 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 2005 | 6 | 82.4 | 32 | 76.4 | 875.6 | 3.5 | 1.8 | 0.3 | 0.4 | 0 | 4 | 0.01 | 75 |  | 72 | 0.013 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 2005 | 6 | 67 | 50 | 65.9 | 977.7 | 0 | 0.4 | 0.4 | 0.3 | 0 | 6 | 0.003 | 86 |  | 55 | 0.021 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable. Corrosive IEC. Corrosive ASTM 4A.
33000 | 2005 | 6 | 57.2 | 28 | 51 | 944.5 | 3.3 | 1.7 | 0.7 | 0.5 | 0 | 4 | 0.001 | 66 |  | 52 | 0.02 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 2005 | 6 | 65.6 | 45 | 56.3 | 977.9 | 6.7 | 1.6 | 0.6 | 0.4 | 0 | 4 | 0.002 | 52 |  | 70 | 0.019 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 2005 | 6 | 116.8 | 18 | 90.9 | 523.7 | 17.9 | 2.5 | 0.8 | 4.7 | 0 | 4 | 0.01 | 68 |  | 15 | 0.026 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 2005 | 6 | 104 | 43 | 89.7 | 821.7 | 4.8 | 2.3 | 0.6 | 6.6 | 0 | 3 | 0.01 | 75 |  | 12 | 0.03 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 2005 | 6 | 102.9 | 50 | 73.8 | 946.3 | 28 | 0.2 | 0.4 | 0.5 | 0 | 4 | 0.01 | 75 |  | 21 | 0.014 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable. Corrosive IEC. Non-corrosive ASTM 3B.
33000 | 2005 | 6 | 83.1 | 46 | 71.2 | 966.2 | 9.1 | 1.9 | 0.2 | 0.7 | 0 | 6 | 0.003 | 73 |  | 30 | 0.014 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 2005 | 6 | 87.3 | 41.81 | 63.8 | 474 | 6.3 | 2.7 | 1.3 | 13.2 | 0 | 3 | 0.01 | 75 |  | 42 | 0.014 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 2005 | 6 | 128.7 | 37 | 103.9 | 771.3 | 11.1 | 3.2 | 0.7 | 9.8 | 0 | 5 | 0.004 | 74 |  | 43 | 0.013 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 2005 | 6 | 123.6 | 36 | 105.3 | 1386 | 7.2 | 3.8 | 0.6 | 6.7 | 0 | 7 | 0.004 | 71 |  | 26 | 0.021 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable. Corrosive IEC. Corrosive ASTM 4A.
33000 | 2005 | 6 | 93.4 | 33 | 82.2 | 1237.4 | 0 | 2.4 | 0.5 | 8.3 | 0 | 8 | 0.003 | 81 |  | 31 | 0.019 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable. Corrosive IEC. Corrosive ASTM 4A.
33000 | 2005 | 6 | 85.7 | 32 | 68.3 | 1162.6 | 0 | 2.7 | 3.1 | 11.6 | 0 | 54 | 0.004 | 23 |  | 92 | 0.004 | DGA is assessed as acceptable. | Breakdown voltage is low. Oil is cloudy in appearance. Other oil quality results are assessed as acceptable.
33000 | 2005 | 6 | 74.9 | 25 | 59 | 1105.9 | 4.6 | 1.8 | 2.2 | 7.3 | 0 | 12 | 0.004 | 72 |  | 61 | 0.008 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 2005 | 6 | 76.1 | 20 | 56.8 | 280.6 | 13.6 | 1.7 | 0.6 | 3 | 0.4 | 3 | 0.01 | 73 |  | 33 | 0.025 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 2005 | 6 | 67.2 | 32 | 60.6 | 634.6 | 0 | 1.9 | 0.3 | 4.4 | 0 | 3 | 0.01 | 75 |  | 41 | 0.015 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 2005 | 6 | 94.2 | 24 | 67.9 | 825.4 | 0 | 3.2 | 3.8 | 19.3 | 0 | 6 | 0.01 | 52 |  | 26 | 0.015 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 2005 | 6 | 72.1 | 28 | 55.5 | 900.5 | 9.8 | 2 | 1.3 | 3.5 | 0 | 5 | 0.003 | 82 |  | 74 | 0.006 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 2005 | 6 | 86.6 | 30 | 64.6 | 438.8 | 13.6 | 1.9 | 1.1 | 5.4 | 0 | 6 | 0.01 | 75 |  | 25 | 0.029 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 2005 | 6 | 91.9 | 43 | 83.1 | 767.3 | 3.5 | 2 | 0.5 | 2.8 | 0 | 3 | 0.011 | 75 |  | 36 | 0.017 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 2005 | 6 | 237.5 | 47 | 65.6 | 912 | 170.7 | 0.2 | 0.4 | 0.6 | 0 | 5 | 0.01 | 75 |  | 92 | 0.007 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 2005 | 6 | 331.2 | 30 | 81 | 807.7 | 159.1 | 13.3 | 12.7 | 2.6 | 62.5 | 16 | 0.01 | 46 |  | 13 | 0.029 | DGA is assessed as acceptable. | Breakdown voltage is slightly low. Other oil quality results are assessed as acceptable.
33000 | 2005 | 6 | 322 | 38 | 96.2 | 1173.5 | 209.2 | 4.8 | 1.3 | 10.5 | 0 | 6 | 0.006 | 84 |  | 94 | 0.006 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 2005 | 6 | 114.6 | 48 | 79.1 | 979.5 | 29.8 | 2.1 | 0.9 | 1.8 | 0.9 | 4 | 0.003 | 88 |  | 106 | 0.004 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 2005 | 6 | 55.8 | 37 | 51.6 | 851.9 | 0 | 1.7 | 1.3 | 1.2 | 0 | 3 | 0.001 | 80 |  | 17 | 0.031 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 2005 | 6 | 126.6 | 35 | 114 | 732.8 | 5.5 | 3.2 | 0.7 | 3.2 | 0 | 3 | 0.01 | 75 |  | 18 | 0.035 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 2005 | 6 | 129.6 | 30 | 110.2 | 972.7 | 8.5 | 2.3 | 1.5 | 7.1 | 0 | 3 | 0.003 | 91 |  | 24 | 0.022 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable. Corrosive IEC. Non-corrosive ASTM 3B.
33000 | 2005 | 6 | 125.1 | 39 | 105.6 | 1125.6 | 11.2 | 2.7 | 1.2 | 4.4 | 0 | 4 | 0.004 | 82 |  | 22 | 0.025 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 2005 | 6 | 102.4 | 35 | 87.2 | 998.3 | 6.4 | 2.2 | 4.1 | 2.5 | 0 | 10 | 0.005 | 86 |  | 25 | 0.018 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 2005 | 6 | 147.6 | 34 | 129.3 | 497.5 | 15.1 | 2.6 | 0.6 | 0 | 0 | 10 | 0.01 | 75 |  | 25 | 0.049 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 2005 | 6 | 129.5 | 26 | 118.1 | 737.3 | 2.7 | 6.7 | 0.6 | 1.4 | 0 | 2 | 0.01 | 75 |  | 24 | 0.024 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable. Corrosive IEC. Corrosive ASTM 4A.
33000 | 2005 | 6 | 102.9 | 32 | 87.4 | 887.3 | 7.5 | 1.9 | 1.9 | 3.8 | 0.4 | 17 | 0.002 | 51 |  | 22 | 0.021 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 2005 | 6 | 84.8 | 38 | 71.3 | 891.5 | 7.3 | 2 | 1.1 | 3.1 | 0 | 8 | 0.001 | 81 |  | 29 | 0.018 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 2005 | 6 | 1172.7 | 30 | 150.9 | 1024.5 | 978.8 | 17.7 | 1.9 | 23.3 | 0.1 | 18 | 0.01 | 48 |  | 13 | 0.028 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable at present.
33000 | 2005 | 6 | 124 | 45 | 109.8 | 1004.5 | 2.9 | 2.7 | 5.7 | 2.9 | 0 | 6 | 0.01 | 75 |  | 12 | 0.031 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 2005 | 6 | 167.7 | 23 | 127.4 | 1122.6 | 26.8 | 3.2 | 6.1 | 4.2 | 0 | 5 | 0.01 | 66 |  | 11 | 0.046 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 2005 | 6 | 97.8 | 30 | 81.4 | 902.3 | 6.3 | 2.2 | 3.1 | 4.8 | 0 | 7 | 0.01 | 75 |  | 15 | 0.032 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable. Corrosive IEC. Corrosive ASTM 4B.
33000 | 2005 | 6 | 194.3 | 32 | 140.4 | 1271.8 | 23.4 | 5.9 | 4.8 | 17.2 | 2.6 | 14 | 0.009 | 71 |  | 12 | 0.032 | DGA is assessed as acceptable at present. | Oil quality is assessed as acceptable. Corrosive IEC. Corrosive ASTM 4A.
33000 | 2005 | 6 | 129.7 | 37 | 103.7 | 1202.8 | 18.9 | 2.5 | 1.2 | 3.4 | 0 | 6 | 0.007 | 91 |  | 12 | 0.029 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 2005 | 6 | 116 | 41 | 108.1 | 1089.8 | 3.7 | 3 | 0.5 | 0.5 | 0.2 | 6 | 0.01 | 75 |  | 79 | 0.013 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 2005 | 6 | 118.6 | 40 | 108.2 | 1432.1 | 5 | 2.9 | 1.4 | 1.1 | 0 | 4 | 0.01 | 75 |  | 67 | 0.015 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable. Corrosive IEC. Corrosive ASTM 4A.
33000 | 2005 | 6 | 57.9 | 37 | 49.4 | 1066.3 | 0.6 | 2.6 | 1.9 | 3.4 | 0 | 3 | 0 | 90 |  | 58 | 0.016 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable. Corrosive IEC. Corrosive ASTM 4A.
33000 | 2005 | 6 | 73.1 | 35 | 60.7 | 1066.8 | 6.2 | 1.7 | 1.8 | 2.5 | 0.2 | 8 | 0.003 | 74 |  | 54 | 0.018 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 2005 | 6 | 60.2 | 38 | 50.1 | 862.7 | 5.1 | 3.5 | 0.9 | 0.6 | 0 | 7 | 0.001 | 47 |  | 51 | 0.015 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 2005 | 6 | 108.1 | 30 | 96.9 | 577.3 | 5 | 2.2 | 0.5 | 3.5 | 0 | 2 | 0.01 | 75 |  | 83 | 0.009 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 2005 | 6 | 200.5 | 44 | 138.1 | 1497.3 | 44.2 | 4.6 | 2 | 11.6 | 0 | 4 | 0.014 | 75 |  | 34 | 0.008 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 2005 | 6 | 207.9 | 46 | 134.3 | 1516.8 | 63.1 | 3.2 | 1.3 | 6 | 0 | 7 | 0.024 | 81 |  | 21 | 0.013 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 2005 | 6 | 116.7 | 25 | 99.3 | 480.8 | 14.7 | 1.8 | 0.3 | 0.4 | 0.2 | 3 | 0.01 | 56 |  | 35 | 0.012 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 2005 | 6 | 75.9 | 50 | 73 | 751 | 0.5 | 1.7 | 0.4 | 0.3 | 0 | 3 | 0.01 | 73 |  | 34 | 0.012 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 2005 | 6 | 108.4 | 32 | 103.7 | 1010.6 | 1.6 | 1.9 | 0.7 | 0.5 | 0 | 4 | 0.004 | 88 |  | 27 | 0.019 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable. Corrosive IEC. Corrosive ASTM 4A.
33000 | 2005 | 6 | 83.9 | 32 | 77.7 | 959.1 | 3 | 1.8 | 1.2 | 0.2 | 0 | 4 | 0.001 | 87 |  | 35 | 0.016 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 2005 | 6 | 89 | 40 | 82 | 634.3 | 4 | 1.9 | 0.2 | 0.9 | 0 | 2 | 0.01 | 75 |  | 122 | 0.008 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 2005 | 6 | 76.9 | 40 | 69.9 | 922.6 | 3.3 | 1.9 | 0.5 | 1.3 | 0 | 4 | 0.01 | 75 |  | 84 | 0.011 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 2005 | 6 | 60.3 | 68 | 53.8 | 876.6 | 2.6 | 1.9 | 0.4 | 1.6 | 0 | 5 | 0.01 | 75 |  | 104 | 0.012 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable. Corrosive IEC. Corrosive ASTM 4A.
33000 | 2005 | 6 | 79.9 | 40 | 75.1 | 971.9 | 0 | 2 | 0.4 | 2.4 | 0 | 10 | 0.002 | 85 |  | 64 | 0.012 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 2005 | 6 | 69.7 | 41.81 | 57.6 | 921.8 | 8.5 | 1.8 | 0.7 | 1.1 | 0 | 5 | 0.003 | 74 |  | 99 | 0.009 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 2005 | 6 | 65.2 | 38 | 50.2 | 848.8 | 6.5 | 8 | 0.2 | 0.3 | 0 | 8 | 0.004 | 85 |  | 90 | 0.01 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 2005 | 6 | 145.7 | 33 | 114.9 | 856.5 | 3.7 | 3.6 | 2.1 | 21.4 | 0 | 3 | 0.01 | 75 |  | 58 | 0.008 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 2005 | 6 | 142.2 | 42 | 117.3 | 1156.7 | 9.3 | 3.7 | 0.9 | 11 | 0 | 6 | 0.01 | 75 |  | 59 | 0.006 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 2005 | 6 | 92.1 | 44 | 80.1 | 1053.5 | 5.9 | 2.5 | 0.5 | 3.1 | 0 | 8 | 0.008 | 88 |  | 64 | 0.007 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 2005 | 6 | 173.5 | 25 | 77 | 432.6 | 30.7 | 14.6 | 1.5 | 49.7 | 0 | 27 | 0.01 | 38 |  | 24 | 0.014 | DGA is assessed as acceptable at present. | Oil quality is assessed as acceptable. Tested to be uncontaminated by PCB.
33000 | 2005 | 6 | 99.2 | 30 | 88 | 824.2 | 0 | 2.8 | 1.4 | 7 | 0 | 3 | 0.004 | 76 |  | 96 | 0.005 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable. Corrosive according to IEC CCD method.
33000 | 2005 | 6 | 113.2 | 39 | 84.3 | 1135.2 | 14.3 | 4.2 | 2 | 8.4 | 0 | 4 | 0.005 | 53 |  | 33 | 0.012 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 2005 | 6 | 122.7 | 33 | 83.1 | 1240.3 | 32.2 | 2.6 | 1 | 3.8 | 0 | 3 | 0.014 | 94 |  | 22 | 0.012 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 2005 | 6 | 74.1 | 28 | 59.1 | 319.4 | 12.3 | 1.3 | 0.6 | 0.8 | 0 | 3 | 0.01 | 75 |  | 43.4 | 0.013 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 2005 | 6 | 177 | 28 | 151.8 | 659.8 | 19.3 | 2.9 | 0.7 | 2.3 | 0 | 4 | 0.01 | 74 |  | 60 | 0.01 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 2005 | 6 | 163.6 | 29.5 | 143.2 | 1161 | 9 | 3.8 | 0.8 | 6.8 | 0 | 5 | 0.01 | 75 |  | 43 | 0.0132 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 2005 | 6 | 166.4 | 54 | 149.4 | 1238.7 | 10.3 | 3.2 | 0.5 | 3 | 0 | 4 | 0.003 | 97 |  | 43 | 0.013 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable. Corrosive IEC. Corrosive ASTM 4A.
33000 | 2005 | 6 | 128.3 | 34 | 114.5 | 1142.9 | 8.6 | 2.7 | 0.6 | 1.9 | 0 | 6 | 0.005 | 96 |  | 42 | 0.017 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable. Corrosive IEC. Corrosive ASTM 4A.
33000 | 2005 | 6 | 127.6 | 30 | 98.5 | 562.5 | 12.5 | 2.5 | 1.1 | 13 | 0 | 4 | 0.01 | 75 |  | 37 | 0.015 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 2005 | 6 | 159.7 | 40 | 117.9 | 935.4 | 10.4 | 5.2 | 4.4 | 21.8 | 0 | 5 | 0.012 | 75 |  | 37 | 0.013 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 2005 | 6 | 123.3 | 32 | 108.6 | 1108.8 | 6.3 | 2.5 | 0.1 | 5.8 | 0 | 8 | 0.01 | 75 |  | 29 | 0.017 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable. Corrosive IEC. Corrosive ASTM 4A.
33000 | 2005 | 6 | 98.1 | 29 | 85.5 | 1020.4 | 7 | 2.4 | 0.2 | 3 | 0 | 4 | 0.007 | 82 |  | 40 | 0.01 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable. Corrosive IEC. Corrosive ASTM 4A.
33000 | 2005 | 6 | 43.4 | 40 | 26.8 | 380.3 | 13.6 | 2.1 | 0.2 | 0.7 | 0 | 8 | 0.01 | 75 |  | 85 | 0.008 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 2005 | 6 | 133.2 | 45 | 85.1 | 771.4 | 7 | 4.5 | 2.1 | 34.5 | 0 | 20 | 0.01 | 47 |  | 94 | 0.009 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 2005 | 6 | 101.1 | 41.81 | 74.6 | 842 | 17.8 | 1.6 | 0.2 | 6.9 | 0 | 4 | 0.01 | 75 |  | 77 | 0.01 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable. Corrosive IEC. Corrosive ASTM 4A.
33000 | 2005 | 6 | 31.4 | 41.81 | 26.2 | 604.6 | 2.5 | 1.3 | 0.1 | 1.3 | 0 | 12 | 0.006 | 61 |  | 72 | 0.01 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 2005 | 6 | 103.4 | 30 | 74.6 | 381.9 | 25.3 | 1.5 | 0.6 | 1.4 | 0 | 5 | 0.01 | 70 |  | 52 | 0.011 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 2005 | 6 | 89.7 | 50 | 79 | 669.6 | 1.8 | 2.4 | 0.5 | 6 | 0 | 4 | 0.01 | 75 |  | 38 | 0.011 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 2005 | 6 | 129.4 | 26 | 106.7 | 987.9 | 3.9 | 4.1 | 2.9 | 8.8 | 3 | 6 | 0.004 | 86 |  | 27 | 0.02 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable. Corrosive IEC. Corrosive ASTM 4A.
33000 | 2005 | 6 | 76.2 | 36 | 70 | 943.5 | 1.5 | 2.3 | 0.5 | 1.9 | 0 | 3 | 0.001 | 68 |  | 32 | 0.016 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 2005 | 6 | 102.8 | 26 | 74.8 | 325.2 | 21.6 | 2 | 0.7 | 3.7 | 0 | 8 | 0.01 | 73 |  | 37 | 0.019 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 2005 | 6 | 116.9 | 36 | 97.2 | 1046.7 | 13.5 | 1.1 | 0.8 | 4.3 | 0 | 3 | 0.01 | 75 |  | 56 | 0.007 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 2005 | 6 | 111.6 | 41.81 | 78.4 | 1017.5 | 14 | 4.3 | 2.4 | 12.5 | 0 | 4 | 0.007 | 55 |  | 40 | 0.008 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 2005 | 6 | 79.3 | 31 | 71.3 | 552 | 2 | 2.2 | 0.5 | 3.3 | 0 | 11 | 0.01 | 66 |  | 10 | 0.051 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 2005 | 6 | 72.4 | 57 | 68.1 | 663 | 0 | 1.8 | 0.3 | 2.2 | 0 | 4 | 0.01 | 58 |  | 14 | 0.04 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable. Corrosive IEC. Corrosive ASTM 4B.
33000 | 2005 | 6 | 106.9 | 32 | 88 | 1063 | 6 | 4 | 0.9 | 8 | 0 | 10 | 0.005 | 75 |  | 87 | 0.005 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 2005 | 6 | 72.4 | 33 | 66.4 | 854.3 | 2.1 | 2.1 | 0.4 | 1.4 | 0 | 3 | 0.005 | 90 |  | 16 | 0.03 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 2005 | 6 | 96.1 | 40 | 85.7 | 1015.2 | 4.6 | 2.9 | 0.5 | 2.4 | 0 | 4 | 0.006 | 82 |  | 59 | 0.011 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 2005 | 6 | 66.6 | 33 | 62.6 | 992.5 | 0 | 1.6 | 1.1 | 1.3 | 0 | 8 | 0.004 | 71 |  | 69 | 0.006 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 2005 | 6 | 88.2 | 28 | 73.3 | 493.3 | 5.4 | 2.1 | 0.5 | 6.9 | 0 | 2 | 0.01 | 67 |  | 61 | 0.011 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 2005 | 6 | 72.9 | 31 | 63.4 | 633.1 | 3.2 | 1.9 | 0.5 | 3.9 | 0 | 6 | 0.01 | 74 |  | 60 | 0.01 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable. Corrosive IEC. Corrosive ASTM 4A.
33000 | 2005 | 6 | 72.4 | 39 | 67.9 | 658.6 | 4.3 | 0.2 | 0 | 0 | 0 | 2 | 0.01 | 71 |  | 33 | 0.021 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 2005 | 6 | 87.3 | 31 | 77.1 | 891.7 | 5.5 | 2 | 0.6 | 2.1 | 0 | 6 | 0.005 | 73 |  | 51 | 0.01 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable. Corrosive IEC. Corrosive ASTM 4A.
33000 | 2005 | 6 | 183.6 | 27 | 65.8 | 198.9 | 47 | 15.4 | 1.5 | 53.9 | 0 | 24 | 0.01 | 46 |  | 30 | 0.019 | DGA is assessed as acceptable at present. | Oil quality is assessed as acceptable. Tested to be uncontaminated by PCB.
33000 | 2005 | 6 | 111.2 | 34 | 96.3 | 761 | 4.7 | 2.8 | 2.2 | 5.2 | 0 | 3 | 0.01 | 75 |  | 10 | 0.0796 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable. Corrosive according to IEC CCD method.
33000 | 2005 | 6 | 112.3 | 39 | 86.7 | 1054.2 | 13.2 | 3.2 | 1.7 | 7.5 | 0 | 2 | 0.01 | 50 |  | 12 | 0.06 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 2005 | 6 | 93.4 | 33 | 71.9 | 1076.9 | 15.8 | 2.3 | 0.8 | 2.6 | 0 | 2 | 0.01 | 97 |  | 12 | 0.038 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 2005 | 6 | 46.3 | 32 | 38.7 | 349.4 | 2.5 | 1.3 | 0.6 | 3.2 | 0 | 5 | 0.01 | 75 |  | 10 | 0.06 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable at present.
33000 | 2005 | 6 | 86.3 | 36 | 75.2 | 557.2 | 4.7 | 1.7 | 0.4 | 4.3 | 0 | 4 | 0.01 | 75 |  | 60 | 0.01 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 2005 | 6 | 178 | 50 | 153.4 | 1034.4 | 16.4 | 3.1 | 0.5 | 4.6 | 0 | 4 | 0.01 | 75 |  | 33 | 0.015 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 2005 | 6 | 152.7 | 64 | 122.6 | 1203.3 | 10.3 | 4.6 | 2 | 12.9 | 0.3 | 10 | 0.01 | 68 |  | 24 | 0.026 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 2005 | 6 | 144.3 | 42 | 110.9 | 1183 | 13 | 5.9 | 2 | 12.5 | 0 | 8 | 0.004 | 87 |  | 46 | 0.011 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 2005 | 6 | 77.6 | 42 | 44.2 | 273.2 | 29.5 | 2.2 | 0.5 | 1 | 0.2 | 1 | 0 | 73 |  | 128 | 0.007 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 2005 | 6 | 159 | 85 | 118 | 1156 | 22 | 4 | 2 | 13 | 0 | 4 | 0.004 | 72 |  | 30 | 0.022 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 2005 | 6 | 191.7 | 60 | 150.2 | 1326.9 | 32.4 | 2.8 | 0.9 | 5.4 | 0 | 5 | 0.005 | 83 |  | 47 | 0.01 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 2005 | 6 | 492.2 | 40 | 178.9 | 1643.1 | 289.7 | 5.7 | 2.8 | 15.1 | 0 | 5 | 0.023 | 78 |  | 17 | 0.015 | Hydrogen level is increased, otherwise DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 2005 | 6 | 383.6 | 36 | 167.6 | 1651.3 | 202.2 | 3.3 | 2.1 | 8.4 | 0 | 7 | 0.028 | 92 |  | 25 | 0.011 | Dissolved gas levels are relatively stable. | Oil quality is assessed as acceptable.
33000 | 2005 | 6 | 357.2 | 59 | 160.2 | 1803.2 | 180.8 | 4.6 | 2.5 | 9.1 | 0 | 9 | 0.029 | 81 |  | 21 | 0.012 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 2005 | 6 | 482.2 | 52 | 218 | 1964 | 251.7 | 3.9 | 2.2 | 6.4 | 0 | 8 | 0.033 | 77 |  | 15 | 0.017 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 2005 | 6 | 433.3 | 58 | 231.5 | 2053.4 | 190.1 | 4.2 | 2.5 | 5 | 0 | 16 | 0.029 | 77 |  | 17 | 0.015 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable. Corrosive IEC. Corrosive ASTM 4A.
33000 | 2005 | 6 | 155.1 | 34 | 127.9 | 477.9 | 22.6 | 2.6 | 0.6 | 1.4 | 0 | 6 | 0.01 | 75 |  | 44 | 0.011 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 2005 | 6 | 77.2 | 39 | 69.9 | 656.9 | 0 | 2.1 | 0.5 | 4.7 | 0 | 3 | 0.01 | 75 |  | 37 | 0 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 2005 | 6 | 90 | 40 | 89.1 | 966.4 | 0 | 0.3 | 0.6 | 0 | 0 | 7 | 0.01 | 74 |  | 42 | 0.014 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable. Corrosive IEC. Corrosive ASTM 4A.
33000 | 2005 | 6 | 78.4 | 36 | 64.5 | 939.3 | 9.4 | 1.8 | 0.7 | 2 | 0 | 5 | 0.002 | 85 |  | 47 | 0.01 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable. Corrosive IEC. Non-corrosive ASTM 3B.
33000 | 2005 | 6 | 112 | 35 | 89.3 | 552.2 | 16 | 2.5 | 0.7 | 3.5 | 0 | 15 | 0.01 | 47 |  | 31 | 0.021 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 2005 | 6 | 151.4 | 47 | 118.8 | 1005.5 | 11.2 | 5.6 | 1.7 | 14.1 | 0 | 6 | 0.01 | 75 |  | 62 | 0.009 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 2005 | 6 | 120.5 | 45 | 106.6 | 1137 | 6.4 | 2.8 | 0.5 | 4.2 | 0 | 4 | 0.005 | 92 |  | 44 | 0.012 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable. Corrosive IEC. Corrosive ASTM 4A.
33000 | 2005 | 6 | 79.1 | 35 | 59.9 | 863.6 | 0 | 3.1 | 3.5 | 12.6 | 0 | 27 | 0.013 | 58 |  | 63 | 0.008 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 2005 | 6 | 96.1 | 40 | 83.1 | 482.8 | 8 | 1.9 | 0.4 | 2.7 | 0 | 4 | 0 | 75 |  | 97 | 0.008 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 2005 | 6 | 62 | 40 | 56 | 711.6 | 0 | 0 | 0.9 | 5.1 | 0 | 6 | 0.01 | 75 |  | 54 | 0.011 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable. Corrosive IEC. Corrosive ASTM 4A.
33000 | 2005 | 6 | 77.6 | 40 | 55.9 | 887.2 | 11.5 | 3.2 | 1 | 6 | 0 | 8 | 0 | 54 |  | 102 | 0.007 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 2005 | 6 | 55.5 | 34 | 45.5 | 238.9 | 7.8 | 1 | 0.4 | 0.8 | 0 | 3 | 0.01 | 75 |  | 69 | 0.01 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 2005 | 6 | 84.3 | 39 | 75.5 | 883.6 | 4.4 | 2.1 | 0.3 | 2 | 0 | 3 | 0.01 | 75 |  | 58 | 0.013 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 2005 | 6 | 70 | 41 | 61.1 | 974.7 | 5.7 | 2 | 0.1 | 1.1 | 0 | 6 | 0 | 72 |  | 55 | 0.013 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 2005 | 6 | 71.6 | 25 | 62.5 | 906.4 | 6.2 | 2 | 0 | 0.9 | 0 | 5 | 0.01 | 75 |  | 115 | 0.007 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 2005 | 6 | 316 | 25 | 118.6 | 755.2 | 132.5 | 12.5 | 6.4 | 2.1 | 43.9 | 18 | 0.01 | 52 |  | 73 | 0.004 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 2005 | 6 | 73.3 | 17 | 58 | 719.5 | 11.6 | 1.5 | 0.9 | 1.3 | 0 | 6 | 0.001 | 81 |  | 77 | 0.007 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
330000 | 2004 | 7 | 254.1 | 18 | 171.4 | 507.5 | 17.2 | 29.7 | 1.1 | 34.7 | 0 | 5 | 0 | 74 | 0 | 132 | 0.006 | DGA is assessed as acceptable. Oil quality is assessed as acceptable. Corrosive IEC. Insulation is assessed as acceptable.
33000 | 2004 | 7 | 61 | 36 | 57.8 | 418.9 | 2 | 0.9 | 0.2 | 0.1 | 0 | 3 | 0.01 | 75 |  | 87 | 0.012 | Dissolved gas analysis is assessed as acceptable. Oil quality is assessed as acceptable. Comments are based on the analysis results without prior knowledge of any history or operating parameters of the transformer.
33000 | 2004 | 7 | 94.2 | 40 | 89.2 | 636.3 | 2.8 | 1.5 | 0.4 | 0.3 | 0 | 4 | 0.01 | 75 |  | 49 | 0.027 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 2004 | 7 | 85.7 | 38 | 81.1 | 861.6 | 2.4 | 1.7 | 0 | 0.5 | 0 | 3 | 0.01 | 75 |  | 66 | 0.019 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 2004 | 7 | 80.1 | 35 | 76.3 | 912 | 1.5 | 1.5 | 0.2 | 0.6 | 0 | 4 | 0.007 | 97 |  | 62 | 0.013 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable. Corrosive IEC. Corrosive ASTM 4A.
33000 | 2004 | 7 | 74.5 | 38 | 72 | 972 | 0 | 2 | 0.2 | 0.3 | 0 | 4 | 0.002 | 89 |  | 49 | 0.019 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 2004 | 7 | 70.1 | 40 | 66.2 | 922.9 | 1.9 | 1.3 | 0.4 | 0.3 | 0 | 3 | 0.002 | 69 |  | 64 | 0.011 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 2004 | 7 | 132 | 32 | 114.8 | 565.5 | 8.9 | 3.1 | 0.2 | 5 | 0 | 6 | 0.01 | 75 |  | 180 | 0.007 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 2004 | 7 | 121.9 | 40 | 80.2 | 984.4 | 27.9 | 2.7 | 1 | 10.1 | 0 | 3 | 0.01 | 75 |  | 48 | 0.018 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 2004 | 7 | 146 | 46 | 69.9 | 952 | 4.4 | 3.6 | 35.5 | 30.8 | 1.8 | 6 | 0.003 | 83 |  | 142 | 0.008 | DGA is assessed as acceptable at present. | Oil quality is assessed as acceptable.
33000 | 2004 | 7 | 88.6 | 36 | 80.9 | 1018.1 | 4.3 | 2.6 | 0.3 | 0.5 | 0 | 4 | 0.003 | 91 |  | 109 | 0.011 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 2004 | 7 | 74.1 | 33 | 65.6 | 954.8 | 3.9 | 1.9 | 0.5 | 2.2 | 0 | 4 | 0.004 | 91 |  | 147 | 0.007 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 2004 | 7 | 77 | 36 | 71.2 | 268.5 | 4.7 | 0.9 | 0.1 | 0.1 | 0 | 5 | 0.01 | 75 |  | 148 | 0.009 | Dissolved gas analysis is assessed as acceptable. Oil quality is assessed as acceptable. Comments are based on the analysis results without prior knowledge of any history or operating parameters of the transformer. (Note: 183A Load.)
33000 | 2004 | 7 | 72.6 | 38 | 70.1 | 853 | 0 | 1.3 | 0.8 | 0.4 | 0 | 4 | 0.01 | 75 |  | 195 | 0.007 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 2004 | 7 | 60.2 | 40 | 57.7 | 925.2 | 0 | 1.3 | 0.8 | 0.4 | 0 | 4 | 0.01 | 75 |  | 276 | 0.006 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 2004 | 7 | 46.2 | 66 | 43.4 | 915.1 | 0.8 | 0.6 | 0.9 | 0.5 | 0 | 5 | 0.01 | 75 |  | 217 | 0.005 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 2004 | 7 | 43.9 | 43 | 42 | 858.1 | 0 | 1.2 | 0.7 | 0 | 0 | 7 | 0.001 | 74 |  | 392 | 0.004 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 2004 | 7 | 79.4 | 40 | 60 | 363.6 | 11.1 | 2.4 | 0.1 | 5.8 | 0 | 3 | 0.01 | 75 |  | 142 | 0.007 | Dissolved gas analysis is assessed as acceptable. Oil quality is assessed as acceptable. Comments are based on the analysis results without prior knowledge of any history or operating parameters of the transformer. (Note: 196A Load)
33000 | 2004 | 7 | 72.2 | 36 | 63.9 | 775.7 | 6.4 | 1.3 | 0.2 | 0.4 | 0 | 4 | 0.01 | 71 |  | 221 | 0.007 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 2004 | 7 | 51 | 38 | 49.4 | 883.4 | 0 | 1.2 | 0.1 | 0.3 | 0 | 3 | 0.001 | 97 |  | 254 | 0.006 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 2004 | 7 | 43.2 | 42 | 41.1 | 857.9 | 1.1 | 0.7 | 0.1 | 0.2 | 0 | 10 | 0 | 73 |  | 165 | 0.009 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 2004 | 7 | 46.8 | 43 | 44.9 | 878.1 | 0 | 1.5 | 0.4 | 0 | 0 | 14 | 0.001 | 71 |  | 338 | 0.005 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 2004 | 7 | 93 | 36 | 78.8 | 384.7 | 10.5 | 1.3 | 0 | 2.4 | 0 | 8 | 0.01 | 75 |  | 194 | 0.011 | Dissolved gas analysis is assessed as acceptable. | Oil quality is assessed as acceptable. The test results are assessed as acceptable for a vacuum oltc.
33000 | 2004 | 7 | 136.2 | 47 | 119 | 766.2 | 11.3 | 2 | 0.3 | 3.6 | 0 | 6 | 0.01 | 67 |  | 129 | 0.009 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 2004 | 7 | 101.2 | 48 | 90.4 | 1139.8 | 4.5 | 2 | 0 | 4.3 | 0 | 4 | 0 | 75 |  | 89 | 0.015 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 2004 | 7 | 91.1 | 34 | 80.7 | 1085.5 | 5.3 | 2 | 0.3 | 2.8 | 0 | 3 | 0.01 | 75 |  | 57 | 0.014 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable. Corrosive IEC. Corrosive ASTM 4A.
33000 | 2004 | 7 | 82.4 | 40 | 74.2 | 1067 | 4.7 | 1.8 | 0.2 | 1.5 | 0 | 6 | 0.004 | 86 |  | 50 | 0.012 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 2004 | 7 | 68.8 | 42 | 61.4 | 963.2 | 4.5 | 1.6 | 0.3 | 1 | 0 | 6 | 0.003 | 90 |  | 84 | 0.008 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 2004 | 7 | 144.3 | 40 | 82.5 | 768.6 | 39.2 | 7.1 | 0.4 | 15.1 | 0 | 14 | 0.01 | 72 |  | 124 | 0.006 | Dissolved gas analysis is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 2004 | 7 | 92.5 | 34 | 74.6 | 783.2 | 10.5 | 5.4 | 0 | 2 | 0 | 6 | 0 | 75 |  | 237 | 0.005 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 2004 | 7 | 63.2 | 32 | 59.1 | 751.2 | 2.5 | 1.1 | 0.2 | 0.3 | 0 | 2 | 0.01 | 75 |  | 309 | 0.007 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 2004 | 7 | 60 | 31 | 54.3 | 800 | 4.5 | 0.8 | 0.3 | 0.1 | 0 | 3 | 0.01 | 75 |  | 361 | 0.004 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable. Corrosive IEC. Corrosive ASTM 4A.
33000 | 2004 | 7 | 71.4 | 25 | 61.2 | 885.6 | 7.2 | 1.4 | 1.3 | 0.3 | 0 | 4 | 0.001 | 93 |  | 148 | 0.007 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 2004 | 7 | 43.6 | 30 | 40.6 | 745.2 | 0 | 1 | 1.8 | 0.2 | 0 | 5 | 0.001 | 79 |  | 121 | 0.006 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 2004 | 7 | 118.4 | 46 | 110.6 | 828.7 | 3.3 | 2 | 0.2 | 2.3 | 0 | 8 | 0.01 | 46 |  | 75 | 0.014 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 2004 | 7 | 92.9 | 46 | 79.3 | 1133.9 | 7 | 2.8 | 0.4 | 3.4 | 0 | 4 | 0.01 | 75 |  | 55 | 0.016 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 2004 | 7 | 61.1 | 44 | 54.7 | 930.1 | 2.6 | 1.5 | 0.3 | 2 | 0 | 3 | 0.01 | 75 |  | 81 | 0.019 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 2004 | 7 | 43.8 | 50 | 43 | 871.4 | 0 | 0.6 | 0.2 | 0 | 0 | 7 | 0.003 | 95 |  | 56 | 0.021 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable. Corrosive IEC. Corrosive ASTM 4A.
33000 | 2004 | 7 | 44.9 | 40 | 31.3 | 833.4 | 11.6 | 1.3 | 0.1 | 0.6 | 0 | 5 | 0.001 | 72 |  | 73 | 0.012 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 2004 | 7 | 30.4 | 34 | 23.9 | 180.8 | 5.1 | 0.6 | 0.3 | 0 | 0.5 | 5 | 0.01 | 75 |  | 57 | 0.047 | Dissolved gas analysis is assessed as acceptable. Oil quality is assessed as acceptable. Comments are based on the analysis results without prior knowledge of any history or operating parameters of the transformer.
33000 | 2004 | 7 | 74.2 | 30 | 70.3 | 730.3 | 2.5 | 1.4 | 0 | 0 | 0 | 6 | 0.01 | 75 |  | 27 | 0.047 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 2004 | 7 | 60.9 | 36 | 54.1 | 654.1 | 5 | 1.1 | 0.3 | 0.4 | 0 | 3 | 0.01 | 72 |  | 56 | 0.037 | DGA is assessed as acceptable | Oil quality is assessed as acceptable.
33000 | 2004 | 7 | 73.3 | 37 | 69.4 | 902 | 0.8 | 1.3 | 1.5 | 0.3 | 0 | 4 | 0.01 | 66 |  | 50 | 0.032 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 2004 | 7 | 92.5 | 40 | 80.3 | 969.2 | 2.4 | 2.1 | 7.4 | 0.3 | 0 | 19 | 0.002 | 85 |  | 29 | 0.033 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 2004 | 7 | 182.5 | 38 | 149.8 | 1238 | 16.6 | 1.9 | 14.2 | 0 | 0 | 11 | 0.006 | 78 |  | 25 | 0.034 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 2004 | 7 | 88.4 | 36 | 82.5 | 977.1 | 3 | 2 | 0.3 | 0.4 | 0.2 | 3 | 0.01 | 75 |  | 160 | 0.006 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 2004 | 7 | 91.8 | 38 | 79.8 | 940.1 | 8.7 | 1.9 | 1 | 0.4 | 0 | 4 | 0.004 | 90 |  | 119 | 0.006 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable. Corrosive IEC. Corrosive ASTM 4A.
33000 | 2004 | 7 | 68.6 | 44 | 65.9 | 983.1 | 0 | 1.1 | 1.6 | 0 | 0 | 5 | 0.002 | 76 |  | 158 | 0.012 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 2004 | 7 | 103.2 | 43 | 69.3 | 938.4 | 26.8 | 3.6 | 2.3 | 1.2 | 0 | 6 | 0.004 | 76 |  | 116 | 0.011 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 2004 | 7 | 90.9 | 35 | 84.4 | 1033.8 | 3.9 | 2 | 0.2 | 0.4 | 0 | 4 | 0.01 | 75 |  | 178 | 0.008 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 2004 | 7 | 87.9 | 34 | 80.1 | 976.6 | 5.1 | 2 | 0.3 | 0.4 | 0 | 4 | 0.003 | 87 |  | 223 | 0.009 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable. Corrosive IEC. Corrosive ASTM 4B.
33000 | 2004 | 7 | 86 | 44 | 67.9 | 1100.8 | 15.2 | 2 | 0.6 | 0.3 | 0 | 4 | 0.002 | 81 |  | 181 | 0.013 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 2004 | 7 | 95.6 | 42 | 63.4 | 930.8 | 27.3 | 3.3 | 0.8 | 0.8 | 0 | 6 | 0.004 | 88 |  | 177 | 0.01 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 2004 | 7 | 84.3 | 42 | 78.5 | 1010.5 | 0 | 1.9 | 0.7 | 0.7 | 2.5 | 4 | 0.01 | 65 |  | 135 | 0.008 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 2004 | 7 | 65.3 | 38 | 62.7 | 1165.3 | 0 | 1.5 | 0.5 | 0.6 | 0 | 7 | 0.01 | 75 |  | 50 | 0.01975 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 2004 | 7 | 72.6 | 33 | 56.2 | 1210.2 | 14.1 | 0.9 | 0 | 1.4 | 0 | 5 | 0.01 | 75 |  | 143 | 0.009 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 2004 | 7 | 49.2 | 40 | 45.8 | 1093.8 | 1.7 | 0.8 | 0.4 | 0.5 | 0 | 3 | 0.003 | 75 |  | 118 | 0.013 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable. Corrosive IEC. Corrosive ASTM 4A.
33000 | 2004 | 7 | 72.1 | 34 | 47 | 949.9 | 3.7 | 2.9 | 6 | 12.5 | 0 | 6 | 0 | 68 |  | 80 | 0.016 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 2004 | 7 | 33.1 | 28 | 10.7 | 212.4 | 4.6 | 3.5 | 0.7 | 13.6 | 0 | 6 | 0.01 | 75 |  | 230 | 0.006 | Dissolved gas analysis is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 2004 | 7 | 134.5 | 30 | 121.4 | 892.1 | 10.3 | 2 | 0.4 | 0.4 | 0 | 2 | 0 | 58 |  | 74 | 0.017 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 2004 | 7 | 131.2 | 66 | 120.9 | 1128.2 | 8.3 | 2 | 0 | 0 | 0 | 4 | 0.01 | 75 |  | 151 | 0.006 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 2004 | 7 | 41.1 | 29 | 36.9 | 627.4 | 2.5 | 1.1 | 0.2 | 0.4 | 0 | 2 | 0.01 | 71 |  | 245 | 0.006 | DGA is assessed as acceptable | Oil quality is assessed as acceptable.
33000 | 2004 | 7 | 41 | 43 | 36.7 | 743.2 | 1.8 | 1.2 | 0.4 | 0.4 | 0.5 | 1 | 0.01 | 75 |  | 186 | 0.005 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 2004 | 7 | 38.5 | 44 | 34.1 | 743.6 | 1.7 | 1.4 | 0.8 | 0.5 | 0 | 6 | 0.003 | 74 |  | 209 | 0.005 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 2004 | 7 | 44.1 | 40 | 36.8 | 744.7 | 5.6 | 1.2 | 0.2 | 0.3 | 0 | 4 | 0 | 77 |  | 150 | 0.011 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 2004 | 7 | 107.9 | 40 | 100.7 | 537.8 | 5.1 | 1.3 | 0.4 | 0.4 | 0 | 7 | 0.01 | 75 |  | 143 | 0.008 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 2004 | 7 | 95 | 38 | 85.8 | 1295.7 | 4.3 | 2 | 0 | 2.9 | 0 | 3 | 0.01 | 75 |  | 67 | 0.017 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 2004 | 7 | 85.5 | 66 | 76.1 | 1335.5 | 4.4 | 2.2 | 0.5 | 2.3 | 0 | 5 | 0.01 | 75 |  | 93 | 0.009 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 2004 | 7 | 65.4 | 43 | 54 | 1198.7 | 5.3 | 2.3 | 1.7 | 1.9 | 0.2 | 8 | 0.01 | 75 |  | 76 | 0.011 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 2004 | 7 | 83.1 | 27 | 63.9 | 1289.2 | 15.7 | 1.7 | 0.6 | 1.2 | 0 | 7 | 0.003 | 90 |  | 97 | 0.005 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 2004 | 7 | 297.6 | 50 | 266.9 | 1750.8 | 25.9 | 3.8 | 0.3 | 0.3 | 0.4 | 8 | 0.01 | 75 |  | 105 | 0.013 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 2004 | 7 | 125 | 35 | 115.3 | 1347.8 | 6.5 | 2.5 | 0.2 | 0.5 | 0 | 4 | 0.01 | 75 |  | 83 | 0.0123 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 2004 | 7 | 105.9 | 32 | 98.1 | 1426.4 | 5.6 | 1.7 | 0.1 | 0.4 | 0 | 5 | 0.01 | 75 |  | 167 | 0.005 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable. Corrosive IEC. Corrosive ASTM 4A.
33000 | 2004 | 7 | 92.2 | 41.81 | 84.1 | 1399.4 | 5.4 | 2.1 | 0.2 | 0.4 | 0 | 6 | 0.001 | 86 |  | 101 | 0.009 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 2004 | 7 | 76.2 | 30 | 63.1 | 1176.8 | 10.2 | 1.8 | 0.2 | 0.9 | 0 | 6 | 0.007 | 71 |  | 151 | 0.006 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 2004 | 7 | 141.7 | 40 | 93.8 | 699.6 | 29.5 | 8.3 | 0 | 10.1 | 0 | 6 | 0.01 | 75 |  | 101 | 0.01 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 2004 | 7 | 82.6 | 38 | 69.9 | 661 | 8.6 | 1.5 | 0.9 | 1.7 | 0 | 3 | 0.01 | 75 |  | 54 | 0.019 | DGA is assessed as acceptable | Oil quality is assessed as acceptable.
33000 | 2004 | 7 | 92.4 | 42 | 76.3 | 861.3 | 12.6 | 1.4 | 1.1 | 1 | 0 | 4 | 0.01 | 73 |  | 30 | 0.034 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 2004 | 7 | 86.8 | 35 | 68.8 | 931.1 | 11.9 | 2.6 | 3 | 0.5 | 0 | 9 | 0.01 | 75 |  | 23 | 0.034 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 2004 | 7 | 91.3 | 42 | 63.1 | 972.3 | 15.3 | 1.9 | 4.7 | 2.2 | 4.1 | 5 | 0.01 | 87 |  | 20 | 0.033 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 2004 | 7 | 8.6 | 31 | 7.9 | 87.3 | 0 | 0.5 | 0 | 0.1 | 0.1 | 3 | 0.01 | 75 |  | 182 | 0.009 | Dissolved gas analysis is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 2004 | 7 | 223.1 | 45 | 174.9 | 778.6 | 41.6 | 3.2 | 0.5 | 2.9 | 0 | 9 | 0 | 75 |  | 190 | 0.006 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 2004 | 7 | 133.7 | 45 | 54.4 | 348.8 | 65.8 | 4.3 | 1.5 | 1.1 | 6.6 | 13 | 0.01 | 75 |  | 116 | 0.008 | Acetylene level is high for a Vacuum OLTC. | Oil quality is assessed as acceptable.
33000 | 2004 | 7 | 188.6 | 42 | 150.4 | 1481.4 | 29.3 | 3.3 | 0 | 5.6 | 0 | 5 | 0.01 | 75 |  | 68 | 0.014 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 2004 | 7 | 111.4 | 39 | 95.4 | 1109.1 | 12.1 | 1.9 | 0.3 | 1.7 | 0 | 6 | 0.002 | 74 |  | 78 | 0.009 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 2004 | 7 | 138.7 | 33 | 100.7 | 1572 | 31.1 | 5.1 | 0.6 | 1.2 | 0 | 7 | 0.001 | 73 |  | 41 | 0.018 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable. Corrosive IEC. Corrosive ASTM 4A.
33000 | 2004 | 7 | 89 | 43 | 70.5 | 1049.4 | 16.7 | 1.6 | 0.2 | 0 | 0 | 10 | 0.003 | 74 |  | 66 | 0.009 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 2004 | 7 | 27.4 | 44 | 24 | 134.2 | 2.7 | 0.7 | 0 | 0 | 0 | 5 | 0.01 | 74 |  | 41 | 0.038 | Dissolved gas analysis is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 2004 | 7 | 78.1 | 42 | 76.7 | 554 | 0 | 1.4 | 0 | 0 | 0 | 3 | 0.01 | 75 |  | 148 | 0.03 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 2004 | 7 | 84.3 | 30 | 69.8 | 852.8 | 12.8 | 1.3 | 0.4 | 0 | 0 | 7 | 0.01 | 69 |  | 58 | 0.028 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 2004 | 7 | 106.2 | 36 | 85.4 | 1026.6 | 17.7 | 1.2 | 1.7 | 0.1 | 0.1 | 5 | 0.002 | 75 |  | 71 | 0.018 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable. Corrosive IEC. Corrosive ASTM 4A.
33000 | 2004 | 7 | 111.9 | 41.81 | 86.4 | 997.2 | 17.6 | 1.9 | 5.2 | 0.8 | 0 | 5 | 0.003 | 75 |  | 50 | 0.02 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 2004 | 7 | 74.6 | 40 | 53.1 | 903.5 | 15.4 | 1.5 | 2.9 | 1.7 | 0 | 5 | 0.002 | 73 |  | 34 | 0.024 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 2004 | 7 | 96.1 | 27 | 64.3 | 892.5 | 27.4 | 2.3 | 2.1 | 0 | 0 | 10 | 0.001 | 80 |  | 38 | 0.02 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 2004 | 7 | 115.5 | 28 | 83.4 | 569.8 | 23.8 | 2.5 | 0.6 | 5.2 | 0 | 8 | 0.01 | 75 |  | 31 | 0.02 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 2004 | 7 | 115.1 | 26 | 95.6 | 878.4 | 13.1 | 1.8 | 1.1 | 3.5 | 0 | 2 | 0.01 | 75 |  | 40 | 0.022 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 2004 | 7 | 96.9 | 32 | 81.3 | 1024.2 | 11.4 | 1.1 | 0.8 | 2.3 | 0 | 3 | 0.01 | 75 |  | 41 | 0.021 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable. Corrosive IEC. Corrosive ASTM 4A.
33000 | 2004 | 7 | 88 | 30 | 67.6 | 1058.7 | 16.2 | 1.8 | 0.9 | 1.5 | 0 | 3 | 0.013 | 100 |  | 17 | 0.035 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 2004 | 7 | 97.4 | 28 | 66.5 | 1083 | 26.8 | 1.5 | 1.5 | 1.1 | 0 | 1 | 0.02 | 85 |  | 12 | 0.032 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 2004 | 7 | 153.3 | 50 | 140.7 | 584.2 | 10.6 | 1.6 | 0.1 | 0.3 | 0 | 5 | 0.01 | 75 |  | 82 | 0.034 | Dissolved gas analysis is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 2004 | 7 | 441.7 | 55 | 188.4 | 1497.3 | 65.6 | 45 | 6.2 | 136.5 | 0 | 5 | 0.01 | 75 |  | 8 | 0.078 | DGA suggests mild oil overheating has occurred. | Oil quality is assessed as acceptable.
33000 | 2004 | 7 | 1001.6 | 45 | 501.5 | 3143.1 | 409.8 | 20.3 | 6 | 64 | 0 | 12 | 0.035 | 39 |  | 10 | 0.025 | Carbon oxides and hydrogen gas levels are increased. | Breakdown voltage is slightly low. Other oil quality results are assessed as acceptable.
33000 | 2004 | 7 | 474.2 | 45 | 306.2 | 2766.8 | 102.4 | 12.7 | 4.7 | 48.2 | 0 | 12 | 0.042 | 75 |  | 3 | 0.094 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable. Corrosive IEC. Corrosive ASTM 4B.
33000 | 2004 | 7 | 209 | 34 | 141.7 | 2006.1 | 46.1 | 5.5 | 3.3 | 12.4 | 0 | 13 | 0.05 | 75 |  | 4 | 0.063 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable. Corrosive IEC. Corrosive ASTM 4B.
33000 | 2004 | 7 | 127.9 | 40 | 94.9 | 1243.8 | 26.8 | 2.4 | 1 | 2.8 | 0 | 15 | 0.048 | 100 |  | 8 | 0.031 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable. Corrosive IEC. Corrosive ASTM 4B.
33000 | 2004 | 7 | 510.5 | 42 | 125.9 | 1206.7 | 320.1 | 27.1 | 2.4 | 35 | 0 | 29 | 0 | 17 |  | 34 | 0.011 | Dissolved hydrocarbon gas levels are high for new transformer. | Moisture content is high for new transformer. Breakdown voltage is very low. Other oil quality results are assessed as acceptable. Possible sample contamination.
33000 | 2004 | 7 | 359.8 | 40 | 178.8 | 1924.7 | 132.5 | 7.4 | 4.1 | 37 | 0 | 6 | 0.036 | 57 |  | 3 | 0.084 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 2004 | 7 | 474.3 | 40 | 296.2 | 2733.9 | 141.8 | 8 | 3.3 | 25 | 0 | 14 | 0.052 | 75 |  | 4 | 0.056 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable. Corrosive IEC. Corrosive ASTM 4B.
33000 | 2004 | 7 | 118.3 | 39 | 87.7 | 1350.2 | 24.9 | 3 | 0.9 | 1.8 | 0 | 8 | 0.05 | 75 |  | 7 | 0.032 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 2004 | 7 | 60.5 | 41.81 | 43.6 | 217.9 | 14.6 | 1.2 | 0.1 | 1 | 0 | 2 | 0.01 | 50 |  | 192 | 0.011 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 2004 | 7 | 74.4 | 18 | 58 | 341 | 10 | 3 | 0.4 | 2 | 1 | 2 | 0.01 | 75 |  | 320 | 0.003 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable. Tested to be uncontaminated by PCB.
33000 | 2004 | 7 | 197 | 42 | 150.9 | 1017 | 38.6 | 3.8 | 0.7 | 3 | 0 | 4 | 0.012 | 75 |  | 15 | 0.018 | DGA is assessed as acceptable. | DDF increased and Resistivity reduced however oil quality is assessed as acceptable.
33000 | 2004 | 7 | 168.1 | 36 | 139.2 | 1378.3 | 24 | 3.1 | 0.5 | 1.3 | 0 | 9 | 0.011 | 75 |  | 10 | 0.027 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable. Corrosive IEC. Corrosive ASTM 4A.
33000 | 2004 | 7 | 100.3 | 41 | 85.6 | 1057.7 | 11.6 | 2.1 | 0.3 | 0.7 | 0 | 6 | 0.013 | 72 |  | 21 | 0.014 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable. Corrosive IEC. Corrosive ASTM 4A.
33000 | 2004 | 7 | 26.4 | 40 | 17.3 | 130.3 | 8.7 | 0.4 | 0 | 0 | 0 | 5 | 0.01 | 75 |  | 54 | 0.037 | Dissolved gas analysis is assessed as acceptable. Oil quality is assessed as acceptable. Comments are based on the analysis results without prior knowledge of any history or operating parameters of the transformer.
33000 | 2004 | 7 | 206.3 | 44 | 81.1 | 1009.8 | 43.7 | 14.7 | 2.5 | 64.3 | 0 | 2 | 0.01 | 75 |  | 11 | 0.043 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 2004 | 7 | 316.3 | 49 | 154.4 | 1342.3 | 125.4 | 6.2 | 2.5 | 27.8 | 0 | 8 | 0.025 | 95 |  | 9 | 0.03 | DGA is assessed as acceptable at present. | Oil quality is assessed as acceptable.
33000 | 2004 | 7 | 328 | 49 | 239.1 | 2068.3 | 77.2 | 4.8 | 1.8 | 5.1 | 0 | 10 | 0.049 | 76 |  | 8 | 0.031 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 2004 | 7 | 225.7 | 41 | 177.9 | 1815.4 | 40.5 | 4.2 | 1.3 | 1.8 | 0 | 10 | 0.059 | 96 |  | 7 | 0.031 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 2004 | 7 | 142.5 | 24 | 112.2 | 1439.1 | 24.3 | 2.8 | 1.1 | 2.1 | 0 | 15 | 0.059 | 82 |  | 4 | 0.074 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 2004 | 7 | 142.2 | 60 | 128.1 | 653.5 | 9.9 | 1.5 | 2.1 | 0.6 | 0 | 8 | 0.01 | 75 |  | 63 | 0.03 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 2004 | 7 | 87.8 | 48 | 78.4 | 854.1 | 6.2 | 1.7 | 0.2 | 1.3 | 0 | 7 | 0.01 | 36 |  | 80 | 0.026 | DGA is assessed as acceptable. | Breakdown voltage is decreased. Other oil quality results are assessed as acceptable.
33000 | 2004 | 7 | 305 | 56 | 124 | 1247 | 92 | 15 | 4 | 70 | 0 | 2 | 0.014 | 75 |  | 13 | 0.025 | DGA suggests mild oil overheating has occurred. | Oil quality is assessed as acceptable.
33000 | 2004 | 7 | 419.8 | 50 | 168.5 | 1213 | 145.6 | 19.8 | 4 | 81.9 | 0 | 2 | 0.017 | 75 |  | 17 | 0.02 | Dissolved gas levels are relatively stable and assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 2004 | 7 | 498.8 | 51 | 200.4 | 2029.5 | 200.7 | 11.8 | 4.8 | 81.1 | 0 | 4 | 0.026 | 45 |  | 10 | 0.024 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 2004 | 7 | 504.4 | 57 | 208.9 | 1939.2 | 249.4 | 6.4 | 3.4 | 36.3 | 0 | 5 | 0.026 | 61 |  | 6 | 0.039 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 2004 | 7 | 297 | 38 | 161.5 | 1912 | 124.8 | 2.8 | 1.5 | 6.4 | 0 | 9 | 0.043 | 75 |  | 8 | 0.03 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable. Corrosive IEC. Corrosive ASTM 4A.
33000 | 2004 | 7 | 198.6 | 42 | 136.7 | 1661.8 | 56.5 | 2.4 | 0.9 | 2.1 | 0 | 15 | 0.056 | 81 |  | 8 | 0.026 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 2004 | 7 | 48.9 | 28 | 36.2 | 179 | 11.8 | 0.6 | 0.1 | 0.2 | 0 | 3 | 0.01 | 75 |  | 158 | 0.01 | Dissolved gas analysis is assessed as acceptable. Oil quality is assessed as acceptable.
33000 | 2004 | 7 | 206.5 | 36 | 179.8 | 861.1 | 19.2 | 3 | 1.7 | 2.8 | 0 | 4 | 0.01 | 75 |  | 45 | 0.024 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 2004 | 7 | 149.2 | 29 | 94.9 | 1198.9 | 37.6 | 4.8 | 1.7 | 10.2 | 0 | 1 | 0.01 | 75 |  | 15 | 0.028 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 2004 | 7 | 407 | 44 | 225 | 2032 | 162 | 6 | 3 | 11 | 0 | 5 | 0.037 | 71 |  | 12 | 0.022 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable. Corrosive IEC. Corrosive ASTM 4B
33000 | 2004 | 7 | 149.7 | 38 | 106.8 | 1649.6 | 33.9 | 3.8 | 1.4 | 3.8 | 0 | 8 | 0.043 | 74 |  | 4 | 0.051 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 2004 | 7 | 107 | 32 | 78.7 | 1315.5 | 21.3 | 2.1 | 2.8 | 2.1 | 0 | 8 | 0.049 | 85 |  | 7 | 0.033 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 2004 | 7 | 11.5 | 32 | 6.6 | 116.9 | 3.7 | 1 | 0.2 | 0 | 0 | 4 | 0.01 | 75 |  | 49 | 0.043 | Dissolved gas analysis is assessed as acceptable. Oil quality is assessed as acceptable. Comments are based on the analysis results without prior knowledge of any history or operating parameters of the transformer.
33000 | 2004 | 7 | 163.7 | 33 | 120.7 | 753.3 | 30.9 | 3.1 | 1.5 | 7.5 | 0 | 6 | 0.01 | 75 |  | 33 | 0.042 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 2004 | 7 | 153.3 | 38 | 108.5 | 1205.1 | 32 | 4.3 | 3.4 | 5.1 | 0 | 2 | 0.01 | 75 |  | 17 | 0.032 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 2004 | 7 | 213.2 | 40 | 92.8 | 1123.5 | 91 | 3.9 | 2.2 | 23.3 | 0 | 1 | 0.018 | 86 |  | 15 | 0.017 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 2004 | 7 | 255.7 | 41 | 138.3 | 2243.2 | 98.8 | 3.4 | 3.4 | 11.8 | 0 | 17 | 0.039 | 98 |  | 8 | 0.027 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 2004 | 7 | 155.3 | 36 | 88.7 | 1352.3 | 59.2 | 2.6 | 1.1 | 3.7 | 0 | 11 | 0.048 | 65 |  | 6 | 0.038 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 2004 | 7 | 120.8 | 42 | 93.6 | 832.8 | 20.4 | 1.7 | 0.9 | 4.2 | 0 | 3 | 0.01 | 75 |  | 22 | 0.03037 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 2004 | 7 | 114.3 | 34 | 95.6 | 1000.8 | 13.5 | 1.8 | 1.1 | 2.3 | 0 | 6 | 0.01 | 70 |  | 40 | 0.028 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 2004 | 7 | 108.4 | 47 | 87.1 | 1050 | 16.5 | 1.8 | 1.3 | 1.7 | 0 | 5 | 0.008 | 97 |  | 29 | 0.027 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 2004 | 7 | 109.7 | 42 | 82.5 | 1122.5 | 21.4 | 2.1 | 0.7 | 3 | 0 | 8 | 0.008 | 82 |  | 16 | 0.04 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 2004 | 7 | 120.4 | 24 | 95.8 | 409.5 | 17.8 | 2.6 | 0.5 | 3.4 | 0.3 | 7 | 0.01 | 75 |  | 108 | 0.01 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 2004 | 7 | 98.2 | 36 | 81 | 769.2 | 10.4 | 2.2 | 0.5 | 4.1 | 0 | 4 | 0.01 | 71 |  | 57 | 0.022 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 2004 | 7 | 108.6 | 45 | 83.4 | 970 | 19.6 | 2.4 | 0.7 | 2.5 | 0 | 6 | 0.006 | 50 |  | 54 | 0.021 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 2004 | 7 | 131.1 | 35 | 102.2 | 1168.3 | 21.8 | 3.6 | 0.7 | 2.8 | 0 | 10 | 0.009 | 79 |  | 38 | 0.024 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable. Corrosive IEC. Corrosive ASTM 4A.
33000 | 2004 | 7 | 129.7 | 45 | 92.4 | 1225.3 | 27 | 4.5 | 1 | 4.8 | 0 | 4 | 0.009 | 88 |  | 17 | 0.041 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable. Corrosive IEC. Corrosive ASTM 4B
33000 | 2004 | 7 | 169.6 | 28 | 129.2 | 891.8 | 22.6 | 7.3 | 1.2 | 4 | 5.3 | 4 | 0.01 | 75 |  | 55.5 | 0.023 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 2004 | 7 | 162.4 | 38 | 128 | 531 | 18 | 7 | 2 | 7 | 0.4 | 6 | 0.01 | 75 |  | 52 | 0.02 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 2004 | 7 | 184.8 | 60 | 108.2 | 1371.4 | 70.8 | 1.7 | 1.2 | 2.9 | 0 | 4 | 0.024 | 75 |  | 11 | 0.028 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable. Corrosive IEC. Corrosive ASTM 4A.
33000 | 2004 | 7 | 241.5 | 47 | 119.3 | 1801.4 | 112.3 | 2.7 | 2.5 | 4.1 | 0.6 | 6 | 0.026 | 61 |  | 10 | 0.022 | DGA is assessed as acceptable at present. | Oil quality is assessed as acceptable.
33000 | 2004 | 7 | 12.2 | 40 | 7.2 | 64.7 | 4.7 | 0.3 | 0 | 0 | 0 | 3 | 0.01 | 75 |  | 89 | 0.015 | Dissolved gas analysis is assessed as acceptable. Oil quality is assessed as acceptable. Comments are based on the analysis results without prior knowledge of any history or operating parameters of the transformer.
33000 | 2004 | 7 | 146.6 | 40 | 108.6 | 376.6 | 35.6 | 1.7 | 0.2 | 0.5 | 0 | 4 | 0.01 | 72 |  | 52 | 0.022 | Dissolved gas analysis is assessed as acceptable. Oil quality is assessed as acceptable. Comments are based on the analysis results without prior knowledge of any history or operating parameters of the transformer.
33000 | 2004 | 7 | 229 | 40 | 30.8 | 245.3 | 143.8 | 6.2 | 4.9 | 1.7 | 41.6 | 5 | 0.01 | 75 |  | 144 | 0.006 | Acetylene level is abnormal for Reinhaussen Vacuum OLTC. Oil quality is assessed as acceptable. RECOMMEND RESAMPLE IN 3 MONTHS TO MONITOR TREND. Comments are based on the analysis results without prior knowledge of any history or operating parameters
33000 | 2004 | 7 | 118.6 | 22 | 100.8 | 686.6 | 10.4 | 5.5 | 0 | 1.9 | 0 | 1 | 0.01 | 63 |  | 88.1 | 0.019 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 2004 | 7 | 183.8 | 42 | 82.9 | 1104.1 | 38.1 | 10.8 | 2.4 | 49.6 | 0 | 2 | 0.01 | 75 |  | 13 | 0.041 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 2004 | 7 | 609.1 | 38 | 245.5 | 1686.9 | 307.1 | 14.4 | 3.5 | 38.6 | 0 | 1 | 0.029 | 77 |  | 12 | 0.019 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 2004 | 7 | 293.9 | 30 | 146.4 | 1718.2 | 135.5 | 2.6 | 1.2 | 8.2 | 0 | 6 | 0.038 | 95 |  | 7 | 0.033 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable. Corrosive IEC. Corrosive ASTM 4A.
33000 | 2004 | 7 | 227.2 | 30 | 143 | 1508.1 | 79.1 | 2.1 | 0.9 | 2.1 | 0 | 14 | 0.049 | 72 |  | 13 | 0.019 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 2004 | 7 | 20.8 | 29 | 11.5 | 115.4 | 5.4 | 0.8 | 1.2 | 0.2 | 1.7 | 2 | 0.01 | 75 |  | 97 | 0.025 | Dissolved gas analysis is assessed as acceptable. Oil quality is assessed as acceptable. Comments are based on the analysis results without prior knowledge of any history or operating parameters of the transformer.
33000 | 2004 | 7 | 157 | 31 | 131.5 | 557.6 | 15.7 | 3.8 | 1.5 | 3.5 | 1 | 8 | 0.01 | 75 |  | 23 | 0.045 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 2004 | 7 | 163.5 | 37 | 82.4 | 1032.7 | 22.9 | 10.4 | 2.1 | 45.7 | 0 | 3 | 0.01 | 75 |  | 14 | 0.039 | DGA suggests mild oil overheating has occurred. | Oil quality is assessed as acceptable.
33000 | 2004 | 7 | 232.5 | 32 | 108.6 | 1334.9 | 51.3 | 15.7 | 2.6 | 54.3 | 0 | 25 | 0.01 | 22 |  | 7 | 0.084 | DGA is assessed as acceptable. | Breakdown voltage is low. Other oil quality results are assessed as acceptable.
33000 | 2004 | 7 | 167.9 | 38 | 83.1 | 1082 | 62.2 | 3.8 | 1.5 | 17.3 | 0 | 1 | 0.017 | 75 |  | 9 | 0.027 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 2004 | 7 | 212.7 | 38 | 119.5 | 1898.6 | 71.4 | 5 | 4.5 | 12.3 | 0 | 19 | 0.036 | 82 |  | 5 | 0.046 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 2004 | 7 | 167 | 34 | 112.2 | 1404.6 | 47.8 | 3 | 1 | 3 | 0 | 8 | 0.047 | 85 |  | 13 | 0.018 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 2004 | 7 | 106.8 | 36 | 101.2 | 592.5 | 3 | 1.8 | 0.4 | 0.4 | 0 | 6 | 0 | 75 |  | 105 | 0.008 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 2004 | 7 | 131.8 | 41.81 | 99.6 | 1103.7 | 28.2 | 2.1 | 1.5 | 0.4 | 0 | 2 | 0 | 75 |  | 94 | 0.006 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 2004 | 7 | 126.5 | 34 | 114.2 | 1123.2 | 6.4 | 2.1 | 3.4 | 0.3 | 0.1 | 4 | 0.001 | 68 |  | 158 | 0.006 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable. Corrosive IEC. Corrosive ASTM 4A.
33000 | 2004 | 7 | 128.2 | 37 | 118.5 | 1300 | 1.7 | 2.3 | 5.5 | 0.2 | 0 | 4 | 0.004 | 95 |  | 46 | 0.01 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 2004 | 7 | 114.4 | 37 | 100.9 | 1152.9 | 3.2 | 3.5 | 6.8 | 0 | 0 | 3 | 0.001 | 77 |  | 131 | 0.005 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 2004 | 7 | 2700 | 30 | 279 | 189 | 905 | 210 | 392 | 18 | 896 | 14 | 0 | 56 |  | 683 | 0.003 | Dissolved gas analysis suggests Arcing with power follow through. Carbon oxides suggest possible cellulose involvement. | Oil quality is assessed as acceptable.
33000 | 2004 | 7 | 10.5 | 30 | 7 | 189 | 1 | 1 | 0.5 | 0 | 1 | 6 | 0 | 64 |  | 231 | 0.003 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 2004 | 7 | 83.8 | 43 | 76.3 | 429.2 | 5 | 1.4 | 0.3 | 0.7 | 0.1 | 5 | 0 | 75 |  | 217 | 0.004 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 2004 | 7 | 97.3 | 45 | 90.5 | 387 | 5.4 | 1.4 | 0 | 0 | 0 | 8 | 0.01 | 75 |  | 175 | 0.005 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 2004 | 7 | 122.7 | 31 | 113.4 | 469.4 | 6.8 | 1.6 | 0.4 | 0.5 | 0 | 7 | 0.01 | 75 |  | 209 | 0.006 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 2004 | 7 | 130.4 | 43 | 120.4 | 931.2 | 3.5 | 1.9 | 4.1 | 0.5 | 0 | 4 | 0.01 | 75 |  | 209 | 0.005 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 2004 | 7 | 160.2 | 60 | 143 | 1213.6 | 2.7 | 2.4 | 12.1 | 0 | 0 | 4 | 0.01 | 75 |  | 144 | 0.006 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable. Corrosive IEC. Corrosive ASTM 4A.
33000 | 2004 | 7 | 150 | 49 | 132.7 | 1129.4 | 1.7 | 1.9 | 13.5 | 0.2 | 0 | 5 | 0.005 | 89 |  | 108 | 0.01 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable. Corrosive IEC. Corrosive ASTM 4A.
33000 | 2004 | 7 | 134.1 | 40 | 110.9 | 1009.4 | 13.1 | 4.4 | 0.5 | 3.9 | 1.3 | 7 | 0 | 75 |  | 52 | 0.019 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 2004 | 7 | 83.1 | 40 | 67.7 | 1158.5 | 8.3 | 3.2 | 1.2 | 2.7 | 0 | 5 | 0.01 | 75 |  | 92 | 0.007 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable. Corrosive IEC. Corrosive ASTM 4A.
33000 | 2004 | 7 | 118 | 32 | 61.8 | 1381.9 | 37.9 | 5.5 | 6.1 | 6.7 | 0 | 0 | 0.007 | 78 |  | 38 | 0.011 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 2004 | 7 | 317.4 | 37 | 136.4 | 2138 | 168.8 | 3.9 | 4.7 | 3.6 | 0 | 9 | 0.028 | 90 |  | 21 | 0.012 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 2004 | 7 | 187.5 | 45 | 45.4 | 288.7 | 106.3 | 4.6 | 3 | 1.4 | 26.8 | 13 | 0.01 | 71 |  | 90 | 0.011 | Acetylene level is high for a Vacuum OLTC. | Oil quality is assessed as acceptable.
33000 | 2004 | 7 | 202.2 | 45 | 172.4 | 612.1 | 23.3 | 4.2 | 0.4 | 1.9 | 0 | 12 | 0.01 | 75 |  | 37 | 0.036 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 2004 | 7 | 364.9 | 44 | 116.2 | 1132.1 | 52.7 | 31.6 | 4.7 | 159.7 | 0 | 5 | 0.011 | 75 |  | 8 | 0.058 | DGA suggests mild oil overheating has occurred. | Oil quality is assessed as acceptable.
33000 | 2004 | 7 | 349.6 | 37 | 119.9 | 1291 | 87.8 | 18.6 | 4.4 | 118.9 | 0 | 4 | 0.016 | 75 |  | 5 | 0.074 | Dissolved gas levels are relatively stable. | Oil quality is assessed as acceptable.
33000 | 2004 | 7 | 593.6 | 42 | 255.2 | 1795.3 | 255.4 | 16.6 | 3.6 | 62.8 | 0 | 6 | 0.024 | 71 |  | 8 | 0.032 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 2004 | 7 | 644 | 39 | 389.2 | 3915.2 | 204.3 | 15.1 | 5.5 | 29.9 | 0 | 15 | 0.053 | 56 |  | 3 | 0.091 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable. Corrosive IEC. Corrosive ASTM 4B.
33000 | 2004 | 7 | 290.8 | 48 | 214.3 | 2243.3 | 64.6 | 4.4 | 2.2 | 5.3 | 0 | 16 | 0.061 | 92 |  | 5 | 0.044 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 2004 | 7 | 179.6 | 57 | 165.1 | 1918.9 | 8.2 | 3.9 | 0.6 | 1.8 | 0 | 7 | 0 | 75 |  | 76 | 0.012 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 2004 | 7 | 122.4 | 39 | 107.6 | 1427.8 | 7 | 3.3 | 2.1 | 2.1 | 0.3 | 5 | 0.01 | 75 |  | 70 | 0.01 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable. Corrosive IEC. Corrosive ASTM 4A.
33000 | 2004 | 7 | 177.1 | 76 | 157.8 | 1991.2 | 14.2 | 3.6 | 0.6 | 0.9 | 0 | 10 | 0.006 | 70 |  | 69 | 0.011 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable. Corrosive IEC. Corrosive ASTM 4A.
33000 | 2004 | 7 | 115.1 | 62 | 96.7 | 1733.5 | 13.4 | 2.2 | 1.5 | 1.3 | 0 | 9 | 0.001 | 76 |  | 65 | 0.008 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 2004 | 7 | 133.7 | 30 | 105.5 | 646.7 | 26.1 | 1.9 | 0 | 0.2 | 0 | 5 | 0.01 | 75 |  | 37 | 0.016 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 2004 | 7 | 134.3 | 24 | 109.2 | 887.4 | 20.1 | 4.5 | 0.2 | 0.3 | 0 | 3 | 0.004 | 90 |  | 109 | 0.008 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable. Corrosive IEC. Corrosive ASTM 4A.
33000 | 2004 | 7 | 107 | 15 | 87.3 | 875.5 | 17.3 | 1.8 | 0.2 | 0.4 | 0 | 3 | 0.003 | 76 |  | 62 | 0.013 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 2004 | 7 | 106 | 28 | 86.6 | 893.4 | 16.8 | 1.9 | 0.3 | 0.4 | 0 | 5 | 0.004 | 84 |  | 94 | 0.008 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 2003 | 8 | 258.1 | 50 | 231.9 | 1097.6 | 18.5 | 4 | 1.6 | 2.1 | 0 | 4 | 0.01 | 75 |  | 36 | 0.049 | The test results are assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 2003 | 8 | 290.2 | 50 | 220.3 | 1168.2 | 49 | 7.9 | 0.9 | 12.1 | 0 | 11 | 0.01 | 70 |  | 26 | 0.039 | The test results are assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 2003 | 8 | 109.7 | 40 | 98.1 | 960.5 | 4 | 1.9 | 1.2 | 4.5 | 0 | 2 | 0.01 | 69 |  | 26 | 0.051 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 2003 | 8 | 160.1 | 46 | 99.7 | 1020 | 22.1 | 10.9 | 1.7 | 25.7 | 0 | 3 | 0.01 | 75 |  | 8 | 0.091 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 2003 | 8 | 314.4 | 78 | 166 | 1431.9 | 115.6 | 5.3 | 2.4 | 25.1 | 0 | 3 | 0.024 | 75 |  | 19 | 0.019 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable. Corrosive IEC. Corrosive ASTM 4B.
33000 | 2003 | 8 | 359.1 | 38 | 230.3 | 2312.6 | 111 | 5 | 2.1 | 10.7 | 0 | 12 | 0.043 | 85 |  | 6.3 | 0.048 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 2003 | 8 | 187.1 | 45 | 143.1 | 1668.8 | 36.2 | 2.6 | 1.6 | 3.5 | 0.1 | 12 | 0.048 | 77 |  | 10 | 0.024 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 2003 | 8 | 322.2 | 46 | 247.9 | 813 | 66.1 | 5.5 | 0.9 | 1.8 | 0 | 6 | 0.01 | 75 |  | 227 | 0.004 | The test results are assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 2003 | 8 | 89.2 | 34 | 79.3 | 713.7 | 5.3 | 2.2 | 0.6 | 1.8 | 0 | 7 | 0.01 | 75 |  | 65 | 0.014 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 2003 | 8 | 82.15 | 42 | 70 | 821.9 | 8.4 | 2 | 0.8 | 0.95 | 0 | 5 | 0.01 | 75 |  | 50 | 0.019 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 2003 | 8 | 115.3 | 47 | 70.9 | 909.6 | 3.5 | 2.9 | 21 | 16 | 1 | 6 | 0.002 | 60 |  | 103 | 0.011 | DGA is assessed as acceptable at present. | Oil quality is assessed as acceptable.
33000 | 2003 | 8 | 70.5 | 32 | 59.2 | 907.5 | 1.8 | 9.2 | 0.3 | 0 | 0 | 4 | 0.002 | 95 |  | 131 | 0.013 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 2003 | 8 | 58.3 | 30 | 52.9 | 805.7 | 3 | 1.5 | 0.2 | 0.7 | 0 | 5 | 0.002 | 78 |  | 159 | 0.008 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 2003 | 8 | 110.4 | 37 | 101 | 578.1 | 4 | 1.8 | 0.9 | 1.9 | 0.8 | 6 | 0.01 | 75 |  | 50 | 0.054 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 2003 | 8 | 204.9 | 54 | 187.1 | 1477.5 | 7.5 | 3.2 | 0.4 | 6.7 | 0 | 5 | 0.01 | 75 |  | 65 | 0.014 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 2003 | 8 | 81 | 43 | 70.6 | 1068.8 | 4.6 | 1.9 | 0.3 | 3.6 | 0 | 3 | 0.008 | 79 |  | 141 | 0.006 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 2003 | 8 | 55.8 | 38 | 49.8 | 909.9 | 3.4 | 1.2 | 0.2 | 1.2 | 0 | 5 | 0.003 | 91 |  | 87 | 0.008 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable. Corrosive IEC. Corrosive ASTM 4A.
33000 | 2003 | 8 | 61.3 | 40 | 60 | 872.4 | 0 | 1.3 | 0 | 0 | 0 | 9 | 0.003 | 66 |  | 138 | 0.006 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 2003 | 8 | 73.2 | 56 | 63.2 | 373.1 | 8.9 | 1.1 | 0 | 0 | 0 | 5 | 0.01 | 75 |  | 134 | 0.01 | Dissolved gas analysis is assessed as acceptable. | Oil quality is assessed as acceptable. The test results are assessed as acceptable for a vacuum oltc.
33000 | 2003 | 8 | 115.6 | 40 | 105.7 | 628 | 7.1 | 1.5 | 0.6 | 0.7 | 0 | 7 | 0.01 | 56 |  | 70 | 0.016 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 2003 | 8 | 82.7 | 42 | 76.4 | 919.8 | 3.6 | 1.6 | 0 | 1.1 | 0 | 3 | 0.01 | 75 |  | 245 | 0.005 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 2003 | 8 | 80.4 | 43 | 75.3 | 970.3 | 2.4 | 1.4 | 0.2 | 1.1 | 0 | 4 | 0.01 | 75 |  | 204 | 0.007 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable. Corrosive IEC. Corrosive ASTM 4A.
33000 | 2003 | 8 | 146.4 | 60 | 135.5 | 1460.3 | 4.3 | 5.1 | 0.4 | 1.1 | 0 | 4 | 0.002 | 94 |  | 132 | 0.009 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 2003 | 8 | 44.5 | 50 | 39.9 | 914.9 | 1.9 | 1.3 | 0.3 | 1.1 | 0 | 4 | 0.003 | 94 |  | 276 | 0.004 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 2003 | 8 | 93 | 47 | 84 | 645.8 | 6.6 | 1.4 | 0.2 | 0.8 | 0 | 2 | 0.01 | 75 |  | 218 | 0.006 | Dissolved gas analysis is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 2003 | 8 | 219.6 | 61 | 201.3 | 1378.8 | 12.6 | 3 | 0 | 2.6 | 0.1 | 3 | 0.01 | 75 |  | 46 | 0.018 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 2003 | 8 | 173.9 | 64 | 160 | 1829.6 | 6.1 | 2.9 | 0 | 4.9 | 0 | 5 | 0.01 | 75 |  | 15 | 0.031 | DGA is assessed as acceptable | Oil quality is assessed as acceptable.
33000 | 2003 | 8 | 45.8 | 40 | 38.2 | 885.5 | 4.5 | 1.1 | 0.3 | 1.7 | 0 | 4 | 0.01 | 67 |  | 96 | 0.009 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 2003 | 8 | 44.5 | 38 | 36.2 | 847.5 | 3.4 | 3.8 | 0.2 | 0.9 | 0 | 5 | 0.002 | 92 |  | 62 | 0.012 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable. Corrosive IEC. Corrosive ASTM 4A.
33000 | 2003 | 8 | 37.3 | 45 | 33.1 | 689.9 | 2 | 1.9 | 0.1 | 0.2 | 0 | 4 | 0.002 | 88 |  | 82 | 0.01 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable. Corrosive IEC. Corrosive ASTM 4A.
33000 | 2002 | 9 | 115.2 | 47 | 99.4 | 369.7 | 12.5 | 2 | 0.5 | 0.8 | 0 | 5 | 0.01 | 61 |  | 118 | 0.009 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 2002 | 9 | 101.4 | 34 | 94.1 | 540.4 | 4.4 | 2.1 | 0.2 | 0.5 | 0.1 | 6 | 0.01 | 75 |  | 67 | 0.012 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 2002 | 9 | 111.9 | 35 | 104.7 | 1128.1 | 0 | 2.3 | 0.8 | 4.1 | 0 | 3 | 0.01 | 75 |  | 97 | 0.014 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 2002 | 9 | 93.6 | 40 | 84.7 | 1156.3 | 3.5 | 1.8 | 0.4 | 3 | 0.2 | 6 | 0.01 | 75 |  | 104 | 0.008 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 2002 | 9 | 132 | 47 | 120.6 | 1158.6 | 5.5 | 4.1 | 0.2 | 1.6 | 0 | 6 | 0.01 | 75 |  | 122 | 0.007 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable. Corrosive IEC. Corrosive ASTM 4A.
33000 | 2002 | 9 | 88 | 38 | 82 | 1319.7 | 2.3 | 1.5 | 0.4 | 1.8 | 0 | 4 | 0.004 | 83 |  | 61 | 0.012 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 2002 | 9 | 65.4 | 40 | 60.3 | 1084.6 | 2.3 | 1.4 | 0.5 | 0.9 | 0 | 8 | 0.001 | 91 |  | 148 | 0.006 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 2002 | 9 | 95.4 | 33 | 86.9 | 620.9 | 4.9 | 2.6 | 0.2 | 0.8 | 0 | 1 | 0.01 | 75 |  | 78 | 0.013 | The test results are assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 2002 | 9 | 85.1 | 40 | 76 | 691.6 | 5.2 | 3 | 0.2 | 0.7 | 0 | 4 | 0.01 | 75 |  | 103 | 0.013 | The test results are assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 2002 | 9 | 237.6 | 42 | 94 | 374.1 | 92.9 | 7 | 5.7 | 2.4 | 35.6 | 16 | 0.01 | 48 |  | 52 | 0.019 | The test results are assessed as acceptable for tapchanger. | Oil quality is assessed as acceptable.
33000 | 2002 | 9 | 76.8 | 40 | 70.1 | 1192.5 | 2.3 | 2.5 | 0.7 | 1 | 0.2 | 6 | 0 | 75 |  | 38 | 0.023 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 2002 | 9 | 78.3 | 40 | 75.1 | 1239.7 | 0 | 2.2 | 0.5 | 0.5 | 0 | 4 | 0.01 | 75 |  | 30 | 0.026 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 2002 | 9 | 68.1 | 39 | 64.6 | 1204 | 0 | 2.1 | 0.6 | 0.8 | 0 | 3 | 0.01 | 75 |  | 55 | 0.024 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 2002 | 9 | 72.3 | 44 | 68.2 | 1292.1 | 1.5 | 1.9 | 0.7 | 0 | 0 | 3 | 0.003 | 80 |  | 52 | 0.027 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 2002 | 9 | 67.2 | 41.81 | 62.4 | 1295.8 | 0 | 1.8 | 1.9 | 1.1 | 0 | 3 | 0.004 | 89 |  | 23 | 0.032 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 2002 | 9 | 41.2 | 38 | 36.3 | 927.8 | 0 | 1.2 | 3.1 | 0.6 | 0 | 4 | 0.002 | 85 |  | 50 | 0.027 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 2002 | 9 | 194.3 | 59 | 182.2 | 1203.9 | 6.4 | 3.6 | 0.9 | 1.2 | 0 | 3 | 0.01 | 66 |  | 22 | 0.058 | Dissolved gas analysis is assessed as acceptable. Oil quality is assessed as acceptable.
33000 | 2002 | 9 | 73.4 | 56 | 67.1 | 844.4 | 3.4 | 2.1 | 0.2 | 0.6 | 0 | 3 | 0.01 | 75 |  | 29 | 0.031 | Dissolved gas analysis is assessed as acceptable. Oil quality is assessed as acceptable.
33000 | 2002 | 9 | 113.7 | 65 | 105.6 | 1065 | 4.4 | 2.5 | 0.2 | 1 | 0 | 7 | 0.01 | 75 |  | 82 | 0.011 | Dissolved gas analysis is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 2002 | 9 | 114.2 | 59 | 107.4 | 1238 | 3.2 | 2.5 | 0.5 | 0.6 | 0 | 5 | 0.01 | 75 |  | 29 | 0.032 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 2002 | 9 | 50.4 | 35 | 47.3 | 858.5 | 0 | 1.7 | 0.9 | 0.5 | 0 | 9 | 0.01 | 75 |  | 38 | 0.023 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 2002 | 9 | 53.3 | 62 | 46.1 | 779.3 | 4.8 | 1.3 | 0.8 | 0.3 | 0 | 11 | 0 | 75 |  | 50 | 0.023 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable. Corrosive IEC. Corrosive ASTM 4A.
33000 | 2002 | 9 | 35.7 | 47 | 31.6 | 687 | 2 | 1.3 | 0.6 | 0.2 | 0 | 13 | 0.002 | 86 |  | 30 | 0.026 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable. Corrosive IEC. Corrosive ASTM 4A.
33000 | 2002 | 9 | 172.1 | 36 | 143.7 | 683.7 | 24 | 3 | 0.4 | 1 | 0 | 3 | 0.01 | 75 |  | 82 | 0.015 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 2002 | 9 | 151 | 40 | 126.2 | 803.8 | 18.5 | 4.9 | 0.5 | 0.9 | 0 | 1 | 0.01 | 75 |  | 115 | 0.009 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 2002 | 9 | 106.3 | 26 | 94.3 | 962.3 | 5.9 | 5.3 | 0.8 | 0 | 0 | 4 | 0.01 | 58 |  | 68 | 0.015 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 2002 | 9 | 115.9 | 43 | 100.9 | 836.9 | 6.3 | 2.5 | 4.6 | 1.2 | 0.4 | 5 | 0.01 | 75 |  | 69 | 0.014 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 2002 | 9 | 112 | 42 | 99.3 | 975.3 | 3.1 | 2.4 | 5.9 | 1.3 | 0 | 3 | 0 | 69 |  | 79 | 0.013 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable. Corrosive IEC. Corrosive ASTM 4A.
33000 | 2002 | 9 | 129.5 | 42 | 114.4 | 1112.3 | 2.6 | 0.8 | 10.8 | 0.9 | 0 | 7 | 0.002 | 81 |  | 27 | 0.022 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 2002 | 9 | 249.9 | 67 | 215.6 | 1589 | 15.4 | 4 | 13.4 | 1.5 | 0 | 5 | 0.003 | 82 |  | 44 | 0.014 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 2002 | 9 | 167.3 | 55 | 146.4 | 851.7 | 18.6 | 1.7 | 0.3 | 0.3 | 0 | 5 | 0.01 | 72 |  | 57 | 0.019 | The test results are assessed as acceptable.
33000 | 2002 | 9 | 184.4 | 70 | 166.2 | 1189.6 | 14.4 | 3.4 | 0.4 | 0 | 0 | 6 | 0.01 | 73 |  | 64 | 0.014 | The test results are assessed as acceptable.
33000 | 2002 | 9 | 241.3 | 46 | 221.9 | 1705 | 14.1 | 3.5 | 0.7 | 1.1 | 0 | 3 | 0.01 | 44 |  | 101 | 0.01 | The test results are assessed as acceptable.
33000 | 2002 | 9 | 29.8 | 28 | 27.3 | 509 | 0.6 | 1.2 | 0.4 | 0.3 | 0 | 4 | 0.01 | 60 |  | 57 | 0.017 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 2002 | 9 | 344.8 | 33 | 261.7 | 648.9 | 75.8 | 4 | 1 | 2.3 | 0 | 5 | 0.01 | 75 |  | 172 | 0.008 | Dissolved gas analysis is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 2002 | 9 | 356.6 | 34 | 310.5 | 660.1 | 40.5 | 3.6 | 1 | 1 | 0 | 5 | 0.01 | 75 |  | 111 | 0.007 | Dissolved gas analysis is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 2002 | 9 | 419.1 | 20 | 357.2 | 753.3 | 54.7 | 4.5 | 1.6 | 1.1 | 0 | 3 | 0.01 | 52 |  | 124.2 | 0.008 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 2002 | 9 | 502.5 | 24 | 458.9 | 814.6 | 34.7 | 5.1 | 2.2 | 1.6 | 0 | 3 | 0 | 75 |  | 78 | 0.01 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 2002 | 9 | 706.8 | 16 | 651.3 | 1030.9 | 32.5 | 15.9 | 3.5 | 3.6 | 0 | 4 | 0.01 | 75 |  | 48 | 0.012 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable. Corrosive IEC. Corrosive ASTM 4A.
33000 | 2002 | 9 | 647.3 | 16 | 597.3 | 1190.8 | 28 | 9.9 | 5.1 | 7 | 0 | 2 | 0.003 | 59 |  | 69 | 0.008 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 2002 | 9 | 533.7 | 20 | 479.3 | 1076 | 21.8 | 12.7 | 4.7 | 15.2 | 0 | 6 | 0.004 | 88 |  | 75 | 0.007 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 2002 | 9 | 100.5 | 44 | 91.7 | 1337.4 | 2.4 | 3.1 | 0.4 | 2.8 | 0.1 | 3 | 0.01 | 50 |  | 130 | 0.008 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 2002 | 9 | 488.8 | 41.81 | 457 | 2619 | 17 | 9 | 1.4 | 4.4 | 0 | 9 | 0.01 | 75 |  | 58 | 0.013 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 2002 | 9 | 101.6 | 41.81 | 93.1 | 1009.5 | 2.4 | 2.7 | 0.6 | 2.8 | 0 | 4 | 0.01 | 58 |  | 83 | 0.008 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 2002 | 9 | 84 | 41.81 | 79.2 | 1009 | 0 | 2.5 | 0.4 | 1.9 | 0 | 5 | 0.01 | 75 |  | 87 | 0.011 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable. Corrosive IEC. Corrosive ASTM 4A.
33000 | 2002 | 9 | 26.5 | 25 | 22.9 | 601.1 | 1.6 | 1 | 0.1 | 0.9 | 0 | 7 | 0.002 | 85 |  | 91 | 0.01 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 2002 | 9 | 174.7 | 42 | 56.8 | 476.6 | 18.7 | 2.4 | 95.2 | 0.5 | 1.1 | 10 | 0.01 | 75 |  | 49 | 0.019 | Ethylene level is high. Other dissolved gas levels are assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 2002 | 9 | 71.6 | 42 | 66.2 | 854.1 | 2 | 1.8 | 0.3 | 1 | 0.3 | 3 | 0.01 | 75 |  | 57 | 0.016 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 2002 | 9 | 59.8 | 48 | 57.9 | 873.2 | 0 | 1.4 | 0.1 | 0.4 | 0 | 4 | 0.01 | 75 |  | 68 | 0.022 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 2002 | 9 | 48.4 | 52 | 47.5 | 979.6 | 0 | 0.4 | 0.3 | 0.2 | 0 | 6 | 0.01 | 75 |  | 30 | 0.022 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable. Corrosive IEC. Corrosive ASTM 4A.
33000 | 2002 | 9 | 51.4 | 47 | 36.5 | 995.2 | 11.9 | 1.5 | 0.3 | 1.2 | 0 | 5 | 0.003 | 80 |  | 57 | 0.02 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 2002 | 9 | 65 | 37 | 60.9 | 256.5 | 2.5 | 1.1 | 0 | 0.5 | 0 | 10 | 0.01 | 75 |  | 148 | 0.022 | The test results are assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 2002 | 9 | 79.8 | 23 | 78 | 383.3 | 0 | 1.3 | 0.2 | 0.3 | 0 | 2 | 0.01 | 72 |  | 77 | 0.022 | The test results are assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 2002 | 9 | 96.3 | 37 | 94.1 | 626.7 | 0 | 1.4 | 0.2 | 0.5 | 0.1 | 4 | 0.01 | 75 |  | 274 | 0.005 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 2002 | 9 | 98.2 | 32 | 95.3 | 990.2 | 0 | 1.7 | 0.3 | 0.9 | 0 | 7 | 0.01 | 75 |  | 352 | 0.005 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 2002 | 9 | 112.4 | 32 | 106.9 | 1159.3 | 0 | 2 | 0.4 | 3.1 | 0 | 4 | 0.01 | 75 |  | 367 | 0.004 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable. Corrosive IEC. Corrosive ASTM 4A.
33000 | 2002 | 9 | 55.2 | 41.81 | 52.1 | 918.6 | 0 | 1.3 | 0.3 | 1.5 | 0 | 4 | 0.003 | 66 |  | 240 | 0.004 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 2002 | 9 | 37.2 | 56 | 33.3 | 769.9 | 1.6 | 1.5 | 0.5 | 0.3 | 0 | 5 | 0.002 | 80 |  | 165 | 0.005 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 2002 | 9 | 50.6 | 35 | 48.7 | 835.7 | 0 | 1.2 | 0.7 | 0 | 0 | 7 | 0.002 | 58 |  | 131 | 0.008 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 2002 | 9 | 123.3 | 33 | 114.8 | 562.6 | 5.9 | 1.7 | 0.5 | 0.4 | 0 | 5 | 0.01 | 75 |  | 142 | 0.007 | Dissolved gas analysis is assessed as acceptable. Oil quality is assessed as acceptable.
33000 | 2002 | 9 | 104.6 | 34 | 96 | 526.5 | 4.1 | 1.6 | 2.3 | 0.6 | 0 | 4 | 0.01 | 75 |  | 175 | 0.009 | Dissolved gas analysis is assessed as acceptable. Oil quality is assessed as acceptable.
33000 | 2002 | 9 | 196.4 | 54 | 183.9 | 1112.8 | 9 | 2.3 | 0.2 | 1 | 0 | 6 | 0.01 | 75 |  | 85 | 0.01 | Dissolved gas analysis is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 2002 | 9 | 310.7 | 61 | 279.2 | 2073.3 | 19 | 4.9 | 1.6 | 6 | 0 | 4 | 0.01 | 75 |  | 59 | 0.015 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 2002 | 9 | 203.1 | 49 | 170.3 | 1505.9 | 20.5 | 3.8 | 2.4 | 6.1 | 0 | 6 | 0.01 | 75 |  | 76 | 0.009 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 2002 | 9 | 52.7 | 37 | 42.3 | 764.4 | 7.3 | 1.2 | 0.6 | 1.3 | 0 | 4 | 0 | 75 |  | 76 | 0.009 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable. Corrosive IEC. Corrosive ASTM 4A.
33000 | 2002 | 9 | 47.6 | 46 | 41 | 689.2 | 3.9 | 2.3 | 0.3 | 0.1 | 0 | 6 | 0.001 | 91 |  | 52 | 0.011 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable. Corrosive IEC. Corrosive ASTM 4A.
33000 | 2002 | 9 | 98.2 | 42 | 70.5 | 345.8 | 26.5 | 0.9 | 0.1 | 0.2 | 0 | 4 | 0.01 | 61 |  | 80 | 0.011 | The test results are assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 2002 | 9 | 80.4 | 30 | 73.9 | 499 | 4.7 | 1.3 | 0.1 | 0.4 | 0 | 6 | 0.01 | 74 |  | 86 | 0.049 | The test results are assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 2002 | 9 | 74.5 | 41.81 | 62.2 | 845.6 | 0 | 4.5 | 0.4 | 7.4 | 0 | 4 | 0 | 75 |  | 85 | 0.015 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 2002 | 9 | 65.3 | 36 | 56.1 | 835.8 | 7.4 | 1.3 | 0.1 | 0.3 | 0.1 | 2 | 0.01 | 75 |  | 172 | 0.007 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 2002 | 9 | 118.4 | 45 | 108.2 | 986.5 | 1.3 | 8.1 | 0.3 | 0.5 | 0 | 2 | 0.01 | 75 |  | 235 | 0.006 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable. Corrosive IEC. Corrosive ASTM 4A.
33000 | 2002 | 9 | 67.2 | 41.81 | 62.5 | 1076.9 | 0.9 | 2.9 | 0.5 | 0.4 | 0 | 3 | 0.004 | 81 |  | 97 | 0.012 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 2002 | 9 | 37 | 34 | 34.2 | 866.6 | 0 | 1 | 1.6 | 0.2 | 0 | 5 | 0.001 | 72 |  | 167 | 0.006 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 2002 | 9 | 76.6 | 27 | 69.8 | 404.3 | 5.2 | 1.3 | 0.1 | 0.2 | 0 | 3 | 0.01 | 62 |  | 136 | 0.01 | Dissolved gas analysis is assessed as acceptable. Oil quality is assessed as acceptable. Comments are based on the analysis results without prior knowledge of any history or operating parameters of the transformer.
33000 | 2002 | 9 | 114.6 | 42 | 106.4 | 802.9 | 2.8 | 5.4 | 0 | 0 | 0 | 4 | 0 | 75 |  | 306.6 | 0.006 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 2002 | 9 | 144.5 | 37 | 102.2 | 969.7 | 36.3 | 2.8 | 0.7 | 1.3 | 1.2 | 4 | 0.01 | 75 |  | 267 | 0.007 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 2002 | 9 | 307.1 | 54 | 284.8 | 1901.4 | 6.4 | 11.1 | 0.5 | 4.3 | 0 | 4 | 0.01 | 75 |  | 351 | 0.004 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable. Corrosive IEC. Corrosive ASTM 4A.
33000 | 2002 | 9 | 58.7 | 32 | 54.3 | 1211.3 | 0 | 1.4 | 0.5 | 2.5 | 0 | 2 | 0.004 | 69 |  | 116 | 0.008 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 2002 | 9 | 38.9 | 30 | 35.6 | 722.6 | 0 | 1.3 | 1.2 | 0.8 | 0 | 3 | 0 | 86 |  | 201 | 0.01 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 2001 | 10 | 106 | 29 | 93.6 | 1538.7 | 4.7 | 2.7 | 0.8 | 4.1 | 0.1 | 6 | 0.01 | 72 |  | 29 | 0.02 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 2001 | 10 | 46.5 | 28 | 36 | 913 | 6 | 2 | 0.5 | 2 | 0 | 3 | 0.01 | 75 |  | 39 | 0.013 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 2001 | 10 | 83.1 | 28 | 70.4 | 759 | 2.5 | 8.5 | 0.5 | 0.9 | 0.3 | 6 | 0.01 | 75 |  | 42 | 0.012 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable. Corrosive IEC. Corrosive ASTM 4A.
33000 | 2001 | 10 | 29.7 | 30 | 27.3 | 737.4 | 0.4 | 1.1 | 0.2 | 0.7 | 0 | 5 | 0.004 | 81 |  | 33 | 0.012 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 2001 | 10 | 26.3 | 24 | 24 | 664 | 0 | 0.9 | 1.1 | 0.3 | 0 | 4 | 0.002 | 52 |  | 55 | 0.011 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 2001 | 10 | 41 | 33 | 39 | 274 | 1 | 1 | 0 | 0 | 0 | 6 | 0.01 | 64 |  | 163.2 | 0.006 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 2001 | 10 | 78.2 | 38 | 70.7 | 839 | 4.6 | 1.6 | 0.6 | 0.7 | 0 | 4 | 0.01 | 59 |  | 38 | 0.018 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 2001 | 10 | 84.7 | 41.81 | 74.8 | 956.9 | 6.3 | 1.8 | 0.3 | 1.5 | 0 | 5 | 0 | 68 |  | 46 | 0.013 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 2001 | 10 | 89.5 | 31 | 73.8 | 1051 | 5.7 | 2.1 | 0.9 | 6.8 | 0.2 | 6 | 0.002 | 88 |  | 29 | 0.019 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable. Corrosive IEC. Corrosive ASTM 4A.
33000 | 2001 | 10 | 82.2 | 38 | 67 | 1098.6 | 7.6 | 3.8 | 0.5 | 3.3 | 0 | 7 | 0.002 | 80 |  | 76 | 0.008 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 2001 | 10 | 73.5 | 36 | 63.4 | 1025.4 | 4.5 | 1.9 | 0.8 | 2.8 | 0.1 | 6 | 0.002 | 74 |  | 40 | 0.012 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 2001 | 10 | 65 | 34 | 51 | 394 | 10 | 2 | 1 | 1 | 0 | 4 | 0.01 | 75 |  | 120.1 | 0.009 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 2001 | 10 | 53 | 24 | 43 | 286 | 6 | 3 | 1 | 0 | 0 | 4 | 0.01 | 75 |  | 65 | 0.014 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 2001 | 10 | 72 | 43 | 61.7 | 685.3 | 7.8 | 1.6 | 0.6 | 0.3 | 0 | 6 | 0.01 | 75 |  | 65 | 0.012 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 2001 | 10 | 113.7 | 41 | 103.2 | 1061 | 7 | 2.1 | 0.4 | 1 | 0 | 5 | 0.01 | 68 |  | 78 | 0.01 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 2001 | 10 | 47 | 43 | 41.4 | 831.6 | 2.5 | 1.6 | 0.5 | 1 | 0 | 5 | 0.01 | 0 |  | 88 | 0.009 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 2001 | 10 | 50.5 | 35 | 43.7 | 748.9 | 4.8 | 1.3 | 0.3 | 0.4 | 0 | 7 | 0.01 | 75 |  | 99 | 0.008 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 2001 | 10 | 81.2 | 23 | 36.2 | 805.2 | 35.8 | 1.9 | 2.2 | 2.7 | 2.4 | 5 | 0.01 | 72 |  | 85 | 0.007 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 2001 | 10 | 45 | 40 | 40.3 | 831.4 | 2.2 | 1.8 | 0.3 | 0.4 | 0 | 7 | 0.001 | 86 |  | 108 | 0.007 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 2001 | 10 | 52.7 | 36 | 41.6 | 772 | 9.3 | 1.3 | 0.3 | 0.2 | 0 | 8 | 0.003 | 85 |  | 85 | 0.008 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 2001 | 10 | 71 | 35 | 60 | 234 | 9 | 1 | 0 | 1 | 0 | 3 | 0.01 | 75 |  | 148.2 | 0.01 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 2001 | 10 | 137 | 38 | 115 | 557 | 16 | 3 | 0 | 3 | 0 | 7 | 0.01 | 75 |  | 110.4 | 0.009 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 2001 | 10 | 147 | 45 | 130.7 | 1133.5 | 8.9 | 2.7 | 0.6 | 4 | 0.1 | 5 | 0 | 66 |  | 114 | 0.005 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 2001 | 10 | 181.4 | 42 | 167.5 | 1628.9 | 7.4 | 2.7 | 1 | 2.8 | 0 | 3 | 0.01 | 75 |  | 34 | 0.0131 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 2001 | 10 | 181.8 | 51 | 164 | 2008.4 | 9.3 | 3.6 | 0.9 | 4 | 0 | 9 | 0.01 | 75 |  | 28 | 0.012 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable. Corrosive IEC. Corrosive ASTM 4A.
33000 | 2001 | 10 | 233 | 77 | 153.4 | 1944.4 | 72.4 | 2.5 | 1.3 | 3.1 | 0.3 | 8 | 0.01 | 75 |  | 20 | 0.015 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable. Corrosive IEC. Corrosive ASTM 4A.
33000 | 2001 | 10 | 108.7 | 46 | 92.4 | 1386.6 | 12 | 1.7 | 0.9 | 1.7 | 0 | 8 | 0.009 | 85 |  | 11 | 0.025 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 2001 | 10 | 22 | 28 | 16 | 98 | 3 | 2 | 0 | 1 | 0 | 3 | 0.01 | 75 |  | 148.8 | 0.004 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 2001 | 10 | 105 | 34 | 91 | 380 | 8 | 4 | 0 | 2 | 0 | 6 | 0.01 | 75 |  | 67 | 0.013 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 2001 | 10 | 103.7 | 40 | 90.2 | 829.7 | 9.4 | 2 | 0.8 | 1.3 | 0 | 4 | 0.01 | 75 |  | 49 | 0.018 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 2001 | 10 | 123 | 43 | 93.8 | 1009.2 | 25.7 | 2.1 | 0.5 | 0.8 | 0.1 | 4 | 0.01 | 75 |  | 60 | 0.011 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 2001 | 10 | 140.2 | 36 | 120.3 | 1012.4 | 13.6 | 4.3 | 0.3 | 1.7 | 0 | 4 | 0.01 | 75 |  | 87 | 0.007 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable. Corrosive IEC. Corrosive ASTM 4A.
33000 | 2001 | 10 | 69.2 | 18 | 63.1 | 935.8 | 5.6 | 0.5 | 0 | 0 | 0 | 6 | 0.005 | 83 |  | 58 | 0.008 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 2001 | 10 | 64.5 | 34 | 55.5 | 855.2 | 7 | 1.2 | 0.8 | 0 | 0 | 8 | 0.006 | 87 |  | 47 | 0.011 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 2001 | 10 | 103.5 | 50 | 87.5 | 404.6 | 11.3 | 2.6 | 0.5 | 1.6 | 0 | 4 | 0.01 | 75 |  | 53 | 0.014 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 2001 | 10 | 114.2 | 38 | 99.6 | 892.7 | 10.5 | 1.8 | 1 | 1.3 | 0 | 8 | 0.01 | 74 |  | 70 | 0.011 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 2001 | 10 | 94.6 | 40 | 81.5 | 779.1 | 9.2 | 1.9 | 0.5 | 1.5 | 0 | 6 | 0.01 | 75 |  | 55 | 0.015 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 2001 | 10 | 116.9 | 37 | 84 | 890.4 | 17 | 3.5 | 1.2 | 11.2 | 0 | 5 | 0.01 | 75 |  | 39 | 0.015 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 2001 | 10 | 80.6 | 42 | 70 | 895.1 | 7.2 | 1.6 | 0.6 | 1.2 | 0 | 6 | 0.006 | 90 |  | 54 | 0.01 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable. Corrosive IEC. Corrosive ASTM 4A.
33000 | 2001 | 10 | 89.5 | 36 | 66.2 | 967.7 | 20.6 | 1.4 | 0.5 | 0.7 | 0.1 | 7 | 0.002 | 75 |  | 45 | 0.012 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 2001 | 10 | 76.6 | 36 | 65.6 | 957.1 | 8.4 | 1.5 | 0.6 | 0.3 | 0.2 | 11 | 0.004 | 65 |  | 25 | 0.02 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 2001 | 10 | 150 | 39 | 89 | 848 | 26 | 9 | 2 | 24 | 0 | 6 | 0.01 | 75 |  | 45 | 0.026 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 2001 | 10 | 176.7 | 44 | 157.4 | 1380.1 | 12.9 | 4 | 1.5 | 0.8 | 0.1 | 6 | 0.01 | 75 |  | 63 | 0.011 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 2001 | 10 | 114.3 | 42 | 99.7 | 1386.5 | 8.2 | 6.1 | 0.2 | 0.1 | 0 | 2 | 0.01 | 75 |  | 26 | 0.027 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 2001 | 10 | 135.3 | 41 | 112 | 1396.3 | 12.7 | 3.6 | 1.3 | 4.6 | 1.1 | 4 | 0.01 | 75 |  | 47 | 0.014 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 2001 | 10 | 175 | 50 | 146.5 | 1297.1 | 17.1 | 9.8 | 0.8 | 0.8 | 0 | 3 | 0.01 | 75 |  | 75 | 0.011 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable. Corrosive IEC. Corrosive ASTM 4A.
33000 | 2001 | 10 | 67.1 | 42 | 57.8 | 1013.6 | 5.9 | 2 | 0.9 | 0.4 | 0.1 | 7 | 0.004 | 75 |  | 59 | 0.011 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 2001 | 10 | 46.1 | 36 | 40.6 | 905.9 | 3.2 | 1.3 | 0.7 | 0.3 | 0 | 8 | 0.001 | 74 |  | 67 | 0.009 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 2001 | 10 | 85 | 32 | 72.5 | 639.9 | 7.2 | 2.7 | 1.4 | 1 | 0.2 | 2 | 0.01 | 75 |  | 44 | 0.013 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 2001 | 10 | 90.9 | 39 | 61.2 | 671.9 | 25.7 | 2.4 | 0.9 | 0.7 | 0 | 5 | 0.01 | 75 |  | 74 | 0.013 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 2001 | 10 | 87.6 | 38 | 76.1 | 780.7 | 8 | 2 | 0.8 | 0.7 | 0 | 9 | 0.01 | 63 |  | 40 | 0.028 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 2001 | 10 | 85.3 | 41.81 | 73.5 | 879.4 | 9.3 | 1.8 | 0.3 | 0.4 | 0 | 4 | 0 | 75 |  | 60 | 0.013 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 2001 | 10 | 73.7 | 34 | 64.7 | 849.7 | 6.3 | 1.7 | 0.5 | 0.5 | 0 | 4 | 0.005 | 90 |  | 66 | 0.013 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable. Corrosive IEC. Corrosive ASTM 4A.
33000 | 2001 | 10 | 76.8 | 44 | 62.3 | 903.9 | 9.5 | 2.6 | 1.1 | 1.2 | 0.1 | 4 | 0.003 | 76 |  | 67 | 0.012 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 2001 | 10 | 64.7 | 39 | 54.5 | 912.8 | 7.7 | 1.4 | 0.5 | 0.4 | 0.2 | 31 | 0.002 | 25 |  | 34 | 0.019 | DGA is assessed as acceptable. | Breakdown voltage is low. Other oil quality results are assessed as acceptable.
33000 | 2001 | 10 | 88 | 36 | 67 | 533 | 7 | 4 | 1 | 9 | 0 | 6 | 0.01 | 75 |  | 54 | 0.018 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 2001 | 10 | 82.9 | 38 | 67.3 | 733.2 | 7 | 3 | 0.8 | 4.8 | 0 | 5 | 0.01 | 75 |  | 53 | 0.018 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 2001 | 10 | 182.8 | 34 | 164.7 | 1383.9 | 5.9 | 4 | 1.3 | 6.8 | 0.1 | 6 | 0.01 | 75 |  | 51.2 | 0.018 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 2001 | 10 | 64.9 | 27 | 45.8 | 757 | 14.1 | 1.6 | 0.5 | 2.5 | 0.4 | 3 | 0 | 75 |  | 38 | 0.016 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 2001 | 10 | 104.8 | 27 | 81.6 | 799.2 | 12.6 | 8.4 | 0.3 | 1.9 | 0 | 4 | 0.01 | 75 |  | 49 | 0.015 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable. Corrosive IEC. Corrosive ASTM 4A.
33000 | 2001 | 10 | 42.3 | 25 | 35.5 | 793 | 3.6 | 1.3 | 0.7 | 1 | 0.2 | 3 | 0 | 75 |  | 78 | 0.011 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 2001 | 10 | 53.8 | 42 | 46.6 | 820.2 | 3.6 | 2.1 | 0.3 | 0.9 | 0.3 | 8 | 0.002 | 85 |  | 54 | 0.014 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 2001 | 10 | 39 | 29 | 37.3 | 725.6 | 0 | 1.4 | 0.3 | 0 | 0 | 7 | 0 | 94 |  | 47 | 0.015 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 2001 | 10 | 93.2 | 35 | 84.3 | 689.3 | 6.3 | 1.8 | 0.2 | 0.5 | 0.1 | 4 | 0.01 | 68 |  | 39 | 0.023 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 2001 | 10 | 221.6 | 39 | 207.1 | 1471.5 | 9.1 | 3.4 | 0.4 | 1.6 | 0 | 6 | 0.01 | 75 |  | 50 | 0.011 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 2001 | 10 | 38.2 | 41.81 | 36.4 | 868.1 | 0 | 1.3 | 0.2 | 0.3 | 0 | 6 | 0.01 | 75 |  | 70 | 0.015 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 2001 | 10 | 48.3 | 31 | 46.7 | 889.9 | 0 | 1.4 | 0.2 | 0 | 0 | 4 | 0.01 | 75 |  | 63 | 0.011 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 2001 | 10 | 40.6 | 36 | 39.1 | 847.3 | 0 | 1.2 | 0.2 | 0.1 | 0 | 4 | 0.01 | 75 |  | 70 | 0.012 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 2001 | 10 | 41.5 | 40 | 36 | 847.3 | 3.9 | 1.3 | 0.1 | 0.2 | 0 | 4 | 0 | 91 |  | 48 | 0.015 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 2001 | 10 | 38.1 | 36 | 30.9 | 886.4 | 5.5 | 1.1 | 0.2 | 0.4 | 0 | 7 | 0.004 | 77 |  | 38 | 0.018 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 2001 | 10 | 1171 | 44 | 653.3 | 1920.5 | 473.2 | 36.5 | 0.7 | 7.3 | 0 | 3 | 0.01 | 75 |  | 64 | 0.016 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 2001 | 10 | 1434.2 | 30 | 451.6 | 1764.8 | 942.1 | 32.8 | 0.6 | 7.1 | 0 | 4 | 0 | 75 |  | 99 | 0.01 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 2001 | 10 | 1720 | 40 | 565.1 | 2177.1 | 1105.3 | 35.5 | 0.9 | 13.2 | 0 | 6 | 0.01 | 75 |  | 48 | 0.015 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 2001 | 10 | 1871.7 | 45 | 564.6 | 2215.1 | 1263.9 | 30.5 | 1.2 | 11.5 | 0 | 5 | 0 | 75 |  | 75 | 0.013 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 2001 | 10 | 145.3 | 36 | 129.6 | 1035.8 | 11.6 | 1.9 | 0.5 | 1.4 | 0.3 | 4 | 0.01 | 75 |  | 107 | 0.013 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 2001 | 10 | 112.9 | 48 | 104.4 | 905.5 | 5.2 | 2.1 | 0.2 | 1 | 0 | 7 | 0.01 | 75 |  | 88 | 0.011 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 2001 | 10 | 121.9 | 36 | 113.9 | 1118 | 4.2 | 2.2 | 0.3 | 1.3 | 0 | 5 | 0.01 | 75 |  | 104 | 0.009 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 2001 | 10 | 112.4 | 32 | 100 | 1262.5 | 6.4 | 2 | 0.6 | 1.1 | 2.3 | 4 | 0.01 | 75 |  | 63 | 0.012 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 2001 | 10 | 131.6 | 52 | 125.7 | 1510.5 | 2.7 | 2.4 | 0 | 0.8 | 0 | 29 | 0.01 | 38 |  | 29 | 0.019 | DGA is assessed as acceptable. | Breakdown voltage is slightly low. Other oil quality results are assessed as acceptable. Corrosive IEC. Corrosive ASTM 4A.
33000 | 2001 | 10 | 126.9 | 41.81 | 120.5 | 1828.9 | 3 | 2.6 | 0.3 | 0.5 | 0 | 16 | 0.003 | 31 |  | 59 | 0.012 | DGA is assessed as acceptable. | Breakdown voltage is low. Other oil quality results are assessed as acceptable.
33000 | 2001 | 10 | 94.1 | 67 | 88.3 | 1419.5 | 2.4 | 2.7 | 0.4 | 0.3 | 0 | 40 | 0.002 | 25 |  | 131 | 0.006 | DGA is assessed as acceptable. | Breakdown voltage is low. Other oil quality results are assessed as acceptable.
33000 | 2001 | 10 | 169.2 | 94 | 158.2 | 1812.8 | 5.4 | 3 | 1.1 | 1.5 | 0 | 7 | 0.002 | 84 |  | 94 | 0.006 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 2001 | 10 | 150.8 | 84 | 147.5 | 1784.6 | 0 | 2.9 | 0.4 | 0 | 0 | 8 | 0.003 | 68 |  | 72 | 0.01 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 2000 | 11 | 208 | 67 | 171 | 754 | 22 | 6 | 1 | 8 | 0 | 9 | 0.01 | 75 |  | 109.2 | 0.01 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 2000 | 11 | 939.1 | 65 | 414.8 | 3693.8 | 380.3 | 44.8 | 7.9 | 89.7 | 1.6 | 28 | 0.024 | 33 |  | 8 | 0.039 | Hydrogen and ethane levels are slightly high compared to main tank sample. | Otherwise test results are consistent with main tank sample.
33000 | 2000 | 11 | 744.9 | 65 | 549.8 | 4759.1 | 158.9 | 9.3 | 6.1 | 20.6 | 0.2 | 12 | 0.03 | 52 |  | 15.3437 | 0.023397 | 2-furfural and carbon oxide levels are high for transformer age. Other test results are assessed as acceptable.
33000 | 2000 | 11 | 242 | 46 | 204 | 3150 | 23 | 4 | 3 | 8 | 0 | 10 | 0.03 | 75 |  | 9 | 0.034 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 2000 | 11 | 133 | 30 | 107.3 | 2586 | 16.5 | 2.5 | 3.4 | 3.1 | 0.2 | 6 | 0.045 | 67 |  | 6 | 0.045 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 2000 | 11 | 55.5 | 32 | 45.7 | 1773.8 | 4.4 | 1.4 | 2 | 2 | 0 | 4 | 0.041 | 75 |  | 7 | 0.039 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 2000 | 11 | 48.2 | 28 | 43.6 | 1494.1 | 0 | 2 | 1.1 | 1.5 | 0 | 4 | 0.041 | 86 |  | 7 | 0.04 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 2000 | 11 | 0 | 44 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6 | 0 | 0 |  | 0 | 0
33000 | 2000 | 11 | 177 | 54 | 148 | 666 | 20 | 5 | 2 | 2 | 0 | 6 | 0.01 | 75 |  | 74.2 | 0.006 | Test results are assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 2000 | 11 | 103.9 | 40.3 | 95.7 | 1611.3 | 5.5 | 1.6 | 0.4 | 0.7 | 0 | 4 | 0.01 | 75 |  | 111 | 0.006 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 2000 | 11 | 94.3 | 29 | 88.2 | 1280.4 | 3.6 | 1.3 | 0.6 | 0.6 | 0 | 5 | 0.003 | 74 |  | 75 | 0.007 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable. Corrosive IEC. Corrosive ASTM 4A.
33000 | 2000 | 11 | 64.8 | 28 | 54.7 | 1172.2 | 7.2 | 1.7 | 0.6 | 0.6 | 0 | 7 | 0.001 | 82 |  | 98 | 0.006 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 2000 | 11 | 35.2 | 41.81 | 28.5 | 469.4 | 6.1 | 0.4 | 0.1 | 0.1 | 0 | 4 | 0.005 | 96 |  | 69 | 0.009 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 2000 | 11 | 162.7 | 27 | 29.9 | 465.8 | 60.1 | 1.9 | 2.5 | 0.3 | 68 | 18 | 0.003 | 60 |  | 119 | 0.01 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 2000 | 11 | 33.1 | 27 | 29.7 | 477 | 2.8 | 0.5 | 0.1 | 0 | 0 | 3 | 0.006 | 80 |  | 69 | 0.008 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 2000 | 11 | 34.6 | 17 | 32.4 | 591.5 | 0 | 0.8 | 1.1 | 0.3 | 0 | 6 | 0.002 | 88 |  | 57 | 0.008 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 2000 | 11 | 104 | 38 | 89 | 493 | 13 | 2 | 0 | 0 | 0 | 6 | 0.01 | 75 |  | 252.8 | 0.002 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 2000 | 11 | 116 | 32 | 94 | 575 | 18 | 2 | 1 | 1 | 0 | 11 | 0.01 | 75 |  | 225.3 | 0.002 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 2000 | 11 | 145.8 | 40 | 114.2 | 1537.9 | 10.3 | 2.3 | 2.6 | 0.7 | 15.7 | 7 | 0.01 | 75 |  | 43 | 0.012 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 2000 | 11 | 122.8 | 36 | 107.5 | 1414.8 | 12.3 | 1.8 | 0.7 | 0.5 | 0 | 6 | 0.004 | 88 |  | 38 | 0.009 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable. Corrosive IEC. Non-corrosive ASTM 3B.
33000 | 2000 | 11 | 116 | 43 | 99.3 | 1501.5 | 12.4 | 1.8 | 0.8 | 1.4 | 0.3 | 19 | 0.003 | 43 |  | 21 | 0.02 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 2000 | 11 | 107.9 | 36 | 91.7 | 1313.5 | 11.4 | 2.3 | 1.1 | 1.4 | 0 | 13 | 0 | 94 |  | 24 | 0.011 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 2000 | 11 | 108 | 38 | 78 | 340 | 29 | 1 | 0 | 0 | 0 | 8 | 0.01 | 75 |  | 223.9 | 0.003 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 2000 | 11 | 141 | 33 | 103 | 481 | 35 | 2 | 0 | 1 | 0 | 8 | 0.01 | 75 |  | 88.9 | 0.008 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 2000 | 11 | 229.7 | 42 | 200.2 | 1750 | 24.8 | 2.5 | 1.1 | 0.7 | 0.4 | 5 | 0.01 | 75 |  | 66 | 0.007 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 2000 | 11 | 15051.5 | 37 | 146.9 | 943.6 | 6948.9 | 349.2 | 389.1 | 26.9 | 7190.5 | 23 | 0.01 | 35 |  | 70 | 0.008 | DGA is assessed as acceptable. | Moisture is assessed as acceptable. Breakdown voltage is assessed as acceptable at present. Particle profile is assessed as acceptable. However, particle contamination load is high. ISO CODE: 22/18.
33000 | 2000 | 11 | 236.2 | 42 | 193.4 | 1670.1 | 38.4 | 2.4 | 1.3 | 0.5 | 0.2 | 4 | 0.003 | 86 |  | 48 | 0.008 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable. Corrosive IEC. Non-corrosive ASTM 3B.
33000 | 2000 | 11 | 225.1 | 45 | 181.3 | 1715.3 | 36.3 | 2 | 1.2 | 4.3 | 0 | 5 | 0.004 | 94 |  | 42 | 0.008 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 2000 | 11 | 190.3 | 38 | 159.2 | 1540.8 | 24.7 | 2.6 | 1.6 | 2.2 | 0 | 10 | 0 | 81 |  | 45 | 0.008 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 2000 | 11 | 127 | 44 | 113 | 1097 | 9 | 2 | 2 | 1 | 0 | 7 | 0.01 | 67 |  | 56 | 0.014 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 2000 | 11 | 107.9 | 38 | 76.6 | 1095 | 9.2 | 7.2 | 12.7 | 2.2 | 0 | 4 | 0.01 | 75 |  | 24 | 0.016 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 2000 | 11 | 120.1 | 39 | 79.3 | 1018.9 | 36.8 | 1.8 | 1.4 | 0.8 | 0 | 8 | 0.01 | 75 |  | 57 | 0.009 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 2000 | 11 | 175.9 | 42 | 150.3 | 1315.2 | 17.7 | 5.2 | 1.3 | 1.4 | 0 | 20 | 0.01 | 57 |  | 40 | 0.012 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable. Corrosive IEC. Corrosive ASTM 4A.
33000 | 2000 | 11 | 269.1 | 28 | 65.4 | 918.2 | 195.7 | 2.1 | 2.9 | 3 | 0 | 8 | 0.003 | 82.5 |  | 50 | 0.008 | DGA is assessed as acceptable at present. | Oil quality is assessed as acceptable.
33000 | 2000 | 11 | 110 | 32 | 55 | 875.4 | 49.6 | 2 | 2.3 | 1.1 | 0 | 8 | 0.004 | 92 |  | 47 | 0.008 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 2000 | 11 | 112 | 34 | 95 | 454 | 12 | 2 | 1 | 2 | 0 | 3 | 0.01 | 68 |  | 202.9 | 0.003 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 2000 | 11 | 187 | 57 | 160 | 1124 | 20 | 3 | 1 | 3 | 0 | 7 | 0.01 | 75 |  | 146.9 | 0.004 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 2000 | 11 | 160.8 | 42 | 143.6 | 1416.2 | 10.4 | 2.5 | 1.6 | 2.6 | 0.1 | 6 | 0.013 | 75 |  | 52 | 0.007 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 2000 | 11 | 249.2 | 52 | 226 | 2131.7 | 16.4 | 3.2 | 1.4 | 2.2 | 0 | 4 | 0.01 | 75 |  | 13 | 0.024 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 2000 | 11 | 200 | 38 | 181.9 | 1823 | 12.1 | 2.7 | 1.4 | 1.9 | 0 | 8 | 0.019 | 75 |  | 8 | 0.031 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable. Corrosive IEC. Corrosive ASTM 4A.
33000 | 2000 | 11 | 117.2 | 49 | 104.4 | 1575.1 | 7.7 | 2 | 1.5 | 1.6 | 0 | 6 | 0.012 | 75 |  | 9 | 0.026 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 2000 | 11 | 205.5 | 44 | 188.5 | 2023 | 12.5 | 2.3 | 1.1 | 1.1 | 0 | 8 | 0.015 | 98 |  | 7 | 0.037 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 2000 | 11 | 109.3 | 29 | 91.2 | 1384.9 | 13.2 | 1.6 | 2.1 | 1.2 | 0 | 5 | 0.012 | 81 |  | 10 | 0.022 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 2000 | 11 | 176.3 | 45 | 155.7 | 1118.6 | 15.4 | 3.5 | 0.7 | 1 | 0 | 5 | 0.01 | 75 |  | 38 | 0.019 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 2000 | 11 | 166.9 | 40 | 151.8 | 1411.2 | 10.7 | 2.6 | 1.2 | 0.5 | 0.1 | 4 | 0.01 | 75 |  | 6 | 0.043 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 2000 | 11 | 152.4 | 42 | 133.5 | 1510.4 | 10 | 2.7 | 1.4 | 0.9 | 3.9 | 4 | 0.01 | 75 |  | 42 | 0.012 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 2000 | 11 | 156.3 | 52 | 142.9 | 1581.3 | 8.6 | 2.5 | 1 | 1.3 | 0 | 4 | 0.002 | 94 |  | 38 | 0.013 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable. Corrosive IEC. Corrosive ASTM 4A.
33000 | 2000 | 11 | 97.7 | 41.81 | 81.6 | 1248.3 | 4.7 | 3.9 | 1.9 | 5.5 | 0.1 | 8 | 0.003 | 98 |  | 66 | 0.006 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 2000 | 11 | 58.7 | 41 | 48.2 | 921.8 | 4.8 | 2.3 | 1.7 | 1.7 | 0 | 5 | 0.003 | 98 |  | 67 | 0.006 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 2000 | 11 | 70.2 | 37 | 62.8 | 1066.9 | 5.3 | 1.5 | 0.6 | 0 | 0 | 5 | 0.003 | 61 |  | 31 | 0.013 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 2000 | 11 | 64.3 | 34 | 49.1 | 761.2 | 10.7 | 1.7 | 0.4 | 2.4 | 0 | 5 | 0.01 | 69 |  | 143 | 0.003 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 2000 | 11 | 54.2 | 37 | 47.4 | 713.2 | 3.5 | 1.5 | 0.4 | 1.4 | 0 | 2 | 0.01 | 75 |  | 119 | 0.005 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 2000 | 11 | 39.6 | 47 | 35.9 | 665.3 | 1.8 | 1.2 | 0.2 | 0.4 | 0.1 | 3 | 0.001 | 74 |  | 56 | 0.008 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 2000 | 11 | 50.6 | 38 | 42.8 | 734.8 | 5.5 | 1.4 | 0.5 | 0.3 | 0.1 | 4 | 0.002 | 78 |  | 54 | 0.008 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 2000 | 11 | 80 | 32 | 72 | 329 | 5 | 2 | 0 | 1 | 0 | 7 | 0.01 | 75 |  | 70.8 | 0.009 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 2000 | 11 | 102.4 | 46 | 90.5 | 866.8 | 7.8 | 2.2 | 0.6 | 1.3 | 0 | 4 | 0.01 | 75 |  | 52 | 0.011 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 2000 | 11 | 111.3 | 41.81 | 102.4 | 1119.5 | 5.7 | 2.2 | 0.5 | 0.5 | 0 | 2 | 0 | 70 |  | 82 | 0.007 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 2000 | 11 | 110.8 | 32 | 97.1 | 1219.4 | 8.7 | 2.1 | 1.1 | 1.8 | 0 | 5 | 0.002 | 96 |  | 21 | 0.014 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable. Corrosive IEC. Corrosive ASTM 4A.
33000 | 2000 | 11 | 70.7 | 33 | 67.2 | 949.5 | 0.6 | 1.8 | 0.7 | 0.4 | 0 | 4 | 0.002 | 82 |  | 28 | 0.027 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 2000 | 11 | 95.8 | 38 | 82.8 | 1137.5 | 8.2 | 2.2 | 1.1 | 1.4 | 0.1 | 7 | 0.005 | 81 |  | 53 | 0.008 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 2000 | 11 | 85.6 | 40 | 76.6 | 1061.8 | 5.6 | 1.8 | 0.8 | 0.7 | 0.1 | 10 | 0.003 | 58 |  | 32 | 0.011 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 2000 | 11 | 83 | 30 | 66 | 277 | 12 | 4 | 0 | 1 | 0 | 4 | 0.01 | 74 |  | 118.6 | 0.007 | 2-fufural is abnormal for new transformer. RECOMMEND RESAMPLE IN 6 MONTHS TO MONITOR 2 - FUFURAL.
33000 | 2000 | 11 | 86 | 48 | 67.9 | 871.4 | 13.6 | 1.7 | 0.9 | 1.9 | 0 | 11 | 0.01 | 30 |  | 39 | 0.013 | Dissolved gas analysis is assessed as acceptable. Oil quality is assessed as acceptable. Monitor breakdown voltage next routine sample.
33000 | 2000 | 11 | 85.2 | 47 | 68.3 | 1093.7 | 12.4 | 1.6 | 1.7 | 1.2 | 0 | 4 | 0.01 | 75 |  | 58 | 0.01 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 2000 | 11 | 77.8 | 36 | 65.4 | 1052.5 | 9.2 | 1.4 | 1 | 0.8 | 0 | 4 | 0.01 | 75 |  | 40 | 0.011 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 2000 | 11 | 57.8 | 72 | 47.4 | 1006.1 | 7.4 | 0.9 | 0.8 | 1.3 | 0 | 6 | 0.01 | 75 |  | 29 | 0.015 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 2000 | 11 | 82.7 | 48 | 67.1 | 1040.6 | 12.6 | 1.8 | 0.7 | 0.5 | 0 | 6 | 0.005 | 85 |  | 23 | 0.015 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 2000 | 11 | 68.2 | 46 | 57.1 | 942.8 | 8.7 | 1.8 | 0.6 | 0 | 0 | 6 | 0.003 | 70 |  | 50 | 0.007 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 2000 | 11 | 155 | 38 | 106 | 445 | 45 | 3 | 0 | 1 | 0 | 6 | 0.01 | 75 |  | 89.5 | 0.007 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 2000 | 11 | 444.9 | 45 | 347.7 | 1835.6 | 81.3 | 8.6 | 3.5 | 3.8 | 0 | 11 | 0.01 | 75 |  | 65 | 0.011 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 2000 | 11 | 1398.6 | 44 | 1192.1 | 5243.4 | 114.5 | 70.2 | 11.6 | 10.2 | 0 | 5 | 0.01 | 75 |  | 46 | 0.01389 | Significant increase in hydrocarbon gases and carbon oxides. | Oil quality is assessed as acceptable.
33000 | 2000 | 11 | 1559.4 | 41.81 | 1329.6 | 5694.6 | 126.3 | 73.9 | 14.5 | 15.1 | 0 | 7 | 0.01 | 61 |  | 119 | 0.009 | Dissolved gas levels are relatively stable. | Oil quality is assessed as acceptable.
33000 | 2000 | 11 | 1423 | 39 | 1213.2 | 5315.9 | 103.5 | 78.1 | 13.2 | 15 | 0 | 5 | 0.01 | 42 |  | 109 | 0.009 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable. Corrosive IEC. Corrosive ASTM 4A.
33000 | 2000 | 11 | 1512.5 | 37 | 1286.1 | 5822.5 | 131.4 | 68 | 12.4 | 14.6 | 0 | 8 | 0.004 | 46 |  | 166 | 0.006 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable. Corrosive IEC. Non-corrosive ASTM 3B.
33000 | 2000 | 11 | 1287 | 46 | 1084.2 | 5098 | 97.2 | 79 | 12.3 | 14.3 | 0 | 11 | 0.005 | 80 |  | 166 | 0.006 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable. Corrosive IEC. Corrosive ASTM 4A.
33000 | 2000 | 11 | 124.6 | 35 | 103.9 | 651.3 | 16.1 | 3.2 | 0.3 | 1.1 | 0 | 2 | 0.01 | 62 |  | 56 | 0.042 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 2000 | 11 | 146.5 | 35 | 127.5 | 990.9 | 7 | 3.2 | 5.5 | 3.1 | 0.2 | 3 | 0.01 | 71 |  | 24 | 0.043 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 2000 | 11 | 214.7 | 36 | 95.9 | 1011.8 | 42.3 | 13.6 | 2.9 | 60 | 0 | 8 | 0.016 | 75 |  | 8 | 0.061 | DGA is assessed as acceptable at present. | Oil quality is assessed as acceptable. Corrosive IEC. Corrosive ASTM 4B.
33000 | 2000 | 11 | 321.1 | 35 | 144.4 | 1406 | 107 | 10.1 | 2.5 | 57.1 | 0 | 2 | 0.017 | 87 |  | 10 | 0.033 | DGA is assessed as acceptable at present. | Oil quality is assessed as acceptable.
33000 | 2000 | 11 | 216.5 | 36 | 112.6 | 1263.4 | 78.2 | 5.1 | 1.8 | 18.8 | 0 | 5 | 0.028 | 87 |  | 15 | 0.016 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable. Corrosive IEC. Corrosive ASTM 4B.
33000 | 2000 | 11 | 385.6 | 51 | 283.5 | 4833.1 | 72.7 | 7.5 | 5 | 16.9 | 0 | 9 | 0.032 | 68 |  | 13 | 0.024 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 2000 | 11 | 145.4 | 32 | 93 | 1562.7 | 39.7 | 1.9 | 1.1 | 9.7 | 0 | 9 | 0.036 | 75 |  | 6 | 0.046 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 2000 | 11 | 153.2 | 31 | 108.4 | 1543 | 36.4 | 1.6 | 1.3 | 5.5 | 0 | 12 | 0.038 | 75 |  | 5 | 0.049 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1999 | 12 | 79 | 32 | 69 | 617 | 5 | 2 | 0 | 3 | 0 | 4 | 0.01 | 75 |  | 127.8 | 0.012 | DGA is assessed as acceptable | Oil quality is assessed as acceptable.
33000 | 1999 | 12 | 64.7 | 38 | 52.1 | 983.5 | 8.6 | 1.3 | 0.4 | 2.3 | 0 | 4 | 0.01 | 75 |  | 167.6 | 0.009 | Dissolved gas analysis is assessed as acceptable. Oil quality is assessed as acceptable.
33000 | 1999 | 12 | 70.8 | 38 | 61 | 1110.6 | 4 | 4.5 | 0 | 1.3 | 0 | 3 | 0.01 | 75 |  | 105 | 0.015 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1999 | 12 | 76.9 | 28 | 64.7 | 1005.8 | 8.6 | 1.4 | 0.3 | 1.9 | 0 | 3 | 0.01 | 75 |  | 67 | 0.014 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1999 | 12 | 117.9 | 40 | 101.5 | 983.8 | 10.2 | 4.6 | 0.3 | 1.3 | 0 | 5 | 0.01 | 75 |  | 144 | 0.006 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable. Corrosive IEC. Corrosive ASTM 4A.
33000 | 1999 | 12 | 58.8 | 40 | 51.6 | 973.2 | 4.2 | 1.3 | 0.4 | 1 | 0.3 | 9 | 0.005 | 58 |  | 105 | 0.008 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1999 | 12 | 50 | 30 | 42.2 | 1022.2 | 4.8 | 1.1 | 1.2 | 0.7 | 0 | 25 | 0.006 | 75 |  | 101 | 0.007 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1999 | 12 | 55 | 33 | 46 | 268 | 6 | 1 | 0 | 2 | 0 | 5 | 0.01 | 75 |  | 87.4 | 0.016 | DGA is assessed as acceptable | Oil quality is assessed as acceptable.
33000 | 1999 | 12 | 65.2 | 42 | 52.9 | 823.6 | 8.5 | 1.2 | 0.2 | 2.4 | 0 | 2 | 0.01 | 55 |  | 153.3 | 0.009 | Dissolved gas analysis is assessed as acceptable. Oil quality is assessed as acceptable.
33000 | 1999 | 12 | 68.5 | 47 | 59.2 | 941.6 | 4.1 | 4.3 | 0 | 0.9 | 0 | 4 | 0.01 | 57 |  | 83 | 0.013 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1999 | 12 | 111.8 | 25 | 64.3 | 921.5 | 44.5 | 1.3 | 0.3 | 1.2 | 0.2 | 3 | 0.01 | 75 |  | 78 | 0.00969 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1999 | 12 | 76.6 | 38 | 67.1 | 917.1 | 8.1 | 0.3 | 0.2 | 0.7 | 0.2 | 6 | 0.01 | 56 |  | 49 | 0.015 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable. Corrosive IEC. Corrosive ASTM 4A.
33000 | 1999 | 12 | 48.5 | 40 | 45.2 | 805.5 | 1.7 | 1.1 | 0.2 | 0.3 | 0 | 4 | 0 | 75 |  | 148 | 0.006 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1999 | 12 | 52 | 24 | 43.5 | 823.4 | 6.4 | 1.1 | 0.5 | 0.3 | 0.2 | 3 | 0.004 | 80 |  | 144 | 0.004 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1999 | 12 | 46.9 | 30 | 37.9 | 779.6 | 7.1 | 0.9 | 0.8 | 0.2 | 0 | 8 | 0.006 | 90 |  | 164 | 0.004 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1999 | 12 | 383 | 52 | 111 | 635 | 17 | 83 | 127 | 33 | 12 | 3 | 0.014 | 68 |  | 59.1 | 0.015 | Dissolved gas analysis suggest hot spot in oil; possibly connection/contact. | Oil quality is assessed as acceptable.
33000 | 1999 | 12 | 308 | 42 | 49 | 364 | 37 | 91 | 104 | 26 | 1 | 7 | 0.01 | 75 |  | 121.6 | 0.007 | Dissolved gas analysis suggests hot spot in oil. | Oil quality results are assessed as acceptable.
33000 | 1999 | 12 | 322.9 | 62 | 278 | 2164.9 | 33.1 | 4 | 3.2 | 4.4 | 0.2 | 6 | 0.01 | 75 |  | 64 | 0.006 | Dissolved gas analysis is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1999 | 12 | 141.8 | 54 | 121.7 | 1310.7 | 12.4 | 2 | 2.4 | 3.2 | 0.1 | 10 | 0.01 | 75 |  | 49.9 | 0.01 | Dissolved gas analysis is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1999 | 12 | 227.8 | 68 | 198.6 | 1888.9 | 20.8 | 3.2 | 2.2 | 2.9 | 0.1 | 10 | 0.01 | 47 |  | 47 | 0.008 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1999 | 12 | 164 | 48 | 144.8 | 1530.2 | 13.7 | 2.1 | 1.6 | 1.8 | 0 | 5 | 0.01 | 75 |  | 20 | 0.017 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1999 | 12 | 192.7 | 55 | 149.4 | 1570.1 | 34 | 3.5 | 1.7 | 4.1 | 0 | 8 | 0.01 | 75 |  | 21 | 0.014 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1999 | 12 | 192 | 53 | 169.1 | 1718.9 | 16.7 | 2.5 | 1.9 | 1.8 | 0 | 7 | 0.009 | 88 |  | 15 | 0.02 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable. Corrosive IEC. Corrosive ASTM 4A.
33000 | 1999 | 12 | 176.1 | 52 | 142.1 | 1717.5 | 13 | 5.7 | 2.8 | 12.5 | 0 | 10 | 0.006 | 52 |  | 15 | 0.017 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1999 | 12 | 63 | 34 | 45 | 425 | 16 | 1 | 0 | 1 | 0 | 4 | 0.01 | 75 |  | 163.3 | 0.006 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1999 | 12 | 169.6 | 39 | 112.4 | 1008.7 | 36 | 4.8 | 0.9 | 15.5 | 0 | 6 | 0.01 | 75 |  | 103 | 0.007 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1999 | 12 | 53.5 | 32 | 43 | 987.2 | 7.1 | 1.4 | 0.5 | 0.6 | 0.9 | 5 | 0.01 | 72 |  | 185 | 0.005 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1999 | 12 | 77.5 | 46 | 49.8 | 715.9 | 20.2 | 1.6 | 1.1 | 1.2 | 3.6 | 3 | 0.01 | 75 |  | 102 | 0.006 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1999 | 12 | 41.6 | 41.81 | 35.3 | 675.9 | 4.5 | 1.2 | 0.2 | 0.4 | 0 | 2 | 0.01 | 75 |  | 103 | 0.008 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1999 | 12 | 29.3 | 41.81 | 23.2 | 488.2 | 4 | 1 | 0.3 | 0.2 | 0.6 | 9 | 0.01 | 75 |  | 83 | 0.01 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1999 | 12 | 40.1 | 42 | 33.3 | 677.3 | 5 | 1.2 | 0.3 | 0.3 | 0 | 3 | 0.01 | 75 |  | 237 | 0.004 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1999 | 12 | 44.8 | 41.81 | 35.5 | 627.9 | 7.1 | 1.2 | 0.2 | 0.8 | 0 | 2 | 0.01 | 75 |  | 185 | 0.004 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1999 | 12 | 17.3 | 40 | 16.4 | 529.7 | 0 | 0.7 | 0.2 | 0 | 0 | 15 | 0.01 | 70 |  | 156 | 0.006 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1999 | 12 | 42.7 | 31 | 37.2 | 605.6 | 4.4 | 0.9 | 0.2 | 0 | 0 | 4 | 0.009 | 84 |  | 179 | 0.004 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable. Corrosive IEC. Corrosive ASTM 4A.
33000 | 1999 | 12 | 33 | 30 | 27.8 | 682.8 | 3.2 | 1.1 | 0.3 | 0.6 | 0 | 7 | 0.003 | 89 |  | 42 | 0.017 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1999 | 12 | 118 | 33 | 37 | 367 | 72 | 6 | 1 | 2 | 0 | 7 | 0.01 | 75 |  | 76.1 | 0.011 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1999 | 12 | 146 | 35 | 62 | 490 | 74 | 5 | 1 | 4 | 0 | 5 | 0.01 | 75 |  | 78.2 | 0.015 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1999 | 12 | 98.5 | 26 | 68.4 | 762.1 | 25.3 | 2.3 | 0.7 | 1.7 | 0.1 | 3 | 0.01 | 53 |  | 30 | 0.038 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1999 | 12 | 117.9 | 30 | 81.6 | 887.6 | 32 | 2.2 | 0.5 | 1.5 | 0.1 | 12 | 0.01 | 44 |  | 39 | 0.019 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1999 | 12 | 101.6 | 28 | 70.3 | 904.2 | 21.5 | 3.4 | 0.9 | 5.5 | 0 | 7 | 0.01 | 75 |  | 35 | 0.02 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1999 | 12 | 113.7 | 28 | 73.8 | 796.7 | 12.3 | 6.6 | 2.2 | 18.8 | 0 | 5 | 0.01 | 75 |  | 204 | 0.003 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1999 | 12 | 100.8 | 37 | 70.3 | 907.5 | 24.5 | 4.1 | 0.5 | 1.2 | 0.2 | 5 | 0.01 | 75 |  | 65 | 0.008 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable. Corrosive IEC. Corrosive ASTM 4A.
33000 | 1999 | 12 | 99 | 41.81 | 72.5 | 967.7 | 24.2 | 1.7 | 0.2 | 0.4 | 0 | 4 | 0.007 | 49 |  | 79 | 0.009 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1999 | 12 | 64.7 | 44 | 51.3 | 830.9 | 11.3 | 1.6 | 0.2 | 0.3 | 0 | 6 | 0.005 | 72 |  | 34 | 0.021 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1999 | 12 | 120.4 | 35 | 92.1 | 950.9 | 19 | 8.8 | 0.3 | 0.2 | 0 | 6 | 0.003 | 83 |  | 70 | 0.009 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1999 | 12 | 203 | 44 | 171 | 822 | 19 | 6 | 0 | 7 | 0 | 7 | 0.01 | 74 |  | 171.2 | 0.012 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1999 | 12 | 867.4 | 70 | 501.5 | 2848.7 | 307.5 | 23.8 | 4.2 | 30.2 | 0.2 | 8 | 0.019 | 75 |  | 18 | 0.019 | DGA is assessed as acceptable at present. | Oil quality is assessed as acceptable.
33000 | 1999 | 12 | 632.1 | 70 | 451 | 3490.2 | 159.9 | 7.8 | 2.7 | 10.7 | 0 | 16 | 0.034 | 75 |  | 5 | 0.052 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1999 | 12 | 404 | 49 | 318.1 | 3295 | 68.7 | 4.7 | 2.8 | 6 | 3.7 | 14 | 0.041 | 75 |  | 7 | 0.046 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1999 | 12 | 159.1 | 36 | 135.9 | 2432.1 | 14.3 | 2.9 | 2.4 | 3 | 0.6 | 10 | 0.04 | 75 |  | 5 | 0.051 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1999 | 12 | 150.6 | 67 | 124.1 | 1601.9 | 20.3 | 2.2 | 1 | 2.6 | 0.4 | 8 | 0.053 | 83 |  | 4 | 0.051 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1999 | 12 | 101.4 | 50 | 81.1 | 1360.7 | 17.1 | 1.7 | 0.8 | 0.6 | 0.1 | 10 | 0.043 | 85 |  | 3 | 0.092 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1999 | 12 | 100.1 | 58 | 87.2 | 1384.2 | 9.5 | 1.6 | 0.8 | 0.8 | 0.2 | 9 | 0.044 | 83 |  | 9 | 0.035 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1999 | 12 | 71 | 44 | 64 | 422 | 3 | 2 | 0 | 2 | 0 | 2 | 0.012 | 75 |  | 439.2 | 0.003 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1999 | 12 | 107 | 40 | 88.5 | 898.1 | 13 | 2 | 0.4 | 2.9 | 0.2 | 5 | 0.01 | 75 |  | 128 | 0.011 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1999 | 12 | 118 | 43 | 102.5 | 1110.1 | 9.3 | 2.2 | 0.9 | 2.9 | 0.2 | 3 | 0.01 | 52 |  | 127 | 0.007 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1999 | 12 | 160.1 | 50 | 143.2 | 1443 | 11.4 | 2.4 | 0.5 | 2.6 | 0 | 1 | 0.01 | 75 |  | 132 | 0.005 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1999 | 12 | 302.3 | 51 | 202.3 | 1909.7 | 86 | 4.5 | 2 | 6.9 | 0.6 | 8 | 0.015 | 75 |  | 21 | 0.012 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable. Corrosive IEC. Corrosive ASTM 4A.
33000 | 1999 | 12 | 350.7 | 77 | 247.4 | 2704.2 | 94.6 | 2.9 | 2.2 | 3.6 | 0 | 7 | 0.032 | 75 |  | 10 | 0.026 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable. Corrosive IEC. Corrosive ASTM 4A.
33000 | 1999 | 12 | 137.6 | 45 | 116.4 | 1759 | 16.9 | 2 | 1.4 | 0.9 | 0 | 6 | 0.034 | 91 |  | 4 | 0.055 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1999 | 12 | 59 | 42 | 54 | 398 | 3 | 1 | 0 | 1 | 0 | 7 | 0.01 | 75 |  | 60.6 | 0.013 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1999 | 12 | 82.2 | 37 | 71.4 | 1036.4 | 6.7 | 1.6 | 0.2 | 2.3 | 0 | 8 | 0.01 | 75 |  | 79 | 0.013 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1999 | 12 | 75.9 | 42 | 67 | 1172 | 5.3 | 1.5 | 0.5 | 1.6 | 0 | 6 | 0.01 | 75 |  | 83 | 0.01 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1999 | 12 | 51 | 60 | 38.9 | 677.2 | 8.1 | 1.2 | 0.7 | 1.4 | 0.7 | 5 | 0.003 | 82 |  | 96 | 0.008 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1999 | 12 | 43.2 | 34 | 30.3 | 699.4 | 8.9 | 2 | 0.5 | 1.1 | 0.4 | 6 | 0.004 | 79 |  | 123 | 0.007 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1999 | 12 | 68 | 46 | 57 | 530 | 9 | 1 | 0 | 1 | 0 | 29 | 0.01 | 75 |  | 68.6 | 0.015 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1999 | 12 | 77 | 32 | 69 | 858 | 3 | 3 | 0 | 2 | 0 | 5 | 0.01 | 65 |  | 43 | 0.014 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1999 | 12 | 75 | 43 | 49.9 | 1143.6 | 16.1 | 3 | 0 | 6 | 0 | 5 | 0.01 | 74 |  | 63 | 0.016 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1999 | 12 | 62.1 | 43 | 51.5 | 914.7 | 7.4 | 1.5 | 0.4 | 0.9 | 0.4 | 10 | 0.01 | 63 |  | 82 | 0.008 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1999 | 12 | 25.5 | 41.81 | 22.1 | 170.3 | 3.4 | 0 | 0 | 0 | 0 | 8 | 0.01 | 75 |  | 48 | 0.014 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1999 | 12 | 10.5 | 19 | 6.5 | 182.6 | 2.6 | 0.8 | 0.2 | 0.4 | 0 | 3 | 0.01 | 75 |  | 49 | 0.013 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1999 | 12 | 117.3 | 24 | 71.3 | 1048.9 | 34.6 | 3.3 | 1.5 | 6.6 | 0 | 34 | 0.01 | 34 |  | 24 | 0.016 | DGA is assessed as acceptable. | Breakdown voltage is low. Other oil quality results are assessed as acceptable.
33000 | 1999 | 12 | 47.6 | 24 | 16.8 | 216.5 | 26.9 | 0.5 | 1.5 | 1.9 | 0 | 19 | 0.01 | 53 |  | 22 | 0.019 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1999 | 12 | 98.8 | 29 | 28 | 231.3 | 58.6 | 2 | 5.3 | 2.4 | 2.5 | 23 | 0.006 | 42 |  | 21 | 0.018 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1999 | 12 | 30.1 | 29 | 15.8 | 267.9 | 11.6 | 0.8 | 0.2 | 1.7 | 0 | 8 | 0.005 | 86 |  | 36 | 0.011 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1999 | 12 | 67.2 | 46 | 46.7 | 717.4 | 19.1 | 1 | 0.2 | 0.2 | 0 | 5 | 0.007 | 92 |  | 25 | 0.017 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable. Corrosive IEC. Corrosive ASTM 4A.
33000 | 1999 | 12 | 56.5 | 32 | 41.3 | 752.8 | 13.5 | 1.2 | 0.2 | 0.3 | 0 | 9 | 0.002 | 88 |  | 32 | 0.011 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1999 | 12 | 50 | 36 | 44 | 563 | 0 | 2 | 2 | 2 | 0 | 4 | 0.01 | 74 |  | 112.5 | 0.016 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1999 | 12 | 255.4 | 40 | 197.1 | 1795.1 | 36.7 | 9.1 | 1.2 | 11.2 | 0.1 | 4 | 0.01 | 75 |  | 53 | 0.01 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1999 | 12 | 344.8 | 36 | 182.4 | 1387 | 130.2 | 9.1 | 1.7 | 21.4 | 0 | 4 | 0.012 | 75 |  | 27 | 0.013 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1999 | 12 | 198.8 | 34 | 125.5 | 1516.8 | 64.6 | 2.3 | 1.3 | 5.1 | 0 | 8 | 0.025 | 75 |  | 8 | 0.035 | DGA is assessed as acceptable. | Resistivity is low. Other oil quality results are assessed as acceptable.
33000 | 1999 | 12 | 141 | 37 | 105 | 1329 | 32 | 2 | 1 | 1 | 0 | 6 | 0.031 | 75 |  | 22 | 0.015 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable. Corrosive IEC. Corrosive ASTM 4B.
33000 | 1999 | 12 | 101.5 | 35 | 83.7 | 1262.1 | 15.2 | 1.4 | 0.5 | 0.7 | 0 | 7 | 0.03 | 85 |  | 7 | 0.035 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable. Corrosive IEC. Corrosive ASTM 3B.
33000 | 1999 | 12 | 80.3 | 30 | 63.6 | 1060.6 | 13.6 | 1.2 | 1.5 | 0.4 | 0 | 9 | 0.033 | 93 |  | 6 | 0.044 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1998 | 13 | 170 | 41.81 | 19 | 259 | 148 | 2 | 1 | 0 | 0 | 4 | 0.01 | 75 |  | 102.2 | 0.006 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1998 | 13 | 469.5 | 48 | 405.1 | 1408.7 | 53.7 | 6.4 | 2.6 | 1.7 | 0 | 8 | 0.01 | 75 |  | 37 | 0.017 | The test results are assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1998 | 13 | 618.7 | 26 | 546 | 1671.7 | 61.6 | 8.2 | 1.5 | 1.4 | 0 | 4 | 0.01 | 75 |  | 25 | 0.026 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1998 | 13 | 782.7 | 16 | 711.1 | 2155.9 | 57.9 | 10.7 | 1.5 | 1.5 | 0 | 4 | 0.01 | 75 |  | 43 | 0.014 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable. Corrosive IEC. Corrosive ASTM 4A.
33000 | 1998 | 13 | 578.2 | 13 | 510.5 | 2164.4 | 55.5 | 8.8 | 1.8 | 1.6 | 0 | 3 | 0.005 | 79 |  | 35 | 0.015 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1998 | 13 | 412.5 | 32 | 355.8 | 1887 | 47.4 | 8.2 | 1.1 | 0 | 0 | 9 | 0.002 | 84 |  | 30 | 0.019 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1998 | 13 | 470.8 | 20 | 399.7 | 2012.5 | 60.5 | 7.6 | 1.7 | 1.3 | 0 | 11 | 0.005 | 80 |  | 41 | 0.016 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1997 | 14 | 42 | 25 | 24 | 163 | 17 | 1 | 0 | 0 | 0 | 4 | 0.01 | 56 |  | 137.1 | 0.003 | Traces of hydrocarbon gases. | Oil quality is assessed as acceptable.
33000 | 1997 | 14 | 51 | 41.81 | 41 | 470 | 6 | 1 | 2 | 1 | 0 | 17 | 0.01 | 60 |  | 77.5 | 0.005 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1997 | 14 | 182.9273 | 45 | 135.8604 | 1423.5416 | 37.6452 | 2.6595 | 2.55 | 3.9875 | 0.2247 | 4 | 0.013 | 75 |  | 18 | 0.015 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1997 | 14 | 229.6 | 50 | 196.5 | 1912.5 | 24.3 | 2.8 | 3.3 | 2.6 | 0.1 | 13 | 0.036 | 75 |  | 4 | 0.049 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1997 | 14 | 221.2 | 49 | 184.9 | 1816 | 28.9 | 2 | 2.7 | 0.4 | 2.3 | 7 | 0.066 | 75 |  | 5 | 0.03694 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1997 | 14 | 230.3 | 50 | 207.2 | 2056 | 14.6 | 3.4 | 3.3 | 1.8 | 0 | 11 | 0.064 | 75 |  | 4 | 0.051 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1997 | 14 | 316.6 | 38 | 292.5 | 2559.9 | 14.6 | 3.2 | 4.3 | 1.8 | 0.2 | 8 | 0.07 | 73 |  | 4 | 0.054 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable. Corrosive IEC. Corrosive ASTM 4B.
33000 | 1997 | 14 | 249.8 | 55 | 225.6 | 2182.7 | 17.3 | 3 | 3.2 | 0.7 | 0 | 13 | 0.083 | 82 |  | 3 | 0.056 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1997 | 14 | 303.5 | 41 | 273 | 2285 | 23 | 2.5 | 4 | 1 | 0 | 18 | 0.087 | 81 |  | 3 | 0.063 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1997 | 14 | 153.2 | 42 | 140.2 | 1566.1 | 8.4 | 1.8 | 1.9 | 0.9 | 0 | 8 | 0.088 | 98 |  | 4 | 0.055 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1997 | 14 | 37 | 25 | 12 | 107 | 20 | 2 | 0 | 3 | 0 | 8 | 0.01 | 58 |  | 29.6 | 0.017 | Traces of hydrocarbon gases. | Oil quality is assessed as acceptable.
33000 | 1997 | 14 | 71 | 48 | 51 | 493 | 12 | 2 | 1 | 5 | 0 | 21 | 0.01 | 31 |  | 86.6 | 0.005 | DGA is assessed as acceptable. | Dielectric strength of oil is slightly low. Other test results are assessed as acceptable.
33000 | 1997 | 14 | 437.4414 | 45 | 283.3946 | 2949.1237 | 132.0676 | 4.1929 | 4.5641 | 13.2222 | 0 | 7 | 0.047 | 75 |  | 8 | 0.027 | The test results are assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1997 | 14 | 270.8 | 50 | 229 | 2748.9 | 28.1 | 7.8 | 2.3 | 3.6 | 0 | 11 | 0.073 | 71 |  | 5 | 0.037 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1997 | 14 | 301.1 | 51 | 264.2 | 2223.6 | 22.9 | 3.7 | 3.9 | 1.3 | 5.1 | 10 | 0.081 | 75 |  | 5 | 0.04 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1997 | 14 | 248.3 | 56 | 229.2 | 2508 | 13.2 | 2.6 | 2.5 | 0.8 | 0 | 17 | 0.11 | 75 |  | 5 | 0.042 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1997 | 14 | 240.5 | 49 | 221.8 | 2688.6 | 12.9 | 2.6 | 2.2 | 1 | 0 | 15 | 0.131 | 40 |  | 4 | 0.056 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable. Corrosive IEC. Corrosive ASTM 4A.
33000 | 1997 | 14 | 148.7 | 59 | 134.7 | 2294.1 | 9.2 | 1.8 | 2.2 | 0.8 | 0 | 9 | 0.128 | 88 |  | 4 | 0.051 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1997 | 14 | 164.8 | 29 | 149.1 | 2051.3 | 8.3 | 3.2 | 1.7 | 2 | 0.5 | 12 | 0.134 | 88 |  | 2 | 0.078 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1997 | 14 | 146 | 44 | 84 | 974 | 50 | 2 | 9 | 1 | 0 | 3 | 0.01 | 75 |  | 159.8 | 0.003 | Test results are assessed as acceptable.
33000 | 1997 | 14 | 483.6 | 47 | 381.3 | 2964.5 | 47.6 | 3.4 | 49.3 | 0.8 | 1.2 | 10 | 0.01 | 75 |  | 42 | 0.01 | The test results are assessed as acceptable at present. | Oil quality is assessed as acceptable.
33000 | 1997 | 14 | 215.7 | 38 | 170.8 | 1666.2 | 8.4 | 1.6 | 33.4 | 0.5 | 1 | 11 | 0.01 | 75 |  | 37 | 0.013 | Dissolved gas analysis is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1997 | 14 | 217.6 | 40 | 154 | 1470.3 | 25.2 | 1.7 | 34.7 | 0.6 | 1.4 | 7 | 0.01 | 67 |  | 36 | 0.011 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1997 | 14 | 156.2 | 35 | 114.2 | 1109.5 | 15.3 | 1.2 | 24.5 | 0 | 1 | 5 | 0.012 | 75 |  | 33 | 0.011 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1997 | 14 | 183.4 | 38 | 130.5 | 1130.5 | 22 | 1.3 | 27.5 | 0.1 | 2 | 5 | 0.015 | 77 |  | 31 | 0.013 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable. Corrosive IEC. Corrosive ASTM 4A.
33000 | 1997 | 14 | 272.6 | 32 | 222.1 | 1420.7 | 13.7 | 1.5 | 33.5 | 0.5 | 1.3 | 8 | 0.019 | 76 |  | 21 | 0.02 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1997 | 14 | 160.2 | 35 | 115.9 | 1201.3 | 13 | 2.2 | 27.5 | 0.2 | 1.4 | 7 | 0.018 | 85 |  | 21 | 0.018 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1997 | 14 | 180 | 36 | 130.7 | 1280.3 | 15.8 | 1.5 | 30.1 | 0 | 1.9 | 11 | 0.017 | 87 |  | 15 | 0.02 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1996 | 15 | 141 | 47 | 88 | 449 | 51 | 1 | 1 | 0 | 0 | 6 | 0.01 | 63 |  | 95.9 | 0.005 | Dissolved gas analysis appears to be normal after buchholz trip. | Oil quality is assessed as acceptable.
33000 | 1996 | 15 | 200 | 48 | 137 | 751 | 57 | 1 | 5 | 0 | 0 | 6 | 0.01 | 68 |  | 80.1 | 0.005 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1996 | 15 | 294.8 | 42 | 219 | 1751.8 | 40.1 | 1 | 30.6 | 0.2 | 3.9 | 3 | 0.01 | 75 |  | 51 | 0.01 | The test results are assessed as acceptable. Acetylene gas possibly from tapchanger. | Oil quality is assessed as acceptable.
33000 | 1996 | 15 | 494.1 | 65 | 386.8 | 2094.7 | 60.2 | 2.8 | 42.7 | 0 | 1.6 | 6 | 0.01 | 75 |  | 43 | 0.009 | The test results are assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1996 | 15 | 213.1 | 42 | 161.2 | 949.9 | 24.6 | 1.4 | 23.6 | 0.7 | 1.6 | 6 | 0.01 | 75 |  | 38.9 | 0.01 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1996 | 15 | 173.4 | 44 | 142 | 907.1 | 11 | 1.2 | 17.9 | 0 | 1.3 | 9 | 0.017 | 32 |  | 16 | 0.023 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable at present.
33000 | 1996 | 15 | 230 | 42 | 182.4 | 1035.1 | 17.4 | 1 | 27.6 | 0 | 1.6 | 7 | 0.018 | 74 |  | 21 | 0.02 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable. Non-corrosive IEC. Non-corrosive ASTM 3B.
33000 | 1996 | 15 | 319.4 | 41.81 | 265.5 | 1422.7 | 13.8 | 2.7 | 36.1 | 1 | 0.3 | 9 | 0.017 | 92 |  | 16 | 0.022 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1996 | 15 | 166.9 | 40 | 129.3 | 954.9 | 11.4 | 2.2 | 22.8 | 0.3 | 0.9 | 5 | 0.023 | 88 |  | 16 | 0.02 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1996 | 15 | 158.4 | 31 | 122.9 | 948.3 | 10 | 1.4 | 23.1 | 0 | 1 | 7 | 0.021 | 80 |  | 19 | 0.017 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1996 | 15 | 150 | 41.81 | 91 | 634 | 50 | 1 | 6 | 1 | 1 | 8 | 0.01 | 59 |  | 147.5 | 0.004 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1996 | 15 | 352.2 | 56 | 280.8 | 1443.9 | 29 | 2.3 | 38.5 | 0.5 | 1.1 | 5 | 0.01 | 75 |  | 39 | 0.009 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1996 | 15 | 315.8 | 35 | 237.6 | 1532.6 | 33.5 | 2.8 | 40.7 | 0.4 | 0.8 | 6 | 0.01 | 75 |  | 39 | 0.009 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1996 | 15 | 135.5 | 32 | 109 | 766.8 | 5.9 | 1.1 | 16.8 | 0.3 | 2.4 | 8 | 0.01 | 56 |  | 29 | 0.014 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1996 | 15 | 130.7 | 30 | 99.9 | 741.5 | 10.6 | 1.3 | 14.9 | 0 | 4 | 7 | 0.012 | 69 |  | 23 | 0.01555 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1996 | 15 | 104.6 | 26 | 87.1 | 612.6 | 3.6 | 0.9 | 12.1 | 0 | 0.9 | 6 | 0.023 | 75 |  | 23 | 0.014 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1996 | 15 | 96.2 | 26 | 85.6 | 619.8 | 0 | 0.9 | 9.7 | 0 | 0 | 5 | 0.012 | 74 |  | 22 | 0.014 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable. Corrosive IEC. Non-corrosive ASTM 3B.
33000 | 1996 | 15 | 127.3 | 24 | 99 | 784.8 | 9.3 | 1 | 17.5 | 0 | 0.5 | 3 | 0.025 | 94 |  | 22 | 0.014 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable. Non-corrosive IEC. Non-corrosive ASTM 3B.
33000 | 1995 | 16 | 93 | 41.81 | 89 | 1125 | 0 | 2 | 1 | 1 | 0 | 6 | 0.01 | 73 |  | 99.2 | 0.023 | Test results are assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1995 | 16 | 15005 | 40 | 34 | 649 | 2287 | 535 | 1108 | 53 | 10988 | 8 | 0.01 | 65 |  | 282.2 | 0.003 | DGA appears typical for a tapchanger. | Oil quality is assessed as acceptable.
33000 | 1995 | 16 | 454.9 | 62 | 423.4 | 4514.7 | 17.1 | 2.9 | 5.8 | 5.4 | 0.3 | 8 | 0.032 | 75 |  | 4 | 0.092 | 2-furfural level is high for transformer age suggesting accelerated rate of insulation degradation. | Other test results are assessed as acceptable.
33000 | 1995 | 16 | 557.5 | 60 | 522.7 | 4071 | 20 | 5.4 | 5.5 | 3.8 | 0.1 | 16 | 0.04 | 56 |  | 3 | 0.117 | The test results are consistent with main tank sample and are assessed as acceptable.
33000 | 1995 | 16 | 619.9 | 60 | 581 | 4225.9 | 25 | 5.6 | 4.8 | 3.4 | 0.1 | 20 | 0.039 | 26 |  | 7.5267 | 0.040513 |  | Breakdown voltage of sample is slightly low. Possible sample contamination. Other test results are assessed as acceptable.
33000 | 1995 | 16 | 401 | 64 | 380.8 | 3311.1 | 12.7 | 1.2 | 3.6 | 2.7 | 0 | 12 | 0.044 | 75 |  | 7 | 0.045 | 2-furfural level is high and trending upwards suggesting advanced state of insulation degradation. Other test results are assessed as acceptable.
33000 | 1995 | 16 | 151.6 | 40 | 143 | 1848 | 5 | 2 | 1 | 0.6 | 0 | 8 | 0.047 | 75 |  | 7 | 0.036 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1995 | 16 | 218.9 | 57 | 208.9 | 2141.5 | 5.7 | 2.3 | 1.4 | 0.6 | 0 | 7 | 0.052 | 71 |  | 5 | 0.058 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1995 | 16 | 50.9 | 22 | 48.7 | 1021 | 0 | 1.1 | 0.6 | 0.5 | 0 | 5 | 0.063 | 64 |  | 5 | 0.059 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1995 | 16 | 50.4 | 21 | 48.7 | 795.8 | 0.2 | 1 | 0.3 | 0.2 | 0 | 5 | 0.06 | 75 |  | 5 | 0.052 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1995 | 16 | 51.3 | 24 | 43.4 | 778.5 | 0 | 1.5 | 1.4 | 5 | 0 | 4 | 0.058 | 79 |  | 8 | 0.032 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1995 | 16 | 34 | 41.81 | 4 | 103 | 30 | 0 | 0 | 0 | 0 | 4 | 0.01 | 64 |  | 424.3 | 0.003 | Test results satisfactory. RECOMMEND RESAMPLE IN 6 MONTHS TO MONITOR INITIAL PERIOD.
33000 | 1995 | 16 | 217.4 | 33 | 123.4 | 1126 | 83.1 | 3.5 | 2.8 | 4.5 | 0.1 | 3 | 0.01 | 75 |  | 47 | 0.014 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1995 | 16 | 46.3 | 30 | 40.3 | 889.2 | 3 | 0.5 | 0.9 | 1.4 | 0.2 | 4 | 0.01 | 75 |  | 97 | 0.006 | Dissolved gas levels are reduced. The test results are assessed as acceptable.
33000 | 1995 | 16 | 130.1 | 37 | 120.5 | 1172.6 | 5.5 | 1.6 | 1.7 | 0.7 | 0.1 | 5 | 0.024 | 66 |  | 28 | 0.013 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1995 | 16 | 205.9 | 48 | 193.6 | 1613.5 | 8.5 | 1.9 | 1.5 | 0.4 | 0 | 4 | 0.019 | 75 |  | 8 | 0.03988 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1995 | 16 | 200.9 | 60 | 188.6 | 1484.4 | 8 | 1.9 | 1.5 | 0.9 | 0 | 7 | 0.026 | 74 |  | 10 | 0.029 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable. Corrosive IEC. Corrosive ASTM 4A.
33000 | 1995 | 16 | 220.6 | 51 | 208.8 | 1706 | 8.7 | 1.7 | 1.2 | 0.2 | 0 | 8 | 0.035 | 86 |  | 6 | 0.048 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1995 | 16 | 110 | 34 | 99.4 | 1151.1 | 7.1 | 1.2 | 1.9 | 0.4 | 0 | 7 | 0.035 | 80 |  | 7 | 0.039 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1995 | 16 | 87 | 63 | 86 | 473 | 0 | 1 | 0 | 0 | 0 | 12 | 0.01 | 48 |  | 94.7 | 0.007 | Dissolved gas analysis is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1995 | 16 | 300 | 52 | 219 | 1648 | 47 | 2 | 32 | 0 | 0 | 6 | 0.01 | 68 |  | 13.5 | 0.017 | Test results are assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1995 | 16 | 319 | 52 | 241.5 | 2184.9 | 14.6 | 1.2 | 58.9 | 0.6 | 2.2 | 6 | 0.013 | 75 |  | 25 | 0.014 | Dissolved gas analysis is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1995 | 16 | 575.9 | 61 | 406.5 | 2700.2 | 75.4 | 3.2 | 88.5 | 0.7 | 1.6 | 10 | 0.019 | 75 |  | 23 | 0.014 | Dissolved gas analysis is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1995 | 16 | 317.4 | 37 | 245.4 | 1889 | 0 | 2.2 | 68.6 | 0 | 1.2 | 9 | 0.018 | 75 |  | 15 | 0.023 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1995 | 16 | 210.9 | 36 | 158 | 1191.2 | 13.6 | 1.4 | 37.9 | 0 | 0 | 12 | 0.034 | 62 |  | 13 | 0.022 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1995 | 16 | 260.3 | 42 | 200.6 | 1458.8 | 4.4 | 1 | 52.7 | 0.4 | 1.2 | 9 | 0.035 | 75 |  | 18 | 0.02 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable. Corrosive IEC. Non-corrosive ASTM 2C.
33000 | 1995 | 16 | 250.4 | 41.81 | 166.1 | 1384.2 | 35.1 | 1.8 | 46.9 | 0 | 0.5 | 8 | 0.036 | 91 |  | 8 | 0.033 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1995 | 16 | 173.3 | 42 | 103.3 | 1104.5 | 28.4 | 1.8 | 35.3 | 0 | 4.5 | 8 | 0.037 | 90 |  | 12 | 0.022 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1995 | 16 | 190.7 | 58 | 143 | 1225.5 | 4.7 | 1.7 | 39.7 | 0 | 1.6 | 9 | 0.04 | 81 |  | 14 | 0.019 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1995 | 16 | 1064 | 50 | 896 | 2971 | 59 | 44 | 17 | 48 | 0 | 11 | 0.034 | 67 |  | 6.4 | 0.046 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1995 | 16 | 1470.4 | 60 | 1249.2 | 5758.8 | 89.6 | 53.7 | 26.5 | 51.4 | 0 | 15 | 0.089 | 33 |  | 2 | 0.148 | DGA is assessed as acceptable. | Oil and insulation are deteriorating at accelerated rate.
33000 | 1995 | 16 | 1454.4 | 54 | 1269.7 | 7497.5 | 107.4 | 21.6 | 25.1 | 30.6 | 0 | 19 | 0.114 | 75 |  | 3 | 0.074 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1995 | 16 | 1230.5 | 57 | 1074.8 | 5283.8 | 97.5 | 23.4 | 15.9 | 18.9 | 0 | 14 | 0.113 | 48 |  | 2 | 0.113 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1995 | 16 | 1244.5 | 62 | 1142.2 | 6640.3 | 73.3 | 13 | 10.6 | 5.4 | 0 | 15 | 0.176 | 68 |  | 2 | 0.121 | DGA is assessed as acceptable | Acidity level is slightly high and trending upwards at a unusually high rate. Other oil quality results are assessed as acceptable.
33000 | 1995 | 16 | 499.6 | 41 | 442.9 | 3397.1 | 43.5 | 3.3 | 5.4 | 4.5 | 0 | 11 | 0.151 | 62 |  | 2 | 0.095 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1995 | 16 | 388 | 38 | 337.2 | 2680.5 | 42.8 | 2.9 | 2.1 | 3 | 0 | 13 | 0.178 | 75 |  | 2 | 0.095 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable. Non-corrosive IEC. Non-corrosive ASTM 3A.
33000 | 1995 | 16 | 360.3 | 32 | 310 | 2137 | 43.1 | 3 | 1.9 | 2 | 0.3 | 9 | 0.17 | 70 |  | 4 | 0.05 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable. Non-corrosive IEC. Non-corrosive ASTM 3B.
33000 | 1995 | 16 | 354.6 | 48 | 299.3 | 2051.7 | 45.3 | 7 | 1.5 | 1.5 | 0 | 12 | 0.162 | 76 |  | 3 | 0.071 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable. Non-corrosive IEC. Non-corrosive ASTM 3B.
33000 | 1995 | 16 | 1135 | 41.81 | 809 | 3975 | 78 | 56 | 134 | 58 | 0 | 10 | 0.033 | 69 |  | 5.4 | 0.065 | Dissolved gas analysis suggests hot spot in oil. | Oil quality is assessed as acceptable.
33000 | 1995 | 16 | 1292 | 54 | 907 | 5352 | 94 | 22 | 190 | 79 | 0 | 13 | 0.049 | 75 |  | 2.7 | 0.091 | Ethylene and ethane gas levels increasing. Dissolved gas analysis suggests hot spot in oil. | Oil quality is assessed as acceptable.
33000 | 1995 | 16 | 1289 | 58 | 978 | 5709 | 58 | 25 | 157 | 69 | 2 | 13 | 0.058 | 67 |  | 4.8 | 0.05 | Dissolved gas analysis suggests oil overheating. | Oil quality is assessed as acceptable.
33000 | 1995 | 16 | 1326 | 77 | 954 | 6290 | 71 | 20 | 158 | 92 | 31 | 12 | 0.077 | 56 |  | 3 | 0.099 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1995 | 16 | 1459.7 | 57 | 1050.4 | 7109 | 91.5 | 17.4 | 160.3 | 92.5 | 47.6 | 10 | 0.085 | 75 |  | 2 | 0.131 | The test results are relatively stable. | Oil quality is assessed as acceptable.
33000 | 1995 | 16 | 1313.8 | 58 | 932.3 | 6685.1 | 76.4 | 17 | 154.2 | 86.5 | 47.4 | 10 | 0.08 | 53 |  | 3 | 0.091 | Test results are relatively stable. | Oil quality is assessed as acceptable.
33000 | 1995 | 16 | 1483.1 | 58 | 1079 | 7007.8 | 87 | 18.4 | 160.2 | 89.2 | 49.3 | 10 | 0.081 | 56 |  | 2 | 0.115 | Test results are relatively stable. | Oil quality is assessed as acceptable.
33000 | 1995 | 16 | 1455.7 | 44 | 1059.2 | 8997 | 88.5 | 18.3 | 153.3 | 86.8 | 49.6 | 13 | 0.085 | 45 |  | 2 | 0.144 | The test results are assessed as relatively stable. | Oil quality is assessed as acceptable.
33000 | 1995 | 16 | 1353.7 | 60 | 993.3 | 8953.4 | 66.1 | 13.9 | 143.8 | 74.7 | 61.9 | 19 | 0.097 | 74 |  | 2 | 0.134 | Dissolved gas levels are relatively stable. | Oil quality is assessed as acceptable.
33000 | 1995 | 16 | 1251.9 | 41 | 964 | 8219.2 | 57 | 13.2 | 118.6 | 57.9 | 41.2 | 17 | 0.099 | 75 |  | 2 | 0.134 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1995 | 16 | 1269.1 | 56 | 1032.5 | 9034.3 | 73.6 | 10.4 | 74 | 44 | 34.6 | 24 | 0.121 | 60 |  | 2 | 0.122 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1995 | 16 | 1107 | 58 | 956.5 | 8222.3 | 50.3 | 9.7 | 40.9 | 19.9 | 29.7 | 16 | 0.125 | 75 |  | 2 | 0.126 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1995 | 16 | 57 | 31 | 53 | 422 | 0 | 2 | 1 | 1 | 0 | 10 | 0.01 | 69 |  | 143.3 | 0.003 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1995 | 16 | 68 | 46 | 42 | 649 | 16 | 6 | 1 | 3 | 0 | 3 | 0.01 | 72 |  | 78.2 | 0.004 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1995 | 16 | 274.8 | 44 | 176.5 | 1588.1 | 89 | 2.9 | 2.6 | 3.4 | 0.4 | 8 | 0.023 | 75 |  | 8 | 0.027 | The test results are assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1995 | 16 | 280.2 | 44 | 239.1 | 2211.4 | 36.1 | 2.3 | 1.9 | 0.8 | 0 | 8 | 0.081 | 75 |  | 7 | 0.028 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1995 | 16 | 275.7 | 40 | 238 | 2087.4 | 32.7 | 2.4 | 2 | 0.6 | 0 | 9 | 0.089 | 91 |  | 6 | 0.035 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable. Corrosive IEC. Non-corrosive ASTM 3B.
33000 | 1995 | 16 | 230.2 | 35 | 196.3 | 1875.7 | 25.9 | 4.5 | 1.6 | 1.9 | 0 | 10 | 0.1 | 93 |  | 4 | 0.043 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1995 | 16 | 144.5 | 48 | 126 | 1462.8 | 14.7 | 1.8 | 1.2 | 0.8 | 0 | 10 | 0.17 | 82 |  | 5 | 0.042 | DGA is assessed as acceptable. | Acidity level is high. Other oil quality results are assessed as acceptable.
33000 | 1995 | 16 | 198.4 | 44 | 174.4 | 1715.9 | 20.8 | 1.9 | 1.3 | 0 | 0 | 10 | 0.112 | 85 |  | 4 | 0.049 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1995 | 16 | 359 | 54 | 111 | 653 | 21 | 31 | 6 | 190 | 0 | 6 | 0.012 | 70 |  | 6.6 | 0.037 | Ethane level high for age of transformer. Slight overheating indicated. | Oil quality poor for age.
33000 | 1995 | 16 | 605.6 | 45 | 370.5 | 2165.6 | 157.6 | 9.3 | 5.1 | 63.1 | 0 | 11 | 0.06 | 75 |  | 2 | 0.08 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1995 | 16 | 421.9 | 44 | 368.2 | 3057.9 | 40.4 | 4.4 | 4.1 | 4.8 | 0 | 12 | 0.159 | 75 |  | 2 | 0.081 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1995 | 16 | 370.4 | 44 | 327.6 | 2747 | 36.3 | 2.3 | 3.2 | 1 | 0 | 11 | 0.162 | 87 |  | 3 | 0.06 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable. Corrosive IEC. Non-corrosive ASTM 3B.
33000 | 1995 | 16 | 384.3 | 35 | 337.5 | 2516 | 34.1 | 8.8 | 2.3 | 1.6 | 0 | 12 | 0.182 | 65 |  | 3 | 0.078 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1995 | 16 | 187.3 | 49 | 165.6 | 1745 | 17 | 2 | 1.8 | 0.9 | 0 | 12 | 0.191 | 100 |  | 3 | 0.073 | DGA is assessed as acceptable. | Acidity level is high. Other oil quality results are assessed as acceptable.
33000 | 1995 | 16 | 278.8 | 44 | 239.3 | 2048.8 | 25.4 | 10.8 | 2.3 | 1 | 0 | 16 | 0.199 | 93 |  | 3 | 0.065 | DGA is assessed as acceptable. | Acidity level is high. Other oil quality results are assessed as acceptable.
33000 | 1995 | 16 | 194 | 41.81 | 135 | 766 | 49 | 1 | 9 | 0 | 0 | 11 | 0.01 | 38 |  | 72.6 | 0.007 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1995 | 16 | 238.6 | 45 | 192.2 | 1351 | 12.4 | 1.6 | 30.8 | 0.6 | 1 | 10 | 0.01 | 75 |  | 36 | 0.016 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1995 | 16 | 181.3 | 38 | 142.9 | 1084.6 | 8.3 | 1.4 | 28 | 0.3 | 0.4 | 7 | 0.014 | 75 |  | 23 | 0.015 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1995 | 16 | 250.1 | 36 | 182.7 | 991.3 | 40 | 1.5 | 25.3 | 0.4 | 0.2 | 5 | 0.018 | 75 |  | 15 | 0.02 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1995 | 16 | 273.3 | 41 | 222.7 | 987 | 14.2 | 8.6 | 27.7 | 0.1 | 0 | 6 | 0.021 | 75 |  | 15 | 0.023 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable. Corrosive IEC. Non-corrosive ASTM 3B.
33000 | 1995 | 16 | 186.5 | 35 | 143.4 | 958 | 12.3 | 1.2 | 28.8 | 0.3 | 0.5 | 8 | 0.035 | 84 |  | 12 | 0.021 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1995 | 16 | 171.9 | 37 | 122 | 923.5 | 19.6 | 1.2 | 29 | 0.1 | 0 | 6 | 0.025 | 55 |  | 11 | 0.024 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1995 | 16 | 187 | 50 | 127 | 930 | 44 | 1 | 15 | 0 | 0 | 7 | 0.012 | 68 |  | 51.4 | 0.011 | Test results are assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1995 | 16 | 225.2226 | 50 | 161.9488 | 906.1117 | 17.4772 | 1.3966 | 43 | 0.5 | 0.9 | 5 | 0.01 | 75 |  | 23 | 0.018 | The test results are assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1995 | 16 | 268.8 | 47 | 218.4 | 1261.4 | 6.1 | 1.7 | 41.8 | 0.3 | 0.5 | 7 | 0.012 | 75 |  | 17 | 0.022 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1995 | 16 | 238.6 | 47 | 183.8 | 1194.1 | 11.5 | 1.6 | 41.5 | 0.2 | 0 | 6 | 0.028 | 75 |  | 14 | 0.024 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1995 | 16 | 236.8 | 42 | 189.1 | 1192.6 | 7.2 | 1.5 | 38.2 | 0 | 0.8 | 8 | 0.03 | 75 |  | 9 | 0.043 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable. Non-corrosive IEC. Non-corrosive ASTM 3B.
33000 | 1995 | 16 | 179.7 | 23 | 127.5 | 983.3 | 14.8 | 1.3 | 35.1 | 0.5 | 0.5 | 6 | 0.037 | 75 |  | 9 | 0.034 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable. Non-corrosive IEC. Non-corrosive ASTM 3A.
33000 | 1995 | 16 | 165.4 | 42 | 124.8 | 859.8 | 17.8 | 1.5 | 20.6 | 0.2 | 0.5 | 9 | 0.034 | 78 |  | 8 | 0.038 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1994 | 17 | 472 | 62 | 365 | 1316 | 50 | 26 | 7 | 23 | 1 | 19 | 0.027 | 57 |  | 69 | 0.005 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1994 | 17 | 585 | 66 | 519 | 2277 | 42 | 9 | 5 | 10 | 0 | 14 | 0.04 | 58 |  | 12.3 | 0.02 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1994 | 17 | 771 | 60 | 717 | 3560 | 37 | 7 | 5 | 5 | 0 | 9 | 0.041 | 75 |  | 3 | 0.093 | 2-furfural level is high for age of transformer. Accelerated aging is suggested.
33000 | 1994 | 17 | 710 | 35 | 639 | 3044 | 52 | 9 | 5 | 5 | 0 | 9 | 0.046 | 75 |  | 6 | 0.044 | 2-furfural level is high but stable. Other test results are assessed as acceptable.
33000 | 1994 | 17 | 482.1 | 40 | 429.4 | 2307 | 40.6 | 6 | 2.9 | 3.2 | 0 | 8 | 0.041 | 75 |  | 4 | 0.056 | 2-furfural level is high but stable. Other test results are assessed as acceptable.
33000 | 1994 | 17 | 506.8 | 34 | 450.3 | 2584.8 | 47.3 | 4 | 2.4 | 2.6 | 0.2 | 5 | 0.047 | 64 |  | 5 | 0.045 | 2-furfural level is trending upwards slightly. | Other test results are assessed as acceptable.
33000 | 1994 | 17 | 284.4 | 44 | 238.2 | 1855.7 | 39.5 | 3.4 | 1.2 | 2 | 0.1 | 10 | 0.044 | 75 |  | 4 | 0.063 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1994 | 17 | 774 | 60 | 516 | 2384 | 243 | 8 | 3 | 4 | 0 | 11 | 0.049 | 56 |  | 16.3 | 0.016 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1994 | 17 | 757 | 44 | 536 | 2790 | 210 | 5 | 3 | 2 | 1 | 9 | 0.053 | 73 |  | 7.7 | 0.027 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1994 | 17 | 518 | 45 | 409 | 2995 | 89 | 8 | 7 | 4 | 1 | 8 | 0.098 | 70 |  | 9 | 0.025 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1994 | 17 | 306 | 59 | 255.2 | 3093.9 | 37.5 | 6.1 | 2.1 | 0.6 | 4.5 | 15 | 0.126 | 75 |  | 6 | 0.04 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1994 | 17 | 508 | 53 | 431 | 3230 | 61 | 5 | 5 | 3 | 3 | 13 | 0.14 | 75 |  | 7 | 0.033 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1994 | 17 | 125.2 | 38 | 98.6 | 1259.3 | 18.5 | 2.7 | 1.4 | 3.8 | 0.2 | 9 | 0.133 | 44 |  | 8 | 0.028 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1994 | 17 | 101.5 | 38 | 87.2 | 1278.6 | 13 | 1.1 | 0.2 | 0 | 0 | 12 | 0.151 | 75 |  | 7 | 0.036 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable. Non-corrosive IEC. Non-corrosive ASTM 3B.
33000 | 1994 | 17 | 90.2 | 48 | 73.3 | 1090.3 | 13 | 2.1 | 0.5 | 1 | 0.3 | 8 | 0.141 | 72 |  | 7 | 0.03 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1994 | 17 | 88.3 | 42 | 67.8 | 1061.5 | 16.4 | 2.7 | 0.5 | 0.7 | 0.2 | 14 | 0.14 | 52 |  | 7 | 0.032 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1994 | 17 | 489 | 16 | 322 | 1411 | 147 | 7 | 3 | 9 | 1 | 10 | 0.023 | 46 |  | 33.8 | 0.009 | Test results satisfactory. (Sampled after low oil trip.)
33000 | 1994 | 17 | 774 | 63 | 589 | 2692 | 160 | 14 | 4 | 7 | 0 | 16 | 0.049 | 75 |  | 7.5 | 0.032 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1994 | 17 | 989 | 44 | 751 | 3435 | 220 | 9 | 5 | 3 | 1 | 12 | 0.083 | 63 |  | 5.2 | 0.048 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1994 | 17 | 645 | 42 | 523 | 3411 | 101 | 7 | 8 | 5 | 1 | 16 | 0.109 | 59 |  | 8 | 0.031 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1994 | 17 | 412.8 | 72 | 339.7 | 3623.4 | 48.4 | 8 | 9.2 | 2.3 | 5.2 | 15 | 0.145 | 75 |  | 6 | 0.035 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1994 | 17 | 620 | 54 | 531 | 3360 | 75 | 5 | 5 | 3 | 1 | 13 | 0.162 | 74 |  | 6 | 0.034 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1994 | 17 | 215.9 | 40 | 174.7 | 1949.9 | 27.4 | 6.8 | 2.1 | 4.9 | 0 | 8 | 0.151 | 75 |  | 6 | 0.037 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1994 | 17 | 165.2 | 48 | 139.8 | 1601.7 | 21.7 | 2 | 0.4 | 1 | 0.3 | 14 | 0.178 | 75 |  | 6 | 0.041 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable. Non-corrosive IEC. Non-corrosive ASTM 3B.
33000 | 1994 | 17 | 153.5 | 46 | 130.7 | 1742.7 | 20.2 | 1.3 | 0.6 | 0.7 | 0 | 12 | 0.169 | 49 |  | 6 | 0.035 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1994 | 17 | 126 | 36 | 102.5 | 1280.5 | 18.2 | 2.3 | 0.8 | 1 | 1.2 | 10 | 0.116 | 74 |  | 6 | 0.036 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1993 | 18 | 120 | 40 | 98 | 1299 | 20 | 2 | 0 | 0 | 0 | 9 | 0.014 | 66 |  | 55.7 | 0.01 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1993 | 18 | 172 | 36 | 123 | 1370 | 46 | 2 | 0 | 1 | 0 | 16 | 0.014 | 57 |  | 30.1 | 0.025 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1993 | 18 | 361 | 36 | 269.9 | 2329.6 | 72.2 | 4.1 | 3.6 | 4.3 | 6.9 | 14 | 0.023 | 75 |  | 21 | 0.012 | The test results are assessed as acceptable at present. | Oil quality is assessed as acceptable.
33000 | 1993 | 18 | 470.7 | 44 | 326.1 | 2635.4 | 122.6 | 5.6 | 5.4 | 10.7 | 0.3 | 11 | 0.031 | 75 |  | 22 | 0.01 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1993 | 18 | 447.8 | 48 | 316.5 | 2595.8 | 113.1 | 5.5 | 4.9 | 7.5 | 0.3 | 13 | 0.031 | 56 |  | 14 | 0.018 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1993 | 18 | 506.8 | 40 | 372.1 | 2659.5 | 102.4 | 8.9 | 8.7 | 14.7 | 0 | 17 | 0.046 | 75 |  | 11 | 0.023 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1993 | 18 | 202.1 | 36 | 166.9 | 1931 | 31.1 | 0.7 | 2.9 | 0.2 | 0.3 | 11 | 0.062 | 66 |  | 15 | 0.013 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1993 | 18 | 310.9 | 48 | 227.4 | 2221.5 | 53.4 | 11.3 | 7.9 | 10.4 | 0.5 | 19 | 0.066 | 51 |  | 16 | 0.018 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1993 | 18 | 442.8 | 62 | 321.4 | 3384.4 | 105.8 | 6.8 | 3.8 | 5 | 0 | 41 | 0.066 | 20 |  | 15 | 0.015 | DGA is assessed as acceptable. | Breakdown voltage is low. Other oil quality results are assessed as acceptable. Non-corrosive IEC. Non-corrosive ASTM 3B. Oil is cloudy in appearance.
33000 | 1993 | 18 | 325.5 | 42 | 225.3 | 2967.3 | 55.6 | 8 | 15.5 | 20.8 | 0.3 | 38 | 0.076 | 26 |  | 16 | 0.015 | DGA is assessed as acceptable. | Breakdown voltage is low. Other oil quality results are assessed as acceptable.
33000 | 1992 | 19 | 457 | 41.81 | 405 | 1905 | 37 | 9 | 1 | 5 | 0 | 9 | 0.004 | 85 |  | 523.4 | 0.002 | Test results are assessed as acceptable.
33000 | 1991 | 20 | 1051 | 34 | 59 | 721 | 44 | 86 | 316 | 19 | 527 | 26 | 0.023 | 19 |  | 37.3 | 0.025 | Oil still contains abnormal hydrocarbon gases dissolved levels. SHOULD BE INVESTIGATED.
33000 | 1991 | 20 | 549 | 47 | 173 | 1024 | 50 | 60 | 13 | 237 | 16 | 12 | 0.021 | 73 |  | 7.4 | 0.058 | DGA suggests slight overheating. RECOMMEND RESAMPLE IN 1 YEAR.
33000 | 1991 | 20 | 745 | 44 | 510 | 3882 | 188 | 12 | 2 | 32 | 1 | 18 | 0.076 | 75 |  | 6.6 | 0.038 | Test results are assessed as acceptable. Has transformer oil been degassed since last sample?
33000 | 1991 | 20 | 567 | 29 | 415 | 3360 | 94 | 17 | 8 | 31 | 2 | 17 | 0.131 | 75 |  | 6 | 0.038 | Acidity of oil is trending upwards. 2-furfural level is high for transformer age. RECOMMEND RESAMPLE IN 1 YEAR TO MONITOR TREND.
33000 | 1991 | 20 | 344 | 48 | 253 | 3070 | 73 | 5 | 4 | 7 | 2 | 32 | 0.142 | 41 |  | 4 | 0.057 | 2-furfural and acidity levels are trending upwards. Moisture content of sample is high. Dissolved gas analysis is assessed as acceptable. RECOMMEND RESAMPLE IN 1 YEAR TO MONITOR TREND.
33000 | 1991 | 20 | 408.9 | 44 | 336.4 | 3533.5 | 60.5 | 4.7 | 3 | 3.7 | 0.6 | 40 | 0.161 | 46 |  | 4 | 0.056 | DGA is assessed as acceptable. | Moisture content is high. Other oil quality results are assessed as acceptable.
33000 | 1991 | 20 | 382.2 | 55 | 320.2 | 3321 | 54.4 | 3.3 | 1.5 | 2 | 0.8 | 19 | 0.2045 | 63 |  | 4 | 0.053 | DGA is assessed as acceptable. | Acidity level is high. Other oil quality results are assessed as acceptable.
33000 | 1991 | 20 | 748.1 | 46 | 602.1 | 5608.3 | 105.9 | 20.2 | 9.9 | 9.2 | 0.8 | 28 | 0.175 | 41 |  | 2 | 0.102 | Carbon oxide levels are increased. | Oil quality is assessed as acceptable.
33000 | 1991 | 20 | 186.5 | 40 | 150.3 | 1997.7 | 28.7 | 2.8 | 1.2 | 2.9 | 0.6 | 27 | 0.202 | 38 |  | 7 | 0.026 | DGA is assessed as acceptable. | Acidity level is high. Other oil quality results are assessed as acceptable. Non-corrosive IEC. Non-corrosive ASTM 2E.
33000 | 1991 | 20 | 214.3 | 45 | 172.6 | 2250.9 | 30.4 | 8.3 | 1.6 | 0.8 | 0.6 | 29 | 0.213 | 42 |  | 6 | 0.032 | DGA is assessed as acceptable. | Acidity level is high. Other oil quality results are assessed as acceptable.
33000 | 1991 | 20 | 3 | 48 | 3 | 66 | 0 | 0 | 0 | 0 | 0 | 8 | 0.014 | 66 |  | 73.4 | 0.006 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1991 | 20 | 45 | 34 | 41 | 503 | 0 | 1 | 1 | 2 | 0 | 24 | 0.021 | 40 |  | 42.4 | 0.01 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1991 | 20 | 604 | 30 | 197 | 896 | 51 | 95 | 41 | 219 | 1 | 9 | 0.01 | 54 |  | 9.7 | 0.044 | Gas levels fairly stable. RECOMMEND RESAMPLE IN 6 MONTHS.
33000 | 1991 | 20 | 571 | 38 | 277 | 1334 | 174 | 15 | 8 | 96 | 1 | 9 | 0.035 | 66 |  | 15.2 | 0.018 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1991 | 20 | 540 | 44 | 413 | 2919 | 122 | 2 | 1 | 2 | 0 | 13 | 0.084 | 66 |  | 9.1 | 0.022 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1991 | 20 | 504 | 25 | 374 | 2910 | 80 | 12 | 8 | 29 | 1 | 10 | 0.147 | 75 |  | 9 | 0.024 | Acidity level is trending upwards. 2-furfural level is high for transformer age. RECOMMEND RESAMPLE IN 1 YEAR TO MONITOR TREND.
33000 | 1991 | 20 | 2273.3 | 29 | 196.3 | 2448.1 | 167.2 | 453.3 | 825.3 | 198.4 | 432.8 | 23 | 0.133 | 64 |  | 8 | 0.035 | Hydrocarbon gas content is abnormal. Dissolved gas analysis suggests high temperature oil overheating with possible arcing has occurred. (Samples taken after tapchanger failure).
33000 | 1991 | 20 | 1728.2 | 25 | 167.7 | 2350.8 | 136.8 | 311.8 | 555.6 | 127.5 | 428.8 | 21 | 0.139 | 59 |  | 8 | 0.029 | Hydrocarbon gas content is abnormal. Dissolved gas analysis suggests high temperature oil overheating with possible arcing has occurred.
33000 | 1991 | 20 | 2680 | 41.81 | 155 | 2093 | 861 | 455 | 627 | 146 | 436 | 16 | 0.133 | 75 |  | 9 | 0.022 | Hydrocarbon gas content is abnormal. Dissolved gas analysis suggests high temperature oil overheating with possible arcing has occurred. (Transformer is out of service undergoing investigation).
33000 | 1991 | 20 | 268.9 | 54 | 235.2 | 1663.9 | 27.9 | 2 | 3.1 | 0.4 | 0.3 | 15 | 0.082 | 75 |  | 7 | 0.034 | Dissolved gas levels are reduced. DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1991 | 20 | 345.7 | 55 | 292.7 | 2077.3 | 46.4 | 2.6 | 3 | 1 | 0 | 12 | 0.104 | 75 |  | 5 | 0.041 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1991 | 20 | 562 | 45 | 461.7 | 3676.1 | 68 | 7.4 | 13.9 | 10.1 | 0.9 | 12 | 0.097 | 46 |  | 6 | 0.04 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1991 | 20 | 252.6 | 51 | 206.9 | 1864.5 | 39.2 | 2.5 | 2.1 | 1.2 | 0.7 | 12 | 0.116 | 77 |  | 6 | 0.035 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable. Corrosive IEC. Non-corrosive ASTM 3B.
33000 | 1991 | 20 | 347.8 | 45 | 284.4 | 2650.1 | 50.6 | 7.2 | 3.7 | 0.9 | 1 | 17 | 0.124 | 53 |  | 5 | 0.045 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1990 | 21 | 611 | 41.81 | 540 | 2597 | 52 | 11 | 2 | 2 | 4 | 7 | 0.005 | 75 |  | 621.9 | 0.002 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1990 | 21 | 15 | 24 | 11 | 862.8 | 1.8 | 0.9 | 1.2 | 0.1 | 0 | 11 | 0.003 | 51 |  | 80 | 0.008 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1990 | 21 | 107.1 | 11 | 79.2 | 2469 | 2.9 | 5.5 | 17.3 | 2 | 0.2 | 3 | 0.002 | 92 |  | 116 | 0.006 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1990 | 21 | 11 | 17 | 7.9 | 820.9 | 1.3 | 0.8 | 0.8 | 0.1 | 0.1 | 10 | 0.004 | 90 |  | 70 | 0.009 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1990 | 21 | 39 | 41.81 | 30 | 1360 | 5 | 1 | 3 | 0 | 0 | 13 | 0.009 | 54 |  | 120.6 | 0.006 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1990 | 21 | 234.8 | 21 | 215.3 | 2282 | 9.8 | 3.9 | 4.6 | 0.9 | 0.3 | 3 | 0.005 | 75 |  | 210 | 0.005 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1990 | 21 | 250.3 | 19 | 229.3 | 2330 | 10.4 | 4.7 | 4.8 | 0.9 | 0.2 | 3 | 0.006 | 91 |  | 167 | 0.006 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1990 | 21 | 90 | 22 | 20 | 127 | 68 | 1 | 1 | 0 | 0 | 10 | 0.01 | 41 |  | 316.7 | 0.003 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1990 | 21 | 61 | 36 | 55 | 482 | 0 | 1 | 5 | 0 | 0 | 9 | 0.01 | 53 |  | 83.8 | 0.005 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1990 | 21 | 132 | 30 | 113 | 909 | 13 | 2 | 3 | 1 | 0 | 6 | 0.01 | 52 |  | 31.3 | 0.011 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1990 | 21 | 92 | 26 | 68 | 989 | 19 | 2 | 2 | 1 | 0 | 6 | 0.014 | 75 |  | 35.3 | 0.009 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1990 | 21 | 171.8 | 41 | 159 | 1570.2 | 5.6 | 2.7 | 3 | 1.3 | 0.2 | 8 | 0.025 | 75 |  | 7 | 0.038 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1990 | 21 | 127.9 | 39 | 121.3 | 1385.6 | 1.7 | 2.1 | 1.6 | 1.1 | 0.1 | 7 | 0.032 | 75 |  | 5 | 0.045 | DGA is assessed as acceptable. | Moisture is assessed as acceptable.
33000 | 1990 | 21 | 255.7 | 54 | 235.7 | 2066.6 | 14.2 | 3.1 | 1.8 | 0.9 | 0 | 9 | 0.04 | 75 |  | 6 | 0.041 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1990 | 21 | 255.7 | 58 | 238.1 | 2169.3 | 11.7 | 3 | 1.6 | 1.3 | 0 | 10 | 0.043 | 80 |  | 5 | 0.043 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1990 | 21 | 71.3 | 33 | 63.6 | 1247.9 | 4.2 | 1.6 | 1 | 0.9 | 0 | 9 | 0.047 | 90 |  | 6 | 0.042 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable. Corrosive IEC. Non-corrosive ASTM 3B.
33000 | 1990 | 21 | 116.8 | 55 | 106.3 | 1294.3 | 6.6 | 2.7 | 0.8 | 0.4 | 0 | 10 | 0.05 | 89 |  | 5 | 0.051 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1990 | 21 | 72 | 41.81 | 21 | 151 | 48 | 1 | 2 | 0 | 0 | 8 | 0.01 | 62 |  | 284.4 | 0.004 | Test results satisfactory. | Oil quality is assessed as acceptable.
33000 | 1990 | 21 | 41 | 32 | 40 | 566 | 0 | 1 | 0 | 0 | 0 | 9 | 0.019 | 47 |  | 64.2 | 0.007 | Test results satisfactory. | Oil quality is assessed as acceptable.
33000 | 1990 | 21 | 102 | 25 | 77 | 1086 | 19 | 2 | 3 | 1 | 0 | 4 | 0.016 | 58 |  | 28 | 0.011 | Test results are assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1990 | 21 | 5036 | 35 | 11 | 606 | 910 | 161 | 302 | 11 | 3641 | 8 | 0.011 | 75 |  | 272.8 | 0.002 | Dissolved gas analysis appears normal for a tapchanger. | Other test results are assessed as acceptable.
33000 | 1990 | 21 | 182.9 | 40 | 168.9 | 1643.9 | 5.6 | 2.8 | 3.9 | 1.6 | 0.1 | 7 | 0.027 | 75 |  | 5 | 0.048 | The test results are assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1990 | 21 | 141 | 33 | 133 | 1388.7 | 2.3 | 2.2 | 2.2 | 1.1 | 0.2 | 8 | 0.04 | 75 |  | 4 | 0.061 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1990 | 21 | 262.7 | 59 | 244.9 | 2087.5 | 11.5 | 3.3 | 2.2 | 0.8 | 0 | 9 | 0.052 | 75 |  | 4 | 0.054 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1990 | 21 | 279.9 | 58 | 262.7 | 2159.7 | 10.6 | 3.2 | 2.1 | 1.3 | 0 | 12 | 0.055 | 81 |  | 4 | 0.058 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1990 | 21 | 281.8 | 51 | 260 | 2263.8 | 15.4 | 3.5 | 1.8 | 1.1 | 0 | 16 | 0.065 | 95 |  | 4 | 0.063 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable. Corrosive IEC. Non-corrosive ASTM 3B.
33000 | 1990 | 21 | 129.8 | 56 | 117.3 | 1281 | 8.2 | 2.8 | 0.6 | 0.9 | 0 | 10 | 0.067 | 95 |  | 4 | 0.062 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable. Corrosive IEC. Non-corrosive ASTM 3B.
33000 | 1990 | 21 | 7 | 20 | 1 | 166 | 6 | 0 | 0 | 0 | 0 | 13 | 0.01 | 42 |  | 43.1 | 0.0076 | Test results satisfactory. Transformer not commissioned.
33000 | 1990 | 21 | 63 | 40 | 58 | 627 | 0 | 1 | 4 | 0 | 0 | 4 | 0.01 | 61 |  | 88 | 0.006 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1990 | 21 | 88 | 50 | 77 | 833 | 0 | 2 | 9 | 0 | 0 | 8 | 0.016 | 54 |  | 28.2 | 0.013 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1990 | 21 | 94 | 40 | 77 | 1181 | 10 | 3 | 2 | 2 | 0 | 10 | 0.022 | 53 |  | 19 | 0.0144 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1990 | 21 | 128 | 40 | 113.6 | 1383.7 | 9.7 | 0 | 3.4 | 1.3 | 0 | 7 | 0.027 | 75 |  | 8 | 0.034 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1990 | 21 | 127.1 | 39 | 116.8 | 1561.1 | 4.6 | 5 | 0.7 | 0 | 0 | 5 | 0.038 | 31 |  | 6.5 | 0.043 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1990 | 21 | 149.2 | 41 | 136.6 | 1586.2 | 7.2 | 2.2 | 1.8 | 1.1 | 0.3 | 8 | 0.04 | 75 |  | 5 | 0.048 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1990 | 21 | 146.8 | 50 | 136.2 | 1761.4 | 6.4 | 1.3 | 1.9 | 1 | 0 | 10 | 0.044 | 62 |  | 5 | 0.05 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable. Corrosive IEC. Non-corrosive ASTM 3B.
33000 | 1990 | 21 | 121.8 | 58 | 115.9 | 1813.6 | 0 | 2.9 | 2 | 1 | 0 | 7 | 0.053 | 75 |  | 5.66 | 0.048 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1990 | 21 | 156 | 64 | 141.5 | 2054.5 | 7.6 | 2.4 | 3.2 | 1.3 | 0 | 11 | 0.056 | 91 |  | 4 | 0.057 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1990 | 21 | 152.4 | 54 | 127.1 | 1803.6 | 18.3 | 2.6 | 2.4 | 2 | 0 | 9 | 0.048 | 57 |  | 4 | 0.06 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1990 | 21 | 32 | 41.81 | 8 | 97 | 24 | 0 | 0 | 0 | 0 | 13 | 0.011 | 50 |  | 108.3 | 0.005 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1990 | 21 | 171 | 40 | 124 | 1126 | 35 | 3 | 2 | 7 | 0 | 12 | 0.017 | 65 |  | 26.5 | 0.012 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1990 | 21 | 133 | 50 | 86 | 981 | 42 | 2 | 1 | 2 | 0 | 8 | 0.026 | 46 |  | 18.5 | 0.014 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1990 | 21 | 90 | 50 | 73 | 1354 | 8 | 3 | 2 | 1 | 3 | 17 | 0.037 | 60 |  | 11.9 | 0.0171 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1990 | 21 | 162.9 | 38 | 103 | 1704.1 | 52.8 | 2.7 | 2.2 | 2.2 | 0 | 8 | 0.054 | 54 |  | 4 | 0.057 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1990 | 21 | 80.3 | 32 | 67.2 | 1430.9 | 6.7 | 5.1 | 0.2 | 1.1 | 0 | 8 | 0.057 | 75 |  | 4 | 0.052 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1990 | 21 | 89.6 | 35 | 75.2 | 1282.7 | 11 | 1.5 | 0.7 | 0.9 | 0.3 | 8 | 0.066 | 75 |  | 3 | 0.066 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1990 | 21 | 85.4 | 36 | 70.8 | 1262.6 | 12.3 | 0.7 | 0.8 | 0.8 | 0 | 9 | 0.064 | 75 |  | 4 | 0.066 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable. Corrosive IEC. Corrosive ASTM 4A.
33000 | 1990 | 21 | 82.1 | 25 | 66.7 | 1433.3 | 8.6 | 1.6 | 3.5 | 1.7 | 0 | 9 | 0.071 | 87 |  | 3 | 0.08 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1990 | 21 | 64.8 | 40 | 62.5 | 1392.5 | 0 | 0 | 1.6 | 0.7 | 0 | 8 | 0.067 | 91 |  | 3 | 0.064 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1989 | 22 | 34 | 41.81 | 32 | 300 | 0 | 0 | 1 | 1 | 0 | 8 | 0.017 | 66 |  | 25 | 0.021 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1989 | 22 | 422 | 49 | 264 | 3527 | 66 | 3 | 10 | 3 | 76 | 12 | 0.0735 | 73 |  | 18.9 | 0.013 | DGA is assessed as acceptable. Acetylene gas possibly communicating from tapchanger. | Oil quality is assessed as acceptable.
33000 | 1989 | 22 | 328 | 50 | 86 | 2268 | 27 | 4 | 14 | 48 | 149 | 18 | 0.107 | 54 |  | 11.3 | 0.02 | DGA is assessed as acceptable. Acetylene gas possibly communicating from tapchanger. | Oil quality is assessed as acceptable.
33000 | 1989 | 22 | 548 | 57 | 294 | 5310 | 32 | 10 | 46 | 18 | 148 | 16 | 0.163 | 75 |  | 2 | 0.095 | 2-furfural level is high and trending upwards; acidity level is trending upwards. Other test results are assessed as acceptable. RECOMMEND RESAMPLE IN 1 YEAR TO MONITOR 2-FURFURAL AND ACIDITY.
33000 | 1989 | 22 | 472.5 | 62 | 336 | 5310.4 | 26 | 7.2 | 22.2 | 14.2 | 66.9 | 26 | 0.18 | 75 |  | 4 | 0.064 | 2-furfural level is high and trending upwards suggesting advanced state of insulation degradation. Acidity level of sample is high. Other test results are assessed as acceptable. RECOMMEND RESAMPLE IN 1 YEAR TO MONITOR CONDITION.
33000 | 1989 | 22 | 455.2 | 50 | 313.4 | 5299.3 | 29.3 | 6.8 | 22.6 | 15.2 | 67.9 | 31 | 0.182 | 22 |  | 5 | 0.046 | Moisture content of sample is high. Breakdown voltage is low. Possible sample contamination. Other test results are consistent with sample taken 15.08.03. RECOMMEND RESAMPLE IN 1 YEAR TO MONITOR CONDITION.
33000 | 1989 | 22 | 468 | 54 | 358 | 6329 | 32 | 8 | 22 | 14 | 34 | 39 | 0.215 | 41 |  | 3 | 0.08 | 2-furfural level is high and trending upwards suggesting advanced state of insulation degradation. Carbon oxide levels are trending upwards. Moisture content of sample is high. Acidity level of sample is high. RECOMMEND RESAMPLE IN 1 YEAR TO MONITOR C
33000 | 1989 | 22 | 430.6 | 60 | 330.8 | 6058.4 | 27.1 | 7.5 | 19.9 | 12.6 | 32.7 | 28 | 0.207 | 39 |  | 4.1503 | 0.06776 | 2-furfural level is high and trending upwards suggesting advanced state of insulation degradation. Acidity level is high but stable. Other test results are assessed as acceptable. RECOMMEND RESAMPLE IN 1 YEAR TO MONITOR CONDITION.
33000 | 1989 | 22 | 265.2 | 60 | 223.4 | 3179.6 | 18 | 3.2 | 6 | 4.2 | 10.4 | 26 | 0.205 | 41 |  | 4 | 0.074 | Dissolved gas analysis is assessed as acceptable. 2-furfural level is high suggesting advanced state of insulation degradation. Other oil quality results are assessed as acceptable. RECOMMEND RESAMPLE IN 1 YEAR TO MONITOR CONDITION.
33000 | 1989 | 22 | 32 | 41.81 | 25 | 335 | 0 | 2 | 3 | 1 | 1 | 15 | 0.017 | 47 |  | 40 | 0.017 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1989 | 22 | 422 | 45 | 252 | 4019 | 55 | 5 | 13 | 5 | 92 | 16 | 0.079 | 45 |  | 19 | 0.015 | DGA is assessed as acceptable. Acetylene gas possibly communicating from tapchanger. | Oil quality is assessed as acceptable.
33000 | 1989 | 22 | 347 | 40 | 180 | 3848 | 26 | 5 | 17 | 4 | 115 | 18 | 0.075 | 69 |  | 6.5 | 0.035 | DGA is assessed as acceptable. Acetylene gas possibly communicating from tapchanger. | Oil quality is assessed as acceptable.
33000 | 1989 | 22 | 243 | 40 | 104 | 1811 | 25 | 4 | 8 | 2 | 100 | 17 | 0.099 | 68 |  | 12.1 | 0.017 | DGA is assessed as acceptable. Acetylene gas possibly communicating from tapchanger. | Oil quality is assessed as acceptable.
33000 | 1989 | 22 | 494 | 52 | 295 | 5880 | 29 | 9 | 29 | 8 | 124 | 16 | 0.165 | 75 |  | 3 | 0.083 | Acidity level is trending upwards. 2-furfural level is high suggesting advanced rate of insulation degradation. RECOMMEND RESAMPLE IN 1 YEAR TO MONITOR CONDITION.
33000 | 1989 | 22 | 532.5 | 56 | 370.7 | 6110.8 | 44.2 | 7.2 | 21.5 | 13.7 | 75.2 | 24 | 0.182 | 75 |  | 5 | 0.042 | 2-furfural level is high and trending upwards suggesting advanced state of insulation degradation. Other test results are assessed as acceptable. Acetylene gas possibly from tapchanger. RECOMMEND RESAMPLE IN 1 YEAR TO MONITOR CONDITION.
33000 | 1989 | 22 | 443.3 | 75 | 310.2 | 6311.4 | 20.9 | 6.2 | 20.9 | 10.2 | 74.9 | 40 | 0.186 | 19 |  | 5 | 0.042 | Moisture content of sample is high. Breakdown voltage of sample is low. Possible sample contamination. Other test results are consistent with sample taken 15.08.03. RECOMMEND RESAMPLE IN 1 YEAR TO MONITOR CONDITION.
33000 | 1989 | 22 | 506 | 41 | 385 | 7054 | 36 | 8 | 22 | 12 | 43 | 35 | 0.215 | 36 |  | 2 | 0.111 | 2-furfural level is high and trending upwards suggesting advanced state of insulation degradation. Carbon oxide levels are trending upwards. Moisture content of sample is high. Acidity level of sample is high. RECOMMEND RESAMPLE IN 1 YEAR TO MONITOR C
33000 | 1989 | 22 | 408.2 | 51 | 306.2 | 6631.9 | 25.4 | 7 | 20.1 | 10.5 | 39 | 22 | 0.209 | 36 |  | 4.8401 | 0.05555 | 2-furfural level is high and trending upwards suggesting advanced state of insulation degradation. Acidity level is high but stable. Other test results are assessed as acceptable. RECOMMEND RESAMPLE IN 1 YEAR TO MONITOR CONDITION.
33000 | 1989 | 22 | 233.4 | 50 | 195.4 | 3339.9 | 16.3 | 2.7 | 4.9 | 3.4 | 10.7 | 24 | 0.206 | 40 |  | 8 | 0.031 | Dissolved gas levels are reduced. 2-furfural level is high suggesting advanced state of insulation degradation. Acidity level of sample is high. Other oil quality results are assessed as acceptable.
33000 | 1989 | 22 | 196 | 45 | 111 | 3539 | 38 | 3 | 7 | 5 | 32 | 18 | 0.095 | 69 |  | 9.7 | 0.026 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1989 | 22 | 169 | 39 | 78 | 2717 | 24 | 3 | 8 | 2 | 54 | 15 | 0.09 | 54 |  | 6.2 | 0.033 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1989 | 22 | 272 | 45 | 119 | 2568 | 28 | 4 | 12 | 4 | 105 | 14 | 0.108 | 75 |  | 6.5 | 0.031 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1989 | 22 | 263 | 46 | 157 | 3980 | 17 | 5 | 14 | 3 | 67 | 10 | 0.152 | 75 |  | 4 | 0.056 | Acidity and 2-furfural are high for age of transformer. RECOMMEND RESAMPLE IN 1 YEAR TO MONITOR 2-FURFURAL AND ACIDITY.
33000 | 1989 | 22 | 636.5 | 62 | 253.5 | 4706.2 | 46 | 10.3 | 31 | 126.6 | 169.1 | 16 | 0.165 | 75 |  | 6 | 0.039 | 2-furfural level is trending upwards suggesting advanced state of insulation degradation. Dissolved gas analysis suggests mild oil overheating has occurred. Other test results are assessed as acceptable. RECOMMEND RESAMPLE IN 1 YEAR TO MONITOR CONDITIO
33000 | 1989 | 22 | 783.9 | 66 | 455.4 | 7127.5 | 63.1 | 15.6 | 46.3 | 17.3 | 186.2 | 32 | 0.193 | 40 |  | 2 | 0.137 | 2-furfural and carbon oxide levels are high and trending upwards suggesting accelerated rate of insulation degradation. Moisture content of sample is slightly high. RECOMMEND RESAMPLE IN 1 YEAR TO MONITOR CONDITION.
33000 | 1989 | 22 | 485 | 67 | 274.9 | 3843.9 | 45.3 | 9.3 | 27.1 | 12.1 | 116.3 | 30 | 0.188 | 30 |  | 5 | 0.046 | DGA is assessed as acceptable. | Oil quality is relatively stable.
33000 | 1989 | 22 | 221.6 | 52 | 172 | 2241.4 | 15.2 | 3.3 | 5.8 | 2.8 | 22.5 | 14 | 0.213 | 59 |  | 4 | 0.054 | DGA is assessed as acceptable. | Acidity level is high. Other oil quality results are assessed as acceptable.
33000 | 1989 | 22 | 156.8 | 43 | 108 | 1694.1 | 8.4 | 3.3 | 5.3 | 3.3 | 28.5 | 14 | 0.191 | 59 |  | 5 | 0.042 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1989 | 22 | 163.3 | 44 | 96.4 | 1504 | 11.8 | 2.6 | 6.3 | 4.3 | 41.9 | 15 | 0.204 | 59 |  | 7 | 0.034 | DGA is assessed as acceptable. | Acidity level is high but stable. Other oil quality results are assessed as acceptable. Corrosive IEC. Non-corrosive ASTM 2E.
33000 | 1989 | 22 | 59.3 | 41.81 | 40.3 | 1291.5 | 3.4 | 1.4 | 1.8 | 1.5 | 10.9 | 13 | 0.216 | 75 |  | 7 | 0.034 | DGA is assessed as acceptable. | Acidity level is high. Other oil quality results are assessed as acceptable. Non-corrosive IEC. Non-corrosive ASTM borderline 3B and 4A.
33000 | 1989 | 22 | 67.4 | 36 | 47.9 | 1297.2 | 1.7 | 1.2 | 1.8 | 1 | 13.8 | 12 | 0.2 | 64 |  | 8 | 0.028 | DGA is assessed as acceptable. | Acidity level is high. Other oil quality results are assessed as acceptable. Non-corrosive IEC. Non-corrosive ASTM 3A.
33000 | 1989 | 22 | 156 | 59 | 115 | 1849.3 | 11.1 | 2.4 | 5.2 | 1.7 | 20.6 | 21 | 0.213 | 75 |  | 6 | 0.04 | DGA is assessed as acceptable. | Acidity level is high. Other oil quality results are assessed as acceptable. Non-corrosive IEC. Non-corrosive ASTM 3B.
33000 | 1989 | 22 | 106 | 35 | 69 | 1355 | 8 | 2.4 | 3.1 | 1.2 | 22.3 | 13 | 0.2 | 79 |  | 7 | 0.033 | DGA is assessed as acceptable. | Acidity level is high. Other oil quality results are assessed as acceptable. Non-corrosive IEC. Non-corrosive ASTM 3A.
33000 | 1989 | 22 | 119.3 | 42 | 86.4 | 1465 | 6.5 | 3.1 | 2.7 | 1.4 | 19.2 | 14 | 0.193 | 88 |  | 7 | 0.031 | DGA is assessed as acceptable. | Acidity level is high. Other oil quality results are assessed as acceptable. Non-corrosive IEC. Non-corrosive ASTM 3A.
33000 | 1989 | 22 | 46 | 30 | 17 | 287 | 29 | 0 | 0 | 0 | 0 | 6 | 0.006 | 71 |  | 1000 | 0.0062 | Test results satisfactory. | Oil quality is assessed as acceptable.
33000 | 1989 | 22 | 248 | 50 | 214 | 1834 | 13 | 3 | 4 | 1 | 13 | 19 | 0.029 | 54 |  | 22.1 | 0.012 | Test results satisfactory. Acetylene gas possibly from tapchanger. | Oil quality is assessed as acceptable.
33000 | 1989 | 22 | 220 | 55 | 191 | 2327 | 9 | 3 | 4 | 1 | 12 | 11 | 0.041 | 66 |  | 17.6 | 0.016 | Test results are assessed as acceptable. | Oil quality is assessed as acceptable. PCB content below 2mg/kg.
33000 | 1989 | 22 | 327 | 55 | 294 | 2321 | 17 | 3 | 4 | 1 | 8 | 12 | 0.029 | 75 |  | 8.8 | 0.031 | Test results are assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1989 | 22 | 243 | 42 | 223 | 2807 | 8 | 4 | 4 | 2 | 2 | 8 | 0.052 | 74 |  | 8 | 0.035 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1989 | 22 | 152.6 | 51 | 140.1 | 2398 | 3.8 | 2.4 | 3.2 | 2.8 | 0.3 | 12 | 0.054 | 75 |  | 6 | 0.036 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1989 | 22 | 108.3 | 29 | 94.1 | 2282.4 | 5.2 | 2.1 | 3.5 | 1.8 | 1.6 | 5 | 0.063 | 75 |  | 7 | 0.037 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1989 | 22 | 112.5 | 32 | 98.5 | 1728 | 10.2 | 1.8 | 0 | 2 | 0 | 10 | 0.062 | 62 |  | 10.4 | 0.028 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1989 | 22 | 60 | 24 | 51.5 | 1119.2 | 5.4 | 1.2 | 0.7 | 0.9 | 0.3 | 6 | 0.066 | 75 |  | 8 | 0.0281 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1989 | 22 | 50 | 30 | 3 | 236 | 46 | 0 | 1 | 0 | 0 | 13 | 0.015 | 59 |  | 120 | 0.0063 | Test results satisfactory. | Oil quality is assessed as acceptable.
33000 | 1989 | 22 | 219 | 50 | 214 | 1812 | 0 | 3 | 2 | 0 | 0 | 10 | 0.036 | 42 |  | 16.2 | 0.016 | Test results satisfactory. | Oil quality is assessed as acceptable.
33000 | 1989 | 22 | 162 | 55 | 156 | 1932 | 1 | 2 | 2 | 1 | 0 | 21 | 0.058 | 54 |  | 14.8 | 0.017 | Test results are assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1989 | 22 | 194 | 55 | 177 | 2610 | 7 | 5 | 3 | 2 | 0 | 14 | 0.058 | 75 |  | 9 | 0.03 | 2-furfural level is high suggesting advanced rate of insulation degradation. Other test results are assessed as acceptable.
33000 | 1989 | 22 | 130.2 | 52 | 122.4 | 2121.2 | 3.2 | 2 | 1.3 | 1.3 | 0 | 10 | 0.06 | 75 |  | 6 | 0.039 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1989 | 22 | 120.9 | 25 | 105.1 | 2286.3 | 11.6 | 2 | 1.3 | 0.9 | 0 | 11 | 0.07 | 75 |  | 8 | 0.032 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1989 | 22 | 67.1 | 33 | 64 | 1794.7 | 0 | 1.5 | 0.8 | 0.8 | 0 | 14 | 0.063 | 67 |  | 8 | 0.032 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1989 | 22 | 64.2 | 30 | 49.3 | 1468.4 | 11.7 | 1.4 | 1.1 | 0.5 | 0.2 | 7 | 0.068 | 75 |  | 8.4 | 0.034 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1988 | 23 | 53 | 41 | 46 | 863 | 0 | 2 | 1 | 4 | 0 | 8 | 0.015 | 64 |  | 160 | 0.0088 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1988 | 23 | 112 | 55 | 53 | 1091 | 15 | 4 | 6 | 10 | 24 | 13 | 0.042 | 55 |  | 27.7 | 0.01 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1988 | 23 | 180 | 38 | 100 | 1304 | 35 | 3 | 6 | 3 | 33 | 13 | 0.051 | 68 |  | 8.5 | 0.031 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1988 | 23 | 260.8 | 50 | 159.9 | 2223.6 | 22.9 | 3.7 | 11.9 | 9.1 | 53.3 | 13 | 0.069 | 73 |  | 4 | 0.06 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1988 | 23 | 166.8 | 36 | 115 | 1865.3 | 16.4 | 3.1 | 4 | 5.8 | 22.5 | 15 | 0.07 | 36 |  | 8 | 0.027 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1988 | 23 | 123.8 | 30 | 80.1 | 1425.2 | 11.4 | 2.2 | 4.5 | 3.8 | 21.8 | 15 | 0.097 | 48 |  | 9 | 0.025 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1988 | 23 | 92.9 | 50 | 70.2 | 1279.6 | 6.6 | 1.7 | 1.8 | 1 | 11.6 | 11 | 0.085 | 68 |  | 10 | 0.027 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1988 | 23 | 147 | 55 | 111.1 | 1427.8 | 8.8 | 4.9 | 3.1 | 2.2 | 16.9 | 18 | 0.089 | 64 |  | 4 | 0.059 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1988 | 23 | 77.7 | 52 | 61.2 | 1205.2 | 5.6 | 1.5 | 1.4 | 0 | 8 | 16 | 0.093 | 83 |  | 6 | 0.036 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1988 | 23 | 57 | 40 | 52 | 608 | 0 | 2 | 0 | 3 | 0 | 8 | 0.004 | 68 |  | 120 | 0.0097 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1988 | 23 | 186 | 56 | 94 | 1884 | 34 | 6 | 8 | 11 | 33 | 15 | 0.108 | 56 |  | 8.9 | 0.028 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1988 | 23 | 207 | 38 | 126 | 1611 | 39 | 3 | 4 | 1 | 34 | 18 | 0.132 | 72 |  | 8.1 | 0.029 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1988 | 23 | 304.3 | 60 | 211.8 | 2435.7 | 24.6 | 3.1 | 7.6 | 1.1 | 56.1 | 12 | 0.152 | 64 |  | 3 | 0.071 | Dissolved gas analysis is assessed as acceptable. Acetylene gas possibly communicating from tapchanger. | Oil quality is assessed as acceptable.
33000 | 1988 | 23 | 165.5 | 62 | 119 | 1865.1 | 16.2 | 3.3 | 3.6 | 4.5 | 18.9 | 12 | 0.159 | 48 |  | 7 | 0.029 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1988 | 23 | 150.5 | 60 | 107.6 | 1563.6 | 13 | 2.9 | 3.8 | 1.1 | 22.1 | 11 | 0.179 | 75 |  | 8 | 0.028 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1988 | 23 | 124.4 | 50 | 95.6 | 1488.2 | 8.4 | 2.2 | 2.9 | 3.6 | 11.7 | 12 | 0.171 | 47 |  | 10 | 0.025 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1988 | 23 | 286.4 | 50 | 204.5 | 2592.9 | 17.3 | 5.7 | 15.4 | 27.9 | 15.6 | 17 | 0.18 | 63 |  | 4 | 0.055 | DGA is assessed as acceptable at present. | Oil quality is assessed as acceptable.
33000 | 1988 | 23 | 91.2 | 58 | 72.4 | 1407.6 | 7.9 | 1.7 | 1.4 | 0 | 7.8 | 16 | 0.163 | 77 |  | 9 | 0.023 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1988 | 23 | 79 | 40 | 60 | 756 | 13 | 2 | 1 | 3 | 0 | 10 | 0.013 | 72 |  | 45 | 0.017 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1988 | 23 | 173 | 30 | 70 | 1601 | 12 | 3 | 46 | 22 | 20 | 13 | 0.09 | 70 |  | 13.4 | 0.017 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1988 | 23 | 220 | 45 | 142 | 1579 | 29 | 4 | 6 | 5 | 34 | 14 | 0.113 | 61 |  | 9.1 | 0.025 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1988 | 23 | 375.5 | 60 | 261.3 | 2510.5 | 30.6 | 5.6 | 11.3 | 13.4 | 53.3 | 13 | 0.131 | 55 |  | 3 | 0.086 | Dissolved gas analysis is assessed as acceptable. Acetylene gas possibly communicating from tapchanger. | Oil quality is assessed as acceptable.
33000 | 1988 | 23 | 205.4 | 37 | 154.5 | 2032.4 | 19.7 | 4.2 | 4.1 | 4.5 | 18.4 | 15 | 0.145 | 66 |  | 6 | 0.033 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1988 | 23 | 157.8 | 35 | 113.1 | 1476 | 14.2 | 2.8 | 4 | 2.8 | 20.9 | 11 | 0.18 | 75 |  | 7 | 0.03 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1988 | 23 | 150.8 | 48 | 123 | 1527.6 | 9.3 | 2.7 | 2.7 | 1.8 | 11.3 | 14 | 0.157 | 61 |  | 7 | 0.039 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1988 | 23 | 283.3 | 48 | 227 | 1952.5 | 17.2 | 9.9 | 5.8 | 3 | 20.4 | 19 | 0.163 | 50 |  | 4 | 0.07 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1988 | 23 | 123.2 | 45 | 67.6 | 1266.1 | 19 | 2.8 | 4.9 | 0 | 28.9 | 15 | 0.146 | 86 |  | 10 | 0.02 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1987 | 24 | 354 | 50 | 309 | 2570 | 37 | 2 | 4 | 2 | 0 | 53 | 0.167 | 24 |  | 8 | 0.0397 | DGA is assessed as acceptable. | Electric strength low. Moisture level slightly high.
33000 | 1987 | 24 | 208 | 50 | 193 | 2200 | 0 | 3 | 8 | 3 | 1 | 22 | 0.147 | 54 |  | 6.7 | 0.044 | DGA is assessed as acceptable. | Previous sample appears to have been contaminated. Test results satisfactory.
33000 | 1987 | 24 | 262 | 52 | 257 | 2376 | 0 | 2 | 3 | 0 | 0 | 25 | 0.163 | 57 |  | 5.6 | 0.047 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1987 | 24 | 215 | 41.81 | 176 | 1897 | 34 | 1 | 4 | 0 | 0 | 27 | 0.157 | 33 |  | 5.3 | 0.045 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1987 | 24 | 295.1 | 50 | 275.8 | 3565.1 | 13.1 | 1.6 | 3.6 | 1 | 0 | 22 | 0.195 | 43 |  | 4 | 0.064 | DGA is assessed as acceptable. | Acidity level is trending upwards. Other test results are assessed as acceptable.
33000 | 1987 | 24 | 409.3 | 50 | 365.2 | 9677.5 | 35.1 | 3.4 | 4.6 | 1 | 0 | 69 | 0.185 | 23 |  | 3 | 0.072 | Carbon oxide levels are high. Other dissolved gas levels are assessed as acceptable. | Moisture content is very high. Oil was cloudy in appearance. Breakdown voltage is very low. Acidity level is high but stable.
33000 | 1987 | 24 | 477.7 | 36 | 447.6 | 4557.7 | 22.9 | 2.8 | 3.3 | 1.1 | 0 | 37 | 0.215 | 40 |  | 4 | 0.062 | DGA is assessed as acceptable. | Moisture content is slightly high. Acidity level is high. Other oil quality results are assessed as acceptable.
33000 | 1987 | 24 | 251.4 | 43 | 234.7 | 4395.5 | 10.7 | 2.3 | 3 | 0.7 | 0 | 35 | 0.262 | 29 |  | 2 | 0.102 | DGA is assessed as acceptable | Acidity level is high. Moisture content is high. Breakdown voltage is low. Possible sample contamination. Other oil quality results are assessed as acceptable.
33000 | 1987 | 24 | 471.2 | 50 | 425.1 | 4747.9 | 37.5 | 3.4 | 4.1 | 1.1 | 0 | 37 | 0.241 | 42 |  | 4 | 0.058 | DGA is assessed as acceptable. | Acidity level is high. Other oil quality results are assessed as acceptable.
33000 | 1987 | 24 | 11.3 | 30 | 9.1 | 594.8 | 0 | 1.7 | 0.2 | 0.1 | 0.2 | 8 | 0.005 | 92 |  | 89 | 0.007 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1987 | 24 | 16 | 19 | 13.2 | 653.4 | 1.3 | 1.1 | 0.2 | 0.1 | 0.1 | 18 | 0.011 | 80 |  | 9 | 0.034 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1987 | 24 | 12 | 41.81 | 11 | 474 | 0 | 1 | 0 | 0 | 0 | 6 | 0.004 | 95 |  | 402.5 | 0.002 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1987 | 24 | 10.9 | 18 | 7.1 | 610.1 | 2.7 | 0.8 | 0.1 | 0.1 | 0.1 | 7 | 0.005 | 54 |  | 136 | 0.005 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1986 | 25 | 785 | 41.81 | 365 | 1986 | 394 | 12 | 4 | 10 | 0 | 18 | 0.072 | 65 |  | 6.2 | 0.034 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1986 | 25 | 918.6 | 40 | 488.1 | 4248.7 | 389.5 | 16.7 | 6.2 | 17.4 | 0.7 | 16 | 0.126 | 44 |  | 4 | 0.053 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1986 | 25 | 920.5 | 38 | 531.7 | 2765.2 | 374.5 | 7.4 | 2.6 | 4.1 | 0.2 | 29 | 0.143 | 51 |  | 4 | 0.051 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1986 | 25 | 815.4 | 35 | 460.1 | 4075.1 | 345.7 | 4.6 | 2.4 | 2.6 | 0 | 23 | 0.161 | 67 |  | 4 | 0.049 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1986 | 25 | 752.8 | 33 | 467.1 | 4243.4 | 273.9 | 4.4 | 4.3 | 3.1 | 0 | 22 | 0.179 | 75 |  | 4 | 0.046 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable. Corrosive IEC. Non-corrosive ASTM 3B.
33000 | 1986 | 25 | 556.2 | 40 | 335.1 | 3819.7 | 205 | 3.9 | 4.7 | 7.5 | 0 | 27 | 0.206 | 56 |  | 4 | 0.047 | DGA is assessed as acceptable. | Acidity level is high. Other oil quality results are assessed as acceptable.
33000 | 1986 | 25 | 449.2 | 35 | 297.9 | 3495.4 | 136.7 | 6.4 | 3.5 | 4.7 | 0 | 29 | 0.189 | 36 |  | 4 | 0.052 | DGA is assessed as acceptable. | Breakdown voltage is low. Other oil quality results are assessed as acceptable.
33000 | 1986 | 25 | 914 | 35 | 426 | 2206 | 445 | 17 | 16 | 10 | 0 | 14 | 0.072 | 71 |  | 6.8 | 0.031 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1986 | 25 | 1048.7 | 40 | 517.7 | 4200.8 | 422.3 | 30.7 | 53.6 | 23.2 | 1.2 | 13 | 0.115 | 53 |  | 4 | 0.05 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1986 | 25 | 936.3 | 39 | 532 | 3790.2 | 350.4 | 17.9 | 23.1 | 12.5 | 0.4 | 23 | 0.134 | 70 |  | 4 | 0.058 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1986 | 25 | 618.4 | 35 | 369.4 | 3095.7 | 232.3 | 5.8 | 6.6 | 4.3 | 0 | 14 | 0.146 | 75 |  | 4 | 0.052 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1986 | 25 | 605.9 | 35 | 397.2 | 3217.3 | 196.6 | 4.2 | 3.7 | 3.6 | 0.6 | 16 | 0.16 | 90 |  | 3 | 0.061 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable. Corrosive IEC. Non-corrosive ASTM 3B.
33000 | 1986 | 25 | 510.1 | 40 | 333.1 | 2722.6 | 151.4 | 7.1 | 12.5 | 6 | 0 | 18 | 0.182 | 88 |  | 3 | 0.058 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1986 | 25 | 349.1 | 35 | 240.1 | 2299.1 | 96.3 | 3.9 | 6.8 | 2 | 0 | 18 | 0.167 | 73 |  | 3 | 0.065 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1986 | 25 | 143 | 41.81 | 89 | 1215 | 47 | 2 | 1 | 2 | 2 | 11 | 0.033 | 64 |  | 45 | 0.0135 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1986 | 25 | 788 | 41 | 473 | 2812 | 303 | 6 | 2 | 3 | 1 | 22 | 0.075 | 65 |  | 10.3 | 0.02 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1986 | 25 | 814 | 52 | 557 | 3464 | 242 | 7 | 3 | 3 | 2 | 25 | 0.094 | 49 |  | 7.9 | 0.027 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1986 | 25 | 1043.7 | 90 | 831.1 | 5115.3 | 184.8 | 12.6 | 7.4 | 7.2 | 0.6 | 40 | 0.162 | 34 |  | 4 | 0.052 | DGA is assessed as acceptable. | Moisture content is high. Other oil quality results are assessed as acceptable.
33000 | 1986 | 25 | 882.9 | 44 | 721.1 | 6597.8 | 138 | 10.6 | 7 | 5.7 | 0.5 | 32 | 0.17 | 38 |  | 4 | 0.068 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1986 | 25 | 907 | 45 | 745 | 6285 | 142 | 9 | 6 | 5 | 0 | 28 | 0.178 | 42 |  | 4 | 0.05 | Carbon oxide levels are high. | Oil quality is assessed as acceptable.
33000 | 1986 | 25 | 563.6 | 60 | 466 | 4393.7 | 87.8 | 4.5 | 2.1 | 3 | 0.2 | 42 | 0.16 | 30 |  | 3 | 0.066 | DGA is assessed as acceptable. | Moisture content is high. Other oil quality results are assessed as acceptable.
33000 | 1986 | 25 | 356 | 50 | 305 | 5111 | 40 | 5 | 3 | 3 | 0 | 28 | 0.187 | 49 |  | 5 | 0.045 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1986 | 25 | 413.4 | 38 | 365 | 3886.3 | 36.8 | 5.6 | 3.5 | 2.5 | 0 | 23 | 0.192 | 38 |  | 4 | 0.05 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1986 | 25 | 309 | 16.5 | 274.1 | 3469.3 | 27.6 | 3.9 | 2.6 | 0.8 | 0 | 25 | 0.194 | 75 |  | 5 | 0.05 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1986 | 25 | 295.2 | 42 | 271.9 | 3536.1 | 16 | 3.6 | 2 | 1.7 | 0 | 27 | 0.207 | 58 |  | 4 | 0.049 | DGA is assessed as acceptable. | Acidity level is high. Other oil quality results are assessed as acceptable. Non-corrosive IEC. Non-corrosive ASTM 3B.
33000 | 1986 | 25 | 189.2 | 39 | 166.2 | 2407.4 | 15 | 3 | 1.5 | 3.5 | 0 | 25 | 0.21 | 53 |  | 4 | 0.047 | DGA is assessed as acceptable. | Acidity level is high. Other oil quality results are assessed as acceptable. Corrosive IEC. Non-corrosive ASTM 3B.
33000 | 1985 | 26 | 391 | 41.81 | 305 | 2950 | 53 | 5 | 7 | 4 | 17 | 20 | 0.022 | 71 |  | 60 | 0.0077 | Test results satisfactory.
33000 | 1985 | 26 | 247 | 41.81 | 178 | 1776 | 39 | 2 | 15 | 3 | 10 | 8 | 0.04 | 47 |  | 35.9 | 0.009 | Test results satisfactory.
33000 | 1985 | 26 | 22 | 41.81 | 13 | 220 | 3 | 0 | 2 | 0 | 4 | 5 | 0.029 | 61 |  | 37.8 | 0.009 | Test results satisfactory. TX out of service.
33000 | 1985 | 26 | 498.8 | 41.81 | 437.8 | 1975.4 | 7.4 | 5 | 30.8 | 0.3 | 17.5 | 17 | 0.054 | 43 |  | 30 | 0.01 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1985 | 26 | 113 | 41.81 | 96.2 | 988.5 | 6.2 | 1.4 | 7.4 | 0 | 1.8 | 12 | 0.032 | 67 |  | 24 | 0.012 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1985 | 26 | 20.2 | 41.81 | 19.1 | 157.1 | 0 | 0.5 | 0.6 | 0 | 0 | 8 | 0.034 | 85 |  | 19 | 0.016 | Dissolved gas levels are reduced. DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1985 | 26 | 680.1 | 25 | 593.1 | 2185.6 | 24.1 | 5.8 | 33.6 | 0.6 | 22.9 | 14 | 0.061 | 70 |  | 26 | 0.01 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1985 | 26 | 21.2 | 25 | 18.1 | 174 | 2 | 0.3 | 0.6 | 0 | 0.2 | 6 | 0.033 | 77 |  | 21 | 0.013 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1985 | 26 | 164 | 30 | 112 | 1469 | 34 | 3 | 2 | 4 | 9 | 12 | 0.014 | 70 |  | 150 | 0.0046 | Test results satisfactory.
33000 | 1985 | 26 | 99 | 37 | 67 | 1580 | 14 | 2 | 5 | 3 | 8 | 9 | 0.023 | 55 |  | 35 | 0.0198 | Test results satisfactory.
33000 | 1985 | 26 | 1144 | 30 | 983 | 5116 | 81 | 13 | 14 | 8 | 45 | 15 | 0.097 | 61 |  | 9.8 | 0.03 | Carbon oxide levels have increased significantly. RECOMMEND RESAMPLE IN 1 YEAR.
33000 | 1985 | 26 | 1165 | 30 | 911 | 5370 | 129 | 9 | 17 | 4 | 95 | 30 | 0.114 | 58 |  | 13.3 | 0.017 | Gas levels have remained fairly stable. Test results satisfactory. Acetylene gas possibly from tapchanger.
33000 | 1985 | 26 | 1025 | 48 | 887 | 5125 | 89 | 8 | 13 | 4 | 24 | 19 | 0.112 | 55 |  | 9.2 | 0.024 | Test results satisfactory. Acetylene gas possibly from tapchanger.
33000 | 1985 | 26 | 862 | 48 | 676 | 6074 | 89 | 7 | 13 | 4 | 73 | 24 | 0.143 | 90 |  | 8.6 | 0.028 | 2-furfural is above 1ppm. Other test results are assessed as acceptable.
33000 | 1985 | 26 | 811 | 27 | 515 | 6711 | 111 | 8 | 21 | 5 | 151 | 18 | 0.129 | 57 |  | 12.4 | 0.02 | 2-Furfural level is very high but stable. Other test results are assessed as acceptable. RECOMMEND RESAMPLE IN 1 YEAR TO MONITOR TREND.
33000 | 1985 | 26 | 313 | 41.81 | 161 | 1719 | 36 | 4 | 12 | 2 | 98 | 12 | 0.028 | 50 |  | 40 | 0.0078 | Test results satisfactory.
33000 | 1985 | 26 | 881 | 41.81 | 715 | 1363 | 77 | 42 | 13 | 29 | 5 | 15 | 0.047 | 40 |  | 11.2 | 0.0278 | Test results satisfactory.
33000 | 1985 | 26 | 1330 | 41.81 | 1054 | 4327 | 115 | 87 | 23 | 46 | 5 | 16 | 0.099 | 54 |  | 7.6 | 0.041 | DGA comparable with substantially loaded transformer. Oil test results satisfactory.
33000 | 1985 | 26 | 1553 | 41.81 | 1221 | 4018 | 151 | 96 | 25 | 49 | 11 | 28 | 0.111 | 60 |  | 8.8 | 0.034 | DGA consistant with previous results. High CO level suggests transformer heavily loaded.
33000 | 1985 | 26 | 1602 | 41.81 | 1311 | 4296 | 146 | 83 | 19 | 34 | 9 | 9 | 0.177 | 56 |  | 5.9 | 0.053 | DGA consistent with previous results.
33000 | 1985 | 26 | 1475 | 41.81 | 1027 | 3790 | 258 | 77 | 36 | 25 | 52 | 52 | 0.233 | 39 |  | 6 | 0.047 | Moisture content of oil is very high; acidity level is slightly high. Other test results are assessed as acceptable.
33000 | 1985 | 26 | 1536 | 41.81 | 1146 | 4032 | 221 | 74 | 35 | 26 | 34 | 29 | 0.247 | 41 |  | 4.1 | 0.068 | Acidity level is slightly high. Other test results are assessed as acceptable. 2-furfural level is high.
33000 | 1985 | 26 | 1855 | 34 | 1374 | 5753 | 258 | 101 | 49 | 40 | 33 | 33 | 0.304 | 58 |  | 3.6 | 0.062 | Acidity level of oil is high. Moisture content of oil is slightly high. 2-Furfural level is stable. Other test results are assessed as acceptable.
33000 | 1985 | 26 | 2066 | 50 | 1606 | 6490 | 226 | 113 | 49 | 66 | 6 | 29 | 0.358 | 56 |  | 5 | 0.06 | Carbon dioxide; acidity and 2-furfural levels are high suggesting advanced rate of insulation degradation.
33000 | 1985 | 26 | 1391.7 | 30 | 1047 | 5831.9 | 173.8 | 71.9 | 35.1 | 53.4 | 10.5 | 21 | 0.386 | 61 |  | 3 | 0.089 | 2-furfural and acidity levels are trending upwards suggesting accelerated rate of insulation degradation. | Other test results are assessed as acceptable.
33000 | 1985 | 26 | 1236.2 | 32 | 857.9 | 4599.5 | 262.1 | 36.3 | 25.6 | 40.9 | 13.4 | 27 | 0.41 | 65 |  | 3 | 0.068 | DGA is assessed as acceptable. | Acidity level of sample is high. Other test results are assessed as acceptable.
33000 | 1985 | 26 | 1433.1 | 46 | 1095.7 | 7407.4 | 199.8 | 67 | 28.3 | 38.2 | 4.1 | 36 | 0.422 | 60 |  | 2 | 0.106 | Dissolved gas levels are relatively stable and accessed as acceptable. | Acidity level is high. Other oil quality results are assessed as acceptable.
33000 | 1985 | 26 | 1154.4 | 22 | 953 | 6207.7 | 109.2 | 46 | 21.9 | 22.7 | 1.6 | 32 | 0.464 | 43 |  | 2 | 0.129 | DGA is assessed as acceptable. | Acidity level is very high. Moisture content is high. Other oil quality results are assessed as acceptable.
33000 | 1985 | 26 | 161 | 28 | 98 | 995 | 46 | 7 | 1 | 9 | 0 | 11 | 0.01 | 64 |  | 40 | 0.013 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1985 | 26 | 146 | 27 | 38 | 1176 | 78 | 9 | 3 | 17 | 1 | 43 | 0.043 | 36 |  | 12 | 0.03 | DGA satisfactory. Moisture content of sample quite high.
33000 | 1985 | 26 | 674 | 31 | 326 | 2387 | 326 | 7 | 3 | 10 | 2 | 8 | 0.092 | 67 |  | 7.7 | 0.027 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1985 | 26 | 719 | 39 | 402 | 3341 | 276 | 14 | 9 | 18 | 0 | 20 | 0.145 | 53 |  | 3.1 | 0.068 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1985 | 26 | 578.4 | 35 | 394.3 | 4540.5 | 133 | 15.8 | 15.2 | 17.8 | 2.3 | 12 | 0.222 | 75 |  | 3 | 0.074 |  | Acidity level of sample is high. Other test results are assessed as acceptable.
33000 | 1985 | 26 | 1075 | 41 | 726.8 | 5761.6 | 219.7 | 41.2 | 64.5 | 21.2 | 1.6 | 27 | 0.251 | 64 |  | 3 | 0.089 | DGA is assessed as acceptable at present. | Acidity level is high and trending upwards. Other oil quality results are assessed as acceptable.
33000 | 1985 | 26 | 1035.3 | 57 | 821.5 | 7209.8 | 175 | 19 | 10.9 | 8.9 | 0 | 29 | 0.3195 | 75 |  | 2 | 0.1 | Carbon oxide levels are increasing. | Acidity level is high. Other oil quality results are assessed as acceptable at present.
33000 | 1985 | 26 | 2161 | 60 | 386 | 4234 | 653 | 220 | 433 | 36 | 433 | 35 | 0.281 | 36 |  | 3 | 0.071 | DGA suggests arcing has occurred. Dissolved gases possibly communicating from tapchager. | Moisture content is high. Breakdown voltage is low. Acidity level is high.
33000 | 1985 | 26 | 148 | 30 | 89 | 1046 | 50 | 4 | 1 | 4 | 0 | 13 | 0.011 | 60.7 |  | 50 | 0.0117 | DGA is assessed as acceptable.
33000 | 1985 | 26 | 98 | 27 | 27 | 1230 | 51 | 6 | 2 | 10 | 2 | 11 | 0.019 | 30 |  | 14 | 0.027 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1985 | 26 | 721 | 30 | 327 | 2245 | 376 | 6 | 2 | 8 | 2 | 6 | 0.077 | 69 |  | 8.9 | 0.025 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1985 | 26 | 740 | 41.81 | 390 | 3064 | 326 | 8 | 4 | 12 | 0 | 19 | 0.116 | 75 |  | 3.1 | 0.061 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1985 | 26 | 942.2 | 44 | 624.1 | 6922.4 | 251.8 | 15.5 | 15 | 34.3 | 1.5 | 19 | 0.174 | 42 |  | 2 | 0.128 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1985 | 26 | 943.5 | 41 | 683.9 | 5223 | 219.1 | 16.7 | 10.1 | 13.3 | 0.4 | 25 | 0.209 | 37 |  | 2 | 0.095 | DGA is assessed as acceptable. | Acidity level is high. Other oil quality results are assessed as acceptable.
33000 | 1985 | 26 | 1014.5 | 55 | 804.3 | 6388.1 | 179.9 | 16.5 | 7.3 | 6.5 | 0 | 26 | 0.271 | 55 |  | 2 | 0.086 | Dissolved gas levels are relatively stable. | Acidity level is high and increasing. Other oil quality results are assessed as acceptable.
33000 | 1985 | 26 | 643.1 | 62 | 541.2 | 5504.4 | 83.6 | 11.6 | 3.8 | 2.9 | 0 | 21 | 0.29 | 49 |  | 4 | 0.052 | DGA is assessed as acceptable. | Acidity level is high. Other oil quality results are assessed as acceptable. Corrosive IEC. Non-corrosive ASTM 3A.
33000 | 1985 | 26 | 654.4 | 65 | 558.4 | 5129.1 | 85.6 | 5.5 | 3.8 | 1.1 | 0 | 28 | 0.301 | 46 |  | 4 | 0.054 | DGA is assessed as acceptable. | Acidity level is high but stable. Other oil quality results are assessed as acceptable.
33000 | 1985 | 26 | 339 | 41 | 286.8 | 3480 | 42.1 | 4.6 | 3.5 | 2 | 0 | 24 | 0.329 | 70 |  | 4 | 0.052 | DGA is assessed as acceptable. | Acidity level is high. Other oil quality results are assessed as acceptable.
33000 | 1985 | 26 | 192.7 | 54 | 166.7 | 2435.4 | 19.8 | 2.8 | 2.5 | 0.9 | 0 | 24 | 0.303 | 64 |  | 4 | 0.046 | DGA is assessed as acceptable. | Acidity level is high. Other oil quality results are assessed as acceptable.
33000 | 1985 | 26 | 216.3 | 45 | 179.4 | 2325.6 | 21.8 | 10.7 | 3.1 | 1.3 | 0 | 22 | 0.321 | 97 |  | 4 | 0.058 | DGA is assessed as acceptable. | Acidity level is high. Other oil quality results are assessed as acceptable.
33000 | 1984 | 27 | 49 | 41.81 | 45 | 829 | 0 | 0 | 3 | 1 | 0 | 5 | 0.01 | 51 |  | 50 | 0.029 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1984 | 27 | 63 | 41.81 | 57 | 858 | 0 | 1 | 4 | 1 | 0 | 8 | 0.012 | 53 |  | 131 | 0.004 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1984 | 27 | 141 | 41.81 | 108 | 1236 | 22 | 2 | 7 | 1 | 1 | 15 | 0.019 | 42 |  | 60.4 | 0.007 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1984 | 27 | 181 | 41.81 | 135 | 1832 | 28 | 2 | 13 | 1 | 2 | 13 | 0.017 | 69 |  | 59.1 | 0.009 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1984 | 27 | 101 | 33 | 78 | 1230 | 4.8 | 1.4 | 13 | 1 | 2.8 | 1 | 0.022 | 74 |  | 27 | 0.017 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1984 | 27 | 100.6 | 45 | 81.4 | 1005.7 | 6.3 | 1.2 | 6 | 1.5 | 4.2 | 11 | 0.016 | 65 |  | 26 | 0.016 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1984 | 27 | 114 | 44 | 103.4 | 1156.6 | 6 | 1.2 | 2.6 | 0.4 | 0.4 | 8 | 0.016 | 62 |  | 33 | 0.012 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1984 | 27 | 114.3 | 52 | 102 | 1166.8 | 7.6 | 1.5 | 2.1 | 0.4 | 0.7 | 9 | 0.016 | 92 |  | 30 | 0.01 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1984 | 27 | 144.1 | 55 | 125.1 | 1423.1 | 7.1 | 8.7 | 2.5 | 0.3 | 0.4 | 9 | 0.025 | 74 |  | 33 | 0.008 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1984 | 27 | 58 | 41.81 | 55 | 751 | 0 | 1 | 1 | 1 | 0 | 5 | 0.008 | 43 |  | 30 | 0.055 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1984 | 27 | 95 | 41.81 | 82 | 992 | 7 | 2 | 1 | 2 | 1 | 6 | 0.016 | 55 |  | 35.1 | 0.009 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1984 | 27 | 661 | 41.81 | 468 | 2701 | 179 | 5 | 4 | 4 | 1 | 8 | 0.008 | 57 |  | 27.6 | 0.011 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1984 | 27 | 509 | 50 | 356 | 2697 | 136 | 5 | 5 | 3 | 4 | 10 | 0.078 | 54 |  | 11.9 | 0.017 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1984 | 27 | 531 | 46 | 415 | 4453 | 86 | 6 | 8 | 8 | 8 | 10 | 0.094 | 73 |  | 9.6 | 0.027 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1984 | 27 | 262 | 41.81 | 204 | 3819 | 28 | 8 | 9 | 7 | 6 | 12 | 0.103 | 75 |  | 7.6 | 0.03 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1984 | 27 | 189.3 | 33 | 142.8 | 1862.4 | 32 | 4.3 | 4.4 | 3.1 | 2.7 | 8 | 0.107 | 75 |  | 8 | 0.027 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1984 | 27 | 125.3 | 45 | 86 | 1284.1 | 22.2 | 2.9 | 3 | 3.4 | 7.8 | 11 | 0.093 | 75 |  | 9 | 0.025 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1984 | 27 | 143.6 | 47 | 120.7 | 1608.5 | 18.5 | 1.8 | 1.3 | 1 | 0.3 | 7 | 0.12 | 70 |  | 8 | 0.028 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1984 | 27 | 129.3 | 51 | 109.9 | 1499.4 | 14.7 | 1.7 | 1 | 1.1 | 0.9 | 10 | 0.111 | 94 |  | 9 | 0.026 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1984 | 27 | 236.5 | 45 | 203.7 | 2042.8 | 22.1 | 8.3 | 1 | 0.8 | 0.6 | 12 | 0.124 | 68 |  | 9 | 0.023 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1984 | 27 | 57 | 29 | 55 | 640 | 0 | 0 | 0 | 1 | 1 | 5 | 0.036 | 63 |  | 50 | 0.031 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1984 | 27 | 302 | 35 | 197 | 1157 | 100 | 2 | 1 | 1 | 1 | 11 | 0.031 | 71 |  | 41 | 0.008 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1984 | 27 | 393 | 41.81 | 260 | 1856 | 128 | 2 | 2 | 1 | 0 | 10 | 0.052 | 54 |  | 13 | 0.018 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1984 | 27 | 484.1 | 43 | 352 | 3361 | 117 | 4.5 | 5.3 | 2.6 | 2.7 | 7 | 0.086 | 75 |  | 7 | 0.041 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1984 | 27 | 461.4 | 55 | 377.1 | 2877.9 | 74.5 | 4.9 | 1.5 | 3 | 0.4 | 14 | 0.09 | 41 |  | 9 | 0.025 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1984 | 27 | 246.8 | 55 | 200.2 | 1907.4 | 34.2 | 5.1 | 2.5 | 3.9 | 0.9 | 12 | 0.114 | 75 |  | 9 | 0.028 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1984 | 27 | 215.1 | 42 | 174.8 | 1788.5 | 32.3 | 2.8 | 1.8 | 1.5 | 1.9 | 10 | 0.112 | 65 |  | 10 | 0.021 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1984 | 27 | 156.1 | 63 | 131 | 1834.4 | 13.7 | 2.3 | 5 | 2.7 | 1.4 | 14 | 0.137 | 76 |  | 11 | 0.02 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1984 | 27 | 178.9 | 65 | 151.4 | 1729 | 17.8 | 6.8 | 1.8 | 0.4 | 0.7 | 20 | 0.121 | 61 |  | 11 | 0.02 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1984 | 27 | 86 | 36 | 58 | 815 | 22 | 2 | 2 | 2 | 0 | 7 | 0.013 | 67 |  | 20 | 0.037 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1984 | 27 | 461 | 46 | 312 | 1486 | 132 | 3 | 3 | 10 | 1 | 19 | 0.052 | 59 |  | 8.8 | 0.025 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1984 | 27 | 390 | 60 | 223 | 1848 | 156 | 3 | 2 | 5 | 1 | 13 | 0.089 | 60 |  | 7.7 | 0.025 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1984 | 27 | 426 | 41.81 | 300 | 2426 | 115 | 4 | 3 | 2 | 2 | 14 | 0.113 | 71 |  | 9.5 | 0.023 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1984 | 27 | 755.8 | 56 | 575.3 | 3541.4 | 159.6 | 7.3 | 6.4 | 6.3 | 0.9 | 11 | 0.176 | 73 |  | 5 | 0.043 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1984 | 27 | 511.3 | 37 | 413.4 | 3627.4 | 77.7 | 8.3 | 6.2 | 5.3 | 0.4 | 21 | 0.187 | 45 |  | 4 | 0.06 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1984 | 27 | 377 | 43 | 302.7 | 3582.4 | 59.7 | 5.4 | 4.2 | 3.8 | 1.2 | 17 | 0.208 | 75 |  | 5 | 0.044 | DGA is assessed as acceptable. | Acidity level is high. Other oil quality results are assessed as acceptable.
33000 | 1984 | 27 | 289.3 | 44 | 240.1 | 2369 | 42.5 | 3.6 | 1.4 | 1.3 | 0.4 | 13 | 0.22 | 75 |  | 5 | 0.041 | DGA is assessed as acceptable. | Acidity level is high. Other oil quality results are assessed as acceptable.
33000 | 1984 | 27 | 289.2 | 56 | 247.3 | 2482.8 | 37.6 | 0.9 | 0.8 | 2 | 0.6 | 14 | 0.226 | 75 |  | 5 | 0.045 | DGA is assessed as acceptable. | Acidity level is high. Other oil quality results are assessed as acceptable. Non-corrosive IEC. Non-corrosive ASTM 3A.
33000 | 1984 | 27 | 342.4 | 45 | 301.1 | 2930.9 | 28.6 | 5.9 | 3.3 | 2.9 | 0.6 | 16 | 0.241 | 100 |  | 5 | 0.042 | DGA is assessed as acceptable. | Acidity level is high. Other oil quality results are assessed as acceptable.
33000 | 1984 | 27 | 230.4 | 50 | 194.5 | 2539.4 | 25.1 | 3.4 | 3.9 | 3.5 | 0 | 19 | 0.229 | 88 |  | 5 | 0.04 | DGA is assessed as acceptable. | Acidity level is high. Other oil quality results are assessed as acceptable.
33000 | 1984 | 27 | 82 | 30 | 65 | 797 | 12 | 2 | 1 | 2 | 0 | 9 | 0.047 | 73 |  | 60 | 0.026 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1984 | 27 | 145 | 32 | 86 | 929 | 56 | 1 | 1 | 1 | 0 | 20 | 0.02 | 53 |  | 60.6 | 0.006 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1984 | 27 | 303 | 45 | 193 | 1418 | 103 | 2 | 2 | 2 | 1 | 11 | 0.034 | 58 |  | 32.1 | 0.014 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1984 | 27 | 352 | 41.81 | 230 | 1752 | 116 | 2 | 2 | 1 | 1 | 10 | 0.063 | 66 |  | 14.9 | 0.016 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1984 | 27 | 380.9 | 26 | 290.3 | 2910 | 77.8 | 3.4 | 3.8 | 2.5 | 3.1 | 8 | 0.091 | 55 |  | 6 | 0.044 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1984 | 27 | 527.3 | 60 | 431.2 | 3301.3 | 86.1 | 3.9 | 3.1 | 2 | 1 | 12 | 0.098 | 59 |  | 9 | 0.025 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1984 | 27 | 249.8 | 54 | 203.7 | 1981.2 | 35.5 | 4.8 | 2.4 | 2.5 | 0.9 | 12 | 0.12 | 70 |  | 10 | 0.025 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1984 | 27 | 221.7 | 45 | 178.2 | 1799.2 | 36.2 | 2.4 | 1.4 | 1 | 2.5 | 10 | 0.117 | 75 |  | 10 | 0.023 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1984 | 27 | 151.7 | 62 | 130.8 | 1793.2 | 12.6 | 2.9 | 3 | 1.4 | 1 | 17 | 0.145 | 47 |  | 12 | 0.02 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1984 | 27 | 159.9 | 65 | 138.6 | 1657.4 | 15.7 | 2.9 | 1.5 | 0.6 | 0.6 | 23 | 0.128 | 51 |  | 11 | 0.02 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1984 | 27 | 182 | 35 | 90 | 974 | 56 | 5 | 8 | 4 | 19 | 9 | 0.036 | 73 |  | 70 | 0.0233 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1984 | 27 | 551 | 43 | 294 | 1755 | 100 | 10 | 16 | 10 | 121 | 11 | 0.043 | 42 |  | 19.1 | 0.018 | DGA is assessed as acceptable. Acetylene gas possibly communicating from tapchanger. | Oil quality is assessed as acceptable.
33000 | 1984 | 27 | 1247 | 43 | 818 | 3286 | 155 | 81 | 48 | 53 | 92 | 29 | 0.079 | 39 |  | 6.8 | 0.062 | Moisture and gas levels increased significantly. RECOMMEND RESAMPLE IN 1 YEAR.
33000 | 1984 | 27 | 1526 | 70 | 1053 | 3445 | 118 | 129 | 49 | 116 | 61 | 31 | 0.129 | 63 |  | 3.1 | 0.098 | Ethane gas level increasing. RECOMMEND RESAMPLE IN 1 YEAR TO MONITOR TREND.
33000 | 1984 | 27 | 1768 | 41 | 1317 | 5244 | 90 | 129 | 54 | 150 | 28 | 19 | 0.151 | 58 |  | 3 | 0.108 | Ethane gas level increasing suggest oil overheating. Other test results are assessed as acceptable. RECOMMEND RESAMPLE IN 1 YEAR TO MONITOR TREND.
33000 | 1984 | 27 | 1596 | 44 | 1105 | 5115 | 145 | 113 | 53 | 111 | 69 | 24 | 0.185 | 75 |  | 3 | 0.113 | Ethane gas level has reduced. Other test results are assessed as acceptable. RECOMMEND RESAMPLE IN 1 YEAR TO MONITOR TREND.
33000 | 1984 | 27 | 1948.1 | 47 | 1425.8 | 8450.6 | 123.5 | 133.6 | 92.8 | 152.9 | 19.5 | 22 | 0.274 | 51 |  | 2 | 0.149 | DGA is assessed as acceptable. Acetylene gas possibly communicating from tapchanger. | Acidity level of sample is very high. Other test results are assessed as acceptable.
33000 | 1984 | 27 | 2130.3 | 60 | 1549.8 | 9614.8 | 220 | 159.2 | 65.9 | 120.7 | 14.7 | 44 | 0.34 | 31 |  | 2 | 0.159 | Hydrogen and methane levels are trending upwards. Dissolved gas analysis suggests mild oil overheating has occurred. | Moisture content of sample is high. Acidity level of sample is high.
33000 | 1984 | 27 | 2210.8 | 60 | 1647.9 | 9121.9 | 224.9 | 163.3 | 52.1 | 106.8 | 15.8 | 43 | 0.345 | 31 |  | 2 | 0.1 | Dissolved gas analysis and oil quality is consistent with main tank sample.
33000 | 1984 | 27 | 1780.4 | 43 | 1359.1 | 7165.9 | 202.8 | 88.6 | 38.3 | 61 | 30.6 | 27 | 0.36 | 66 |  | 2 | 0.092 | Dissolved gas levels are relatively stable. | Acidity level is high. Other oil quality results are assessed as acceptable.
33000 | 1984 | 27 | 1888.8 | 43 | 1474.4 | 7274.7 | 218 | 103.5 | 27.8 | 48.2 | 16.9 | 24 | 0.425 | 51 |  | 2 | 0.094 | DGA is assessed as acceptable. | Acidity level is very high. Other oil quality results are assessed as acceptable at present.
33000 | 1984 | 27 | 1424.8 | 70 | 1144.8 | 7026.5 | 123.1 | 69.1 | 26.9 | 51.4 | 9.5 | 35 | 0.434 | 44 |  | 3 | 0.083 | DGA is assessed as acceptable. | Acidity level is high. Other oil quality results are assessed as acceptable. Corrosive IEC. Non-corrosive ASTM 3B
33000 | 1984 | 27 | 1612 | 40 | 1314.3 | 7059 | 163.1 | 67.4 | 24 | 39.5 | 3.7 | 30 | 0.298 | 88 |  | 4 | 0.058 | DGA is assessed as acceptable. | Acidity level is high. Other oil quality results are assessed as acceptable.
33000 | 1984 | 27 | 1192.2 | 39 | 963.6 | 6317.1 | 166.9 | 26.6 | 16.6 | 16.6 | 1.9 | 36 | 0.571 | 93 |  | 4 | 0.059 | DGA is assessed as acceptable. | Acidity level is high. Other oil quality results are assessed as acceptable.
33000 | 1984 | 27 | 1087 | 36 | 858 | 3703 | 128 | 33 | 25 | 25 | 18 | 13 | 0.067 | 59 |  | 9.7 | 0.032 | CO level quite high. Is transformer highly loaded ?
33000 | 1984 | 27 | 1346 | 34 | 1086 | 5670 | 72 | 73 | 31 | 57 | 27 | 29 | 0.092 | 49 |  | 6 | 0.05 | CO level quite high. DGA suggests slight overheating. RECOMMEND RESAMPLE IN 1 YEAR.
33000 | 1984 | 27 | 1490 | 60 | 1269 | 5845 | 81 | 55 | 32 | 33 | 20 | 22 | 0.158 | 44 |  | 2.9 | 0.102 | Gas levels have remained stable. RECOMMEND RESAMPLE IN 1 YEAR.
33000 | 1984 | 27 | 1425 | 60 | 1207 | 5078 | 106 | 54 | 21 | 16 | 21 | 28 | 0.234 | 43 |  | 4.2 | 0.065 | Acidity level is slightly high. 2-Furfural level is above 1PPM. Other test results are assessed as acceptable.
33000 | 1984 | 27 | 1563 | 44 | 1230 | 5100 | 187 | 55 | 39 | 25 | 27 | 20 | 0.303 | 75 |  | 4 | 0.061 | Acidity and 2-furfural level is high suggesting advanced rate of insulation degradation. Other test results are assessed as acceptable. RECOMMEND RESAMPLE IN 1 YEAR TO MONITOR TREND.
33000 | 1984 | 27 | 1518.3 | 50 | 1173.2 | 6830.3 | 181.5 | 63.1 | 43.7 | 30.3 | 26.5 | 36 | 0.303 | 27 |  | 2 | 0.143 | Oil and insulation condition is degraded. RECOMMEND RESAMPLE IN 1 YEAR TO MONITOR TREND.
33000 | 1984 | 27 | 1684 | 48 | 1360 | 9584 | 200 | 38 | 40 | 31 | 15 | 22 | 0.312 | 34 |  | 3 | 0.076 | Oil and insulation condition is poor. RECOMMEND RESAMPLE IN 1 YEAR TO MONITOR CONDITION.
33000 | 1984 | 27 | 1640.4 | 46 | 1330.7 | 7638.2 | 189.1 | 60.6 | 21.6 | 27.6 | 10.8 | 32 | 0.366 | 63 |  | 4 | 0.072 | DGA is assessed as acceptable. | Moisture content is slightly high. Acidity level is high. Other oil quality results are assessed as acceptable.
33000 | 1984 | 27 | 1555.4 | 50 | 1276.9 | 8205.6 | 151.6 | 62.7 | 22.8 | 29.1 | 12.3 | 32 | 0.411 | 58 |  | 4 | 0.06 | DGA is assessed as acceptable. | Acidity level is high. Other oil quality results are assessed as acceptable.
33000 | 1984 | 27 | 1561.4 | 43 | 1277.5 | 7506.8 | 174.3 | 54.4 | 19.5 | 20.1 | 15.6 | 28 | 0.456 | 45 |  | 3 | 0.08 | DGA is assessed as acceptable. | Acidity level is high. Other oil quality results are assessed as acceptable.
33000 | 1984 | 27 | 1387 | 60 | 1148.1 | 7192.5 | 129.7 | 38.9 | 26.3 | 25 | 19 | 29 | 0.431 | 66 |  | 4 | 0.071 | DGA is assessed as acceptable. | Acidity level is high. Other oil quality results are assessed as acceptable. Corrosive IEC. Non-corrosive ASTM 3B.
33000 | 1984 | 27 | 901.6 | 41.81 | 764.6 | 6171.1 | 93.1 | 9 | 10.9 | 10.4 | 13.6 | 30 | 0.43 | 65 |  | 3 | 0.069 | DGA is assessed as acceptable. | Acidity level is high. Other oil quality results are assessed as acceptable.
33000 | 1984 | 27 | 555.7 | 50 | 435.9 | 4271.7 | 79 | 5 | 9.3 | 2.8 | 23.7 | 31 | 0.474 | 38 |  | 5 | 0.048 | DGA is assessed as acceptable. | Acidity level is high. Breakdown voltage is slightly low. DDF and Resistivity are assessed as acceptable.
33000 | 1984 | 27 | 638.6 | 39 | 507.7 | 4943.5 | 78.7 | 7.3 | 13.6 | 8.7 | 22.6 | 33 | 0.459 | 59 |  | 4 | 0.057 | DGA is assessed as acceptable. | Acidity level is high. Other oil quality results are assessed as acceptable.
33000 | 1983 | 28 | 251 | 46 | 185 | 1299 | 52 | 2 | 3 | 2 | 7 | 10 | 0.028 | 71 |  | 90 | 0.0056 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1983 | 28 | 193 | 55 | 164 | 1671 | 11 | 2 | 4 | 2 | 10 | 8 | 0.026 | 57 |  | 40 | 0.01 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1983 | 28 | 347 | 50 | 154 | 1383 | 56 | 5 | 10 | 1 | 121 | 11 | 0.05 | 50 |  | 28 | 0.011 | DGA is assessed as acceptable. Acetylene gas possibly communicating from tapchanger. | Oil quality is assessed as acceptable.
33000 | 1983 | 28 | 564 | 41.81 | 323 | 2556 | 69 | 4 | 20 | 2 | 146 | 9 | 0.062 | 62 |  | 18.3 | 0.012 | DGA is assessed as acceptable. Acetylene gas possibly communicating from tapchanger. | Oil quality is assessed as acceptable.
33000 | 1983 | 28 | 587.7 | 54 | 439.8 | 2346.1 | 48.6 | 4.7 | 13.2 | 6.3 | 75.1 | 10 | 0.097 | 70 |  | 7 | 0.037 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1983 | 28 | 548.8 | 45 | 413.6 | 4008.7 | 45.1 | 4.8 | 12 | 5.5 | 67.8 | 10 | 0.096 | 74 |  | 7 | 0.036 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1983 | 28 | 706.6 | 45 | 578.9 | 4810.2 | 57.3 | 4.9 | 10.1 | 4.9 | 50.5 | 14 | 0.115 | 65 |  | 5 | 0.044 | The test results are consistent with main tank sample and are assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1983 | 28 | 697.8 | 45 | 571.4 | 4814.7 | 59.3 | 4.5 | 10 | 4.9 | 47.7 | 14 | 0.11 | 54 |  | 6 | 0.035 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1983 | 28 | 296.4 | 39 | 223.3 | 2566.7 | 24.5 | 3.1 | 6.6 | 3 | 35.9 | 13 | 0.098 | 75 |  | 8 | 0.035 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1983 | 28 | 220.2 | 38 | 175.4 | 1998.2 | 21.7 | 2.5 | 2.5 | 1.2 | 16.9 | 7 | 0.104 | 75 |  | 8 | 0.026 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1983 | 28 | 178.8 | 38 | 153.9 | 1821.7 | 8.8 | 3.6 | 1.9 | 0.9 | 9.7 | 9 | 0.111 | 90 |  | 9 | 0.03 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable. Non-corrosive IEC. Non-corrosive ASTM 3B.
33000 | 1983 | 28 | 185.1 | 37 | 166.7 | 1993.5 | 8.3 | 2.9 | 2.1 | 1.7 | 3.4 | 11 | 0.11 | 95 |  | 8 | 0.03 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1983 | 28 | 219 | 38 | 182.2 | 2508.4 | 9 | 11 | 8.6 | 1.8 | 6.4 | 13 | 0.11 | 85 |  | 8 | 0.027 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1983 | 28 | 918 | 40 | 495 | 1709 | 90 | 94 | 40 | 182 | 17 | 17 | 0.019 | 63 |  | 13 | 0.053 | Ethane level slightly high. Could indicate slight overheating. | Oil quality is assessed as acceptable.
33000 | 1983 | 28 | 1328 | 45 | 778 | 2365 | 90 | 135 | 49 | 260 | 16 | 16 | 0.052 | 64 |  | 5 | 0.0967 | Gas analysis shows slight overheating taking place. | Oil quality is assessed as acceptable.
33000 | 1983 | 28 | 1237 | 55 | 929 | 2472 | 0 | 95 | 34 | 176 | 3 | 26 | 0.074 | 54 |  | 5 | 0.097 | Gas analysis indicates slight overheating though gas levels stable. CO quite high for age. | Oil quality is assessed as acceptable.
33000 | 1983 | 28 | 1010 | 50 | 669 | 1897 | 53 | 107 | 30 | 136 | 15 | 27 | 0.107 | 51 |  | 3.5 | 0.135 | Gas levels stable. Oil oxidising at a higher than normal rate. NOTE low level of oxygen in oil. | Oil quality is assessed as acceptable.
33000 | 1983 | 28 | 1468 | 51 | 978 | 3365 | 70 | 154 | 47 | 199 | 20 | 25 | 0.147 | 57 |  | 2.5 | 0.173 | Refer previous comments. | Oil quality is assessed as acceptable.
33000 | 1983 | 28 | 456 | 51 | 374 | 1636 | 20 | 9 | 30 | 9 | 14 | 16 | 0.02 | 65 |  | 27 | 0.023 | Gas levels and acidity reduced after oil change. | Oil quality is assessed as acceptable.
33000 | 1983 | 28 | 480 | 52 | 381 | 3250 | 14 | 4 | 59 | 4 | 18 | 18 | 0.028 | 63 |  | 28.2 | 0.017 | Test results satisfactory. | Oil quality is assessed as acceptable.
33000 | 1983 | 28 | 468 | 50 | 318 | 3106 | 20 | 4 | 55 | 1 | 70 | 24 | 0.048 | 58 |  | 14.6 | 0.014 | Test results are assessed as acceptable at present. | Oil quality is assessed as acceptable.
33000 | 1983 | 28 | 630 | 45 | 415 | 3843 | 25 | 5 | 69 | 2 | 114 | 19 | 0.056 | 56 |  | 14.4 | 0.028 | Test results are assessed as acceptable. Acetylene gas possibly from tapchanger. | Oil quality is assessed as acceptable.
33000 | 1983 | 28 | 618 | 42 | 432 | 4547 | 13 | 5 | 72 | 2 | 94 | 25 | 0.064 | 61 |  | 10.2 | 0.026 | Test results are assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1983 | 28 | 731 | 54 | 606 | 4520 | 17 | 7 | 73 | 2 | 26 | 19 | 0.084 | 75 |  | 12 | 0.028 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1983 | 28 | 780.4 | 58 | 639.1 | 6099.2 | 23.8 | 5.6 | 73.8 | 3.3 | 34.8 | 26 | 0.094 | 54 |  | 9 | 0.039 | Acetylene gas possibly from tapchanger. | Other test results are assessed as acceptable.
33000 | 1983 | 28 | 1043.9 | 60 | 869.7 | 7538.7 | 43.9 | 5 | 76.8 | 4 | 44.5 | 42 | 0.101 | 39 |  | 11.3854 | 0.028468 | Carbon oxide levels are trending upwards. | Moisture content of sample is high. Other test results are assessed as acceptable.
33000 | 1983 | 28 | 633.3 | 50 | 525.2 | 4702.4 | 14.2 | 4.5 | 48 | 2.9 | 38.5 | 27 | 0.097 | 75 |  | 8 | 0.034 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1983 | 28 | 510.3 | 49 | 416.6 | 4101.8 | 16.7 | 3.9 | 40.1 | 0 | 33 | 19 | 0.146 | 40 |  | 6 | 0.041 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1983 | 28 | 554.8 | 70 | 455 | 3817.3 | 17.7 | 3.9 | 39.2 | 2.4 | 36.6 | 22 | 0.116 | 46 |  | 7 | 0.039 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1983 | 28 | 556.9 | 53 | 481 | 4355.6 | 14.9 | 3 | 38.3 | 1.5 | 18.2 | 28 | 0.163 | 37 |  | 5 | 0.05 | DGA is assessed as acceptable. | Breakdown voltage is low. Other oil quality results are assessed as acceptable. Corrosive IEC. Non-corrosive ASTM 2E.
33000 | 1983 | 28 | 466 | 75 | 377.8 | 3486.1 | 14.7 | 9.7 | 30.8 | 1 | 32 | 32 | 0.144 | 38 |  | 7 | 0.035 | DGA is assessed as acceptable. | Breakdown voltage is slightly low. Other oil quality results are assessed as acceptable.
33000 | 1983 | 28 | 777 | 41.81 | 493 | 1743 | 146 | 50 | 21 | 56 | 11 | 15 | 0.029 | 68 |  | 12 | 0.0356 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1983 | 28 | 1253 | 41.81 | 851 | 4018 | 96 | 104 | 55 | 108 | 39 | 35 | 0.214 | 42 |  | 4 | 0.058 | DGA is assessed as acceptable. | Acidity level higher than expected. Other test results satisfactory.
33000 | 1983 | 28 | 1708 | 41.81 | 1169 | 5327 | 189 | 117 | 72 | 106 | 55 | 32 | 0.273 | 46 |  | 1.8 | 0.159 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1983 | 28 | 1484 | 50 | 1050 | 5309 | 159 | 99 | 62 | 78 | 36 | 32 | 0.307 | 69 |  | 2.5 | 0.114 | DGA is assessed as acceptable. | Acidity level of oil is high.
33000 | 1983 | 28 | 1983.8 | 50 | 1503.1 | 13338.2 | 169.3 | 95 | 70.1 | 133.3 | 13 | 35 | 0.367 | 32 |  | 2 | 0.121 | Carbon dioxide level is very high. Acetylene gas possibly from tapchanger. | Moisture content of sample is high. Acidity level of sample is high.
33000 | 1983 | 28 | 1653.3 | 68 | 1311.2 | 7578 | 141.9 | 112 | 30.6 | 56 | 1.6 | 42 | 0.449 | 44 |  | 2 | 0.152 | DGA is assessed as acceptable. | Oil quality is poor. Sample is cloudy in appearance.
33000 | 1983 | 28 | 2056.3 | 50 | 1610.8 | 8034 | 198.9 | 141.9 | 35.5 | 64.4 | 4.8 | 42 | 0.477 | 65 |  | 2 | 0.121 | DGA is assessed as acceptable. | Moisture content is high. Acidity level is high. Other oil quality results are assessed as acceptable.
33000 | 1983 | 28 | 1482.7 | 41 | 1177.1 | 6113.6 | 195 | 53.4 | 23 | 27.9 | 6.3 | 30 | 0.499 | 71 |  | 2 | 0.114 | DGA is assessed as acceptable. | Acidity level is high. Other oil quality results are assessed as acceptable.
33000 | 1983 | 28 | 1345.3 | 50 | 1026.8 | 6034 | 209.5 | 63 | 18.5 | 26.2 | 1.3 | 34 | 0.609 | 40 |  | 2 | 0.098 | DGA is assessed as acceptable. | Acidity level is high. Other oil quality results are assessed as acceptable. Corrosive IEC. Non-corrosive ASTM 3A.
33000 | 1983 | 28 | 1457.4 | 28 | 1135.5 | 6112.9 | 222.2 | 55.8 | 19.2 | 22.7 | 2 | 22 | 0.584 | 67 |  | 3 | 0.087 | DGA is assessed as acceptable. | Acidity level is high. Other oil quality results are assessed as acceptable.
33000 | 1983 | 28 | 363 | 41.81 | 205 | 1694 | 102 | 5 | 7 | 6 | 38 | 15 | 0.026 | 58 |  | 100 | 0.0053 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1983 | 28 | 1074 | 41.81 | 771 | 3592 | 76 | 75 | 33 | 100 | 19 | 20 | 0.023 | 58 |  | 3.3 | 0.102 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1983 | 28 | 1349 | 41.81 | 953 | 3198 | 109 | 112 | 36 | 122 | 17 | 26 | 0.159 | 55 |  | 1.9 | 0.143 | DGA is assessed as acceptable. | Acidity level higher than expected. Other test results satisfactory.
33000 | 1983 | 28 | 1380 | 50 | 1007 | 5047 | 124 | 93 | 41 | 80 | 35 | 27 | 0.228 | 75 |  | 3 | 0.099 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1983 | 28 | 1789.5 | 50 | 1385.7 | 11444.5 | 146.7 | 82.2 | 54.5 | 110 | 10.4 | 32 | 0.365 | 34 |  | 2 | 0.122 | Carbon dioxide level is high. | Moisture content of sample is high. Acidity level of sample is high.
33000 | 1983 | 28 | 1630.9 | 37 | 1330.4 | 6482.8 | 135.8 | 94.6 | 23.4 | 45.3 | 1.4 | 34 | 0.374 | 41 |  | 2 | 0.094 | DGA is assessed as acceptable. | Acidity level is high. Other oil quality results are assessed as acceptable. Sample is cloudy in appearance.
33000 | 1983 | 28 | 1922.7 | 48 | 1553.6 | 5126 | 183.7 | 106.6 | 28.9 | 44.8 | 5.1 | 33 | 0.389 | 75 |  | 2 | 0.09 | DGA is assessed as acceptable. | Acidity level is high. Other oil quality results are assessed as acceptable.
33000 | 1983 | 28 | 1236.2 | 43 | 996 | 6357.8 | 165.1 | 23.2 | 19.3 | 18.8 | 13.8 | 21 | 0.421 | 56 |  | 3 | 0.089 | DGA is assessed as acceptable. | Acidity level is high. Other oil quality results are assessed as acceptable.
33000 | 1983 | 28 | 1202.8 | 50 | 916 | 5949.3 | 236.7 | 20.2 | 12.3 | 11.4 | 6.2 | 31 | 0.527 | 45 |  | 3 | 0.081 | DGA is assessed as acceptable. | Acidity level is high. Other oil quality results are assessed as acceptable. Non-corrosive IEC. Non-corrosive ASTM 3B.
33000 | 1983 | 28 | 1123.6 | 26 | 888.1 | 5831.4 | 192.9 | 14.2 | 12.3 | 8.3 | 7.8 | 21 | 0.5 | 67 |  | 4 | 0.064 | DGA is assessed as acceptable. | Acidity level is high. Other oil quality results are assessed as acceptable.
33000 | 1983 | 28 | 1185 | 25 | 888 | 3330 | 78 | 85 | 30 | 73 | 31 | 23 | 0.215 | 49 |  | 1.6 | 0.189 | Acidity level of oil is high. Other test results are assessed as acceptable.
33000 | 1983 | 28 | 1534 | 50 | 1154 | 5464 | 135 | 95 | 46 | 92 | 12 | 21 | 0.256 | 62 |  | 1.8 | 0.141 | Acidity level is high. Other test results are assessed as acceptable.
33000 | 1983 | 28 | 1865.2 | 45 | 1430.5 | 10087 | 121.3 | 87.2 | 59.1 | 144 | 23.1 | 27 | 0.344 | 34 |  | 2 | 0.121 | Acidity level of sample is high. Carbon dioxide level is high. Acetylene gas possibly from tapchanger. RECOMMEND RESAMPLE IN 1 YEAR TO MONITOR CONDITION.
33000 | 1983 | 28 | 1967.9 | 60 | 1460.9 | 8565.8 | 196.7 | 140.3 | 43.3 | 121.6 | 5.1 | 33 | 0.382 | 55 |  | 2 | 0.122 | Dissolved gas analysis is assessed as acceptable. Moisture content of sample is slightly high. Acidity level of sample is high. 2-furfural level is trending upwards. 2-furfural level is high for transformer age. RECOMMEND OIL CHANGE / TREATMENT. RE
33000 | 1983 | 28 | 217.4 | 43 | 160.9 | 1132.4 | 41.6 | 5.3 | 3.5 | 6.1 | 0 | 8 | 0.01 | 75 |  | 20.3 | 0.042 | Dissolved hydrocarbon gas levels have decreased after oil change. | Oil quality is assessed as acceptable.
33000 | 1983 | 28 | 345 | 24 | 281.7 | 1944.1 | 55.4 | 0.7 | 3.7 | 1.1 | 2.4 | 30 | 0.435 | 48 |  | 3 | 0.092 | DGA is assessed as acceptable. | Acidity level is high. Breakdown voltage, DDF and Resistivity are assessed as acceptable.
33000 | 1983 | 28 | 1 | 41.81 | 0 | 511 | 0 | 0 | 0 | 1 | 0 | 7 | 0.023 | 64 |  | 187.4 | 0.007 | Test results are assessed as acceptable.
33000 | 1983 | 28 | 10.5 | 25 | 8.3 | 638.3 | 0 | 0.8 | 1.3 | 0.1 | 0 | 6 | 0.015 | 87 |  | 123 | 0.011 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1983 | 28 | 5 | 41.81 | 3 | 660 | 0 | 1 | 1 | 0 | 0 | 10 | 0.012 | 65 |  | 138.6 | 0.012 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1983 | 28 | 349 | 41.81 | 33 | 861 | 201 | 42 | 10 | 63 | 0 | 15 | 0.028 | 39 |  | 2.9 | 0.079 | Test results are assessed as acceptable. 2-Furfural = ND
33000 | 1983 | 28 | 73 | 41.81 | 55 | 948 | 2 | 3 | 11 | 2 | 0 | 17 | 0.031 | 46 |  | 9.6 | 0.037 | Test results are assessed as acceptable.
33000 | 1983 | 28 | 109 | 36 | 63 | 813 | 39 | 2 | 2 | 3 | 0 | 9 | 0.015 | 53 |  | 30 | 0.033 | Dissolved gas analysis is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1983 | 28 | 370 | 44 | 275 | 1275 | 88 | 1 | 3 | 2 | 1 | 9 | 0.049 | 56 |  | 26.4 | 0.014 | Dissolved gas analysis is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1983 | 28 | 177 | 40 | 127 | 1190 | 42 | 3 | 1 | 4 | 0 | 13 | 0.04 | 64 |  | 45.4 | 0.008 | Dissolved gas analysis is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1983 | 28 | 500 | 60 | 340 | 2312 | 153 | 2 | 2 | 2 | 1 | 13 | 0.045 | 69 |  | 23.4 | 0.012 | Dissolved gas analysis is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1983 | 28 | 411 | 41.81 | 305 | 2688 | 91 | 6 | 4 | 4 | 1 | 11 | 0.094 | 66 |  | 13.1 | 0.018 | Dissolved gas analysis is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1983 | 28 | 553.9 | 54 | 434.1 | 2705.9 | 86.9 | 11.2 | 9.4 | 10.9 | 1.4 | 13 | 0.122 | 68 |  | 6 | 0.044 | Dissolved gas analysis is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1983 | 28 | 321 | 38 | 274 | 2614.7 | 31 | 6.7 | 5 | 4 | 0.3 | 23 | 0.12 | 40 |  | 5.3 | 0.053 | Dissolved gas analysis is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1983 | 28 | 212.5 | 43 | 182.3 | 2454 | 22.5 | 2.8 | 2.5 | 1.7 | 0.7 | 13 | 0.136 | 75 |  | 10 | 0.024 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1983 | 28 | 156.1 | 45 | 137.5 | 1627.1 | 14.6 | 2 | 0.9 | 0.6 | 0.5 | 9 | 0.157 | 75 |  | 6 | 0.032 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1983 | 28 | 244 | 54 | 217 | 1884.3 | 16 | 8.3 | 0.9 | 1 | 0.8 | 10 | 0.14 | 70 |  | 10 | 0.025 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable. Corrosive IEC. Non-corrosive ASTM 3B.
33000 | 1983 | 28 | 195.7 | 46 | 176.3 | 2236.3 | 14.4 | 2.1 | 1.5 | 0.9 | 0.5 | 13 | 0.155 | 94 |  | 9 | 0.026 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1983 | 28 | 152.8 | 49 | 133.1 | 1889.7 | 14.5 | 1.6 | 2.2 | 0.9 | 0.5 | 12 | 0.142 | 99 |  | 9 | 0.026 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1982 | 29 | 131 | 30 | 72 | 1047 | 29 | 2 | 4 | 2 | 22 | 11 | 0.011 | 68 |  | 70 | 0.01 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1982 | 29 | 98 | 25 | 55 | 1393 | 11 | 1 | 10 | 1 | 20 | 8 | 0.023 | 62 |  | 45 | 0.016 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1982 | 29 | 201 | 24 | 93 | 1134 | 40 | 2 | 11 | 1 | 54 | 5 | 0.022 | 61 |  | 61 | 0.008 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1982 | 29 | 144 | 34 | 101 | 1133 | 20 | 1 | 5 | 0 | 17 | 4 | 0.027 | 73 |  | 39.8 | 0.011 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1982 | 29 | 261.8 | 40 | 181.6 | 2495.2 | 20.9 | 2.4 | 9.5 | 1.4 | 46 | 6 | 0.025 | 75 |  | 25 | 0.013 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1982 | 29 | 255.5 | 22 | 154.1 | 2009.9 | 32.4 | 3.1 | 8.3 | 3 | 54.6 | 4 | 0.022 | 75 |  | 29 | 0.01 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1982 | 29 | 100 | 34 | 72 | 1172 | 2 | 2 | 4 | 3 | 17 | 11 | 0.033 | 64 |  | 100 | 0.01 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1982 | 29 | 42 | 34 | 0 | 1099 | 18 | 3 | 5 | 4 | 12 | 6 | 0.025 | 63 |  | 45 | 0.0164 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1982 | 29 | 305 | 32 | 162 | 1822 | 66 | 3 | 9 | 1 | 64 | 4 | 0.031 | 69 |  | 42.1 | 0.008 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1982 | 29 | 333 | 34 | 225 | 1892 | 75 | 3 | 5 | 4 | 21 | 5 | 0.041 | 75 |  | 22.7 | 0.009 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1982 | 29 | 534.2 | 44 | 352.4 | 4307.4 | 104.5 | 6.5 | 12.2 | 8.8 | 49.8 | 10 | 0.066 | 75 |  | 14 | 0.015 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1982 | 29 | 511.3 | 41.81 | 341.8 | 3832.2 | 95.6 | 4 | 9.7 | 4.8 | 55.4 | 4 | 0.07 | 75 |  | 10 | 0.022 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1982 | 29 | 846 | 52 | 304 | 4020 | 92 | 15 | 42 | 3 | 390 | 12 | 0.065 | 66 |  | 13 | 0.015 | DGA is assessed as acceptable. Acetylene gas possibly communicating from tapchanger. | Oil quality is assessed as acceptable.
33000 | 1982 | 29 | 793 | 48 | 303 | 3433 | 47 | 7 | 51 | 4 | 381 | 6 | 0.091 | 73 |  | 8.8 | 0.024 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1982 | 29 | 707.7 | 52 | 452.4 | 2689.7 | 48.2 | 5.5 | 24.7 | 2.9 | 174 | 10 | 0.105 | 70 |  | 5 | 0.043 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1982 | 29 | 664.5 | 39 | 395.5 | 5191 | 47.4 | 6.2 | 24.4 | 8.4 | 182.6 | 12 | 0.109 | 75 |  | 5 | 0.042 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1982 | 29 | 758.5 | 54 | 516.2 | 5252.7 | 53.8 | 6.5 | 20.1 | 8.6 | 153.3 | 16 | 0.117 | 75 |  | 8 | 0.034 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1982 | 29 | 587.6 | 43 | 420 | 5070.8 | 42.8 | 9.2 | 13.5 | 3 | 99.1 | 12 | 0.122 | 62 |  | 7 | 0.036 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1982 | 29 | 633 | 51 | 306.5 | 3438.5 | 64.3 | 8.6 | 17.5 | 3.3 | 232.8 | 10 | 0.137 | 75 |  | 6 | 0.037 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1982 | 29 | 610.1 | 49 | 259.6 | 2914.8 | 62.9 | 9.5 | 38.8 | 8.3 | 231 | 11 | 0.144 | 75 |  | 6 | 0.042 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable. Non-corrosive IEC. Non-corrosive ASTM 2E.
33000 | 1982 | 29 | 301.2 | 52 | 167.9 | 2519.5 | 25.3 | 3.8 | 14.4 | 3.5 | 86.3 | 9 | 0.135 | 68 |  | 6 | 0.037 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable. Non-corrosive IEC. Non-corrosive ASTM 3A.
33000 | 1982 | 29 | 273.2 | 48 | 144 | 2367.6 | 26.6 | 3.3 | 10.5 | 2 | 86.8 | 17 | 0.148 | 71 |  | 4 | 0.048 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1982 | 29 | 563 | 20 | 310 | 2413 | 133 | 8 | 18 | 19 | 75 | 13 | 0.033 | 56 |  | 400 | 0.0024 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1982 | 29 | 646 | 25 | 446 | 2180 | 132 | 10 | 13 | 6 | 39 | 15 | 0.054 | 63 |  | 10 | 0.0252 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1982 | 29 | 1025 | 45 | 800 | 4413 | 108 | 15 | 22 | 8 | 72 | 17 | 0.146 | 75 |  | 5 | 0.053 | CO and CO2 gas appear high for transformer age. | Oil acidity is high. Other oil quality results are assessed as acceptable.
33000 | 1982 | 29 | 565 | 50 | 470 | 3115 | 50 | 4 | 8 | 3 | 30 | 18 | 0.18 | 61 |  | 4.5 | 0.067 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1982 | 29 | 778 | 60 | 667 | 4150 | 43 | 6 | 11 | 3 | 48 | 23 | 0.18 | 64 |  | 3.4 | 0.078 | Test results satisfactory. Acetylene gas possibly from tapchanger. | Oil quality is assessed as acceptable.
33000 | 1982 | 29 | 688 | 45 | 518 | 3955 | 64 | 6 | 12 | 2 | 86 | 20 | 0.181 | 61 |  | 4.8 | 0.045 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1982 | 29 | 927 | 46 | 690 | 6276 | 69 | 7 | 21 | 3 | 137 | 25 | 0.186 | 71 |  | 4.6 | 0.058 | DGA is assessed as acceptable. | Other test results are assessed as acceptable.
33000 | 1982 | 29 | 779 | 57 | 676 | 5990 | 31 | 8 | 14 | 4 | 46 | 16 | 0.219 | 61 |  | 4 | 0.072 | DGA is assessed as acceptable. | Acidity level is high. Other oil quality results are assessed as acceptable.
33000 | 1982 | 29 | 1022.3 | 60 | 894.5 | 8124.5 | 56.9 | 7.6 | 12.1 | 5.3 | 45.9 | 24 | 0.2115 | 62 |  | 5 | 0.05 | Acetylene gas possibly from tapchanger. | Other test results are assessed as relatively stable.
33000 | 1982 | 29 | 1310.5 | 59 | 1156.8 | 8511.3 | 92.9 | 7.5 | 11 | 5.6 | 36.7 | 28 | 0.253 | 62 |  | 5.2579 | 0.04994 | Carbon oxides are high. | Acidity level of sample is high.
33000 | 1982 | 29 | 819.8 | 51 | 723 | 5930.9 | 45.4 | 6.2 | 7.9 | 4.1 | 33.2 | 25 | 0.245 | 75 |  | 4 | 0.051 | DGA is assessed as acceptable. | Acidity is high but stable. Other oil quality results are assessed as acceptable.
33000 | 1982 | 29 | 574.8 | 27.2 | 494.4 | 5199.7 | 35.9 | 4.9 | 7 | 1.6 | 31 | 19 | 0.302 | 64 |  | 5 | 0.046 | DGA is assessed as acceptable. | Acidity level is high. Other oil quality results are assessed as acceptable.
33000 | 1982 | 29 | 621.8 | 70 | 523.5 | 5014.1 | 39.5 | 5.2 | 8.6 | 6.1 | 38.9 | 22 | 0.262 | 54 |  | 6 | 0.045 | DGA is assessed as acceptable. | Acidity level is high. Other oil quality results are assessed as acceptable.
33000 | 1982 | 29 | 481.4 | 53 | 417.1 | 4820.8 | 22.6 | 3.9 | 5.8 | 4 | 28 | 29 | 0.301 | 51 |  | 5 | 0.041 | DGA is assessed as acceptable. | Acidity level is high. Other oil quality results are assessed as acceptable. Non-corrosive IEC. Non-corrosive ASTM 3A.
33000 | 1982 | 29 | 448.6 | 76 | 371.6 | 4254 | 25.1 | 7.6 | 8.9 | 0.5 | 34.9 | 30 | 0.264 | 70 |  | 6 | 0.039 | DGA is assessed as acceptable. | Acidity level is high. Other oil quality results are assessed as acceptable.
33000 | 1982 | 29 | 88 | 34 | 75 | 1350 | 0 | 1 | 2 | 2 | 8 | 37 | 0.033 | 20 |  | 17 | 0.023 | Breakdown strength of oil sample low, moisture quite high. Perhaps resample for confirmation.
33000 | 1982 | 29 | 52 | 54 | 32 | 1370 | 0 | 2 | 5 | 1 | 12 | 7 | 0.028 | 68 |  | 16 | 0.024 | Test results satisfactory.
33000 | 1982 | 29 | 109 | 51 | 78 | 873 | 0 | 2 | 6 | 1 | 22 | 39 | 0.039 | 25 |  | 43.1 | 0.008 | High moisture and low breakdown strength of oil sample. Suspect sample contamin- ation. Other test results satisfactory.
33000 | 1982 | 29 | 521 | 50 | 176 | 1392 | 65 | 11 | 30 | 2 | 237 | 20 | 0.044 | 71 |  | 22.4 | 0.011 | Test results satisfactory. Acetylene gas possibly from tapchanger.
33000 | 1982 | 29 | 386 | 44 | 74 | 1056 | 62 | 6 | 21 | 1 | 222 | 16 | 0.049 | 58 |  | 20.1 | 0.011 | Dissolved gas analysis is assessed as acceptable. Acetylene gas possibly from tap changer. Oil quality is assessed as acceptable.
33000 | 1982 | 29 | 408 | 44 | 81 | 1111 | 57 | 6 | 24 | 2 | 238 | 11 | 0.044 | 66 |  | 24.2 | 0.012 | Dissolved gas analysis is assessed as acceptable. Acetylene gas possibly from tapchanger. Oil quality is assessed as acceptable.
33000 | 1982 | 29 | 485 | 20 | 70 | 1229 | 73 | 8 | 30 | 2 | 302 | 6 | 0.043 | 83 |  | 20.9 | 0.013 | Dissolved gas analysis is assessed as acceptable. Oil quality is assessed as acceptable.
33000 | 1982 | 29 | 11 | 41.81 | 11 | 176 | 0 | 0 | 0 | 0 | 0 | 6 | 0.009 | 92 |  | 37.3 | 0.01 | Dissolved gas analysis is assessed as acceptable. Oil quality is assessed as acceptable.
33000 | 1982 | 29 | 302.9 | 48 | 148.6 | 2155.8 | 12.7 | 3.2 | 35.2 | 4.6 | 98.6 | 9 | 0.026 | 75 |  | 17 | 0.017 | The test results are assessed as acceptable. Acetylene gas possibly from tapchanger. | Oil quality is assessed as acceptable.
33000 | 1982 | 29 | 281.2 | 42 | 184.3 | 2025.5 | 10.5 | 2.4 | 25.9 | 1.9 | 56.2 | 9 | 0.033 | 72 |  | 18 | 0.013 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1982 | 29 | 232.2 | 45 | 148.2 | 2026.2 | 8.8 | 2.6 | 20.5 | 0 | 52.1 | 10 | 0.032 | 75 |  | 18 | 0.013 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1982 | 29 | 196.7 | 42 | 123.7 | 1724.3 | 7.1 | 2.5 | 16.9 | 0.6 | 45.9 | 12 | 0.034 | 75 |  | 19 | 0.015 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable. Corrosive IEC. Non-corrosive ASTM 2E.
33000 | 1982 | 29 | 139.3 | 40 | 109.4 | 1764.9 | 2.7 | 0 | 9.6 | 0 | 17.6 | 14 | 0.036 | 78 |  | 17 | 0.014 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable. Corrosive IEC. Non-corrosive ASTM 2E.
33000 | 1982 | 29 | 127.3 | 40 | 87.6 | 1396.5 | 6.8 | 1.3 | 10.1 | 0.3 | 21.2 | 11 | 0.039 | 88 |  | 18 | 0.014 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1982 | 29 | 522 | 52 | 255 | 2528 | 115 | 6 | 23 | 8 | 115 | 29 | 0.038 | 38 |  | 70 | 0.007 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1982 | 29 | 608 | 60 | 393 | 2748 | 112 | 5 | 18 | 4 | 76 | 9 | 0.046 | 66 |  | 6 | 0.0442 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1982 | 29 | 731 | 44 | 573 | 3187 | 68 | 7 | 11 | 2 | 70 | 15 | 0.087 | 48 |  | 8.4 | 0.031 | Test results satisfactory at present. | Oil quality is assessed as acceptable.
33000 | 1982 | 29 | 382 | 50 | 292 | 2378 | 47 | 3 | 5 | 1 | 34 | 17 | 0.11 | 66 |  | 9.9 | 0.025 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1982 | 29 | 579 | 45 | 360 | 3533 | 61 | 6 | 14 | 4 | 134 | 16 | 0.13 | 43 |  | 8.5 | 0.03 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1982 | 29 | 655 | 49 | 418 | 4767 | 45 | 6 | 20 | 3 | 163 | 17 | 0.136 | 75 |  | 9 | 0.027 | Acetylene gas possibly from tapchanger. | Other test results are assessed as acceptable.
33000 | 1982 | 29 | 558 | 54 | 399 | 3986 | 37 | 4 | 13 | 2 | 103 | 11 | 0.135 | 72 |  | 8.4 | 0.029 | Acetylene gas possibly from tapchanger. | Other test results are assessed as acceptable.
33000 | 1982 | 29 | 641 | 61 | 524 | 7333 | 22 | 5 | 13 | 6 | 71 | 18 | 0.144 | 60 |  | 7 | 0.034 | DGA is assessed as acceptable. | Other test results are assessed as acceptable.
33000 | 1982 | 29 | 800 | 61 | 669.1 | 6679.2 | 46.7 | 6.2 | 11.7 | 4.9 | 61.4 | 19 | 0.164 | 57 |  | 7 | 0.037 | Acetylene gas possibly from tapchanger. | Other test results are assessed as acceptable.
33000 | 1982 | 29 | 1108.5 | 66 | 963.8 | 7435.8 | 79.7 | 6.6 | 11.1 | 4.9 | 42.4 | 29 | 0.174 | 50 |  | 8.0319 | 0.034177 | Carbon oxide levels are high. | Other test results are assessed as acceptable.
33000 | 1982 | 29 | 655.6 | 53 | 567.1 | 4835.3 | 36.9 | 5.4 | 7.7 | 3.6 | 34.9 | 15 | 0.168 | 74 |  | 6 | 0.037 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1982 | 29 | 525.7 | 46 | 445.6 | 4746.8 | 33.8 | 5.1 | 9.1 | 1.4 | 30.7 | 16 | 0.205 | 65 |  | 7 | 0.028 | DGA is assessed as acceptable. | Acidity level is high. Other oil quality results are assessed as acceptable.
33000 | 1982 | 29 | 596.7 | 70 | 496 | 4554.5 | 40.6 | 5.3 | 9.8 | 5.2 | 39.8 | 19 | 0.187 | 59 |  | 8 | 0.032 | DGA is assessed as acceptable. | Acidity level is high. Other oil quality results are assessed as acceptable.
33000 | 1982 | 29 | 399.3 | 78 | 326.4 | 3571.3 | 26.6 | 7.6 | 8.3 | 0.5 | 29.9 | 25 | 0.189 | 52 |  | 7 | 0.031 | DGA is assessed as acceptable. | Acidity level is high. Other oil quality results are assessed as acceptable.
33000 | 1981 | 30 | 200 | 41.81 | 96 | 1039 | 32 | 3 | 10 | 2 | 57 | 34 | 0.012 | 53 |  | 15 | 0.038 | Test results satisfactory.
33000 | 1981 | 30 | 177 | 45 | 103 | 1049 | 0 | 3 | 10 | 2 | 59 | 14 | 0.034 | 41 |  | 25 | 0.017 | Test results satisfactory.
33000 | 1981 | 30 | 414 | 40 | 226 | 1364 | 44 | 4 | 12 | 1 | 127 | 16 | 0.049 | 48 |  | 25.9 | 0.012 | Test results satisfactory. Acetylene gas possibly from tapchanger.
33000 | 1981 | 30 | 542 | 48 | 253 | 1665 | 62 | 6 | 20 | 2 | 199 | 15 | 0.053 | 56 |  | 23.1 | 0.017 | Test results satisfactory. Acetylene gas possibly from tapchanger.
33000 | 1981 | 30 | 720 | 41.81 | 498 | 2900 | 53 | 11 | 24 | 7 | 127 | 19 | 0.067 | 42 |  | 12.8 | 0.017 | Test results are assessed as acceptable. Acetylene gas possibly from tapchanger.
33000 | 1981 | 30 | 716.2 | 60 | 595.1 | 4223.9 | 29.5 | 7.1 | 15.3 | 4.5 | 64.7 | 24 | 0.094 | 60 |  | 6 | 0.048 | 2-furfural level is high suggesting accelerated rate of insulation degradation. Other test results are assessed as acceptable. RECOMMEND RESAMPLE IN 1 YEAR TO MONITOR CONDITION.
33000 | 1981 | 30 | 923.3 | 69 | 824 | 7060 | 30 | 8.3 | 11 | 5.2 | 44.8 | 33 | 0.115 | 32 |  | 5.9423 | 0.043681 | 2-furfural level is high suggesting advanced state of insulation degradation. Carbon oxide levels are trending upwards. Possibly load related. Moisture content of sample is high. RECOMMEND RESAMPLE IN 6 MONTHS TO MONITOR CONDITION.
33000 | 1981 | 30 | 152 | 41.81 | 82 | 838 | 21 | 3 | 8 | 2 | 36 | 15 | 0.014 | 58 |  | 15 | 0.038 | Test results satisfactory.
33000 | 1981 | 30 | 202 | 47 | 122 | 1044 | 19 | 3 | 9 | 1 | 48 | 9 | 0.026 | 57 |  | 33 | 0.011 | Test results satisfactory.
33000 | 1981 | 30 | 295 | 42 | 161 | 1215 | 29 | 4 | 10 | 1 | 90 | 15 | 0.051 | 50 |  | 26.8 | 0.01 | Test results satisfactory. Acetylene gas possibly from tapchanger.
33000 | 1981 | 30 | 390 | 50 | 162 | 1197 | 47 | 5 | 15 | 1 | 160 | 70 | 0.034 | 63 |  | 35.2 | 0.008 | Moisture content very high possibly sample contamination.Other test results satisfactory.Acetylene gas from t/c?
33000 | 1981 | 30 | 627 | 41.81 | 435 | 2405 | 37 | 7 | 17 | 2 | 129 | 14 | 0.056 | 43 |  | 15.9 | 0.015 | Test results are assessed as acceptable. Acetylene gas possible from tapchanger.
33000 | 1981 | 30 | 559 | 75 | 465 | 3218 | 22 | 5 | 8 | 2 | 57 | 36 | 0.077 | 32 |  | 7.1 | 0.036 | 2-furfural level of oil is high. Other test results are assessed acceptable. RECOMMEND RESAMPLE IN 1 YEAR TO MONITOR CONDITION.
33000 | 1981 | 30 | 723.4 | 63 | 601.4 | 3815.2 | 30.2 | 6.7 | 13.3 | 3.8 | 68 | 24 | 0.086 | 53 |  | 4 | 0.056 | 2-furfural level is trending upwards suggesting accelerated rate of insulation degradation. Other test results are assessed as acceptable. RECOMMEND RESAMPLE IN 1 YEAR TO MONITOR CONDITION.
33000 | 1981 | 30 | 1003.1 | 58 | 903 | 7029 | 37 | 9.5 | 10.9 | 5.5 | 37.2 | 28 | 0.112 | 29 |  | 5.3388 | 0.04609 | 2-furfural level is high suggesting advanced state of insulation degradation. Carbon oxide levels are trending upwards. Possibly load related. Breakdown voltage of sample is slightly low. RECOMMEND RESAMPLE IN 6 MONTHS TO MONITOR CONDITION.
33000 | 1981 | 30 | 354 | 30 | 223 | 1715 | 42 | 5 | 12 | 2 | 70 | 13 | 0.049 | 71 |  | 10 | 0.026 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1981 | 30 | 522 | 58 | 260 | 1800 | 52 | 7 | 19 | 4 | 180 | 25 | 0.078 | 55 |  | 5 | 0.051 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable. PCB contaminated oil.
33000 | 1981 | 30 | 443 | 40 | 272 | 2006 | 0 | 7 | 17 | 2 | 145 | 24 | 0.073 | 64 |  | 7.1 | 0.035 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable. PCB content below 2mg/kg.
33000 | 1981 | 30 | 909 | 50 | 635 | 4242 | 55 | 9 | 21 | 3 | 186 | 28 | 0.084 | 63 |  | 7.5 | 0.03 | Test results satisfactory. Acetylene possibly from tapchanger. | Oil quality is assessed as acceptable.
33000 | 1981 | 30 | 549 | 56 | 340 | 3155 | 23 | 9 | 59 | 27 | 91 | 15 | 0.097 | 69 |  | 3.8 | 0.064 | DGA is assessed as acceptable. | Other test results are assessed as acceptable.
33000 | 1981 | 30 | 645 | 64 | 406 | 4324 | 34 | 8 | 45 | 28 | 124 | 29 | 0.112 | 58 |  | 5.6 | 0.042 | DGA is assessed as acceptable. | Other test results are assessed as acceptable.
33000 | 1981 | 30 | 691 | 47 | 472.7 | 3305.9 | 28 | 7.2 | 27.5 | 12.8 | 142.8 | 23 | 0.113 | 44 |  | 4 | 0.056 | DGA is assessed as acceptable. | Other test results are assessed as acceptable.
33000 | 1981 | 30 | 616.5 | 55 | 445.9 | 3720.5 | 38.6 | 7.2 | 19.3 | 11.4 | 94.1 | 27 | 0.112 | 30 |  | 2 | 0.113 | DGA is assessed as acceptable. | Other test results are assessed as acceptable.
33000 | 1981 | 30 | 768.3 | 60 | 623 | 5660 | 31.7 | 8.2 | 16.2 | 9.1 | 80.1 | 39 | 0.124 | 27 |  | 5 | 0.049 | DGA is assessed as acceptable. | Moisture content of sample is high. Breakdown voltage of sample is low. Other test results are assessed as acceptable at present.
33000 | 1981 | 30 | 306.3 | 40 | 162.1 | 2296.6 | 18.1 | 7.2 | 15.8 | 7.3 | 95.8 | 12 | 0.124 | 60 |  | 7 | 0.03 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1981 | 30 | 437.7 | 46 | 188.9 | 2027.9 | 17.7 | 5.8 | 25 | 2.4 | 197.9 | 17 | 0.109 | 57 |  | 4 | 0.048 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1981 | 30 | 253.2 | 45 | 148.5 | 1728.8 | 9.9 | 3.4 | 10.8 | 1.2 | 79.4 | 17 | 0.127 | 64 |  | 5 | 0.043 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1981 | 30 | 214.4 | 39 | 123.8 | 1393.6 | 12.6 | 4.2 | 8.3 | 1.9 | 63.6 | 16 | 0.127 | 80 |  | 7 | 0.034 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1981 | 30 | 224 | 47 | 173 | 1808 | 0 | 1 | 50 | 0 | 0 | 14 | 0.13 | 56 |  | 5 | 0.05 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1981 | 30 | 310 | 54 | 201 | 1588 | 17 | 4 | 10 | 2 | 76 | 13 | 0.03 | 59 |  | 24.1 | 0.011 | DGA is assessed as acceptable. Acetylene gas possibly communicating from tapchanger. | Oil quality much improved since last sample ?.
33000 | 1981 | 30 | 466 | 57 | 309 | 1676 | 32 | 5 | 12 | 2 | 106 | 17 | 0.074 | 68 |  | 18.8 | 0.014 | DGA is assessed as acceptable. Acetylene gas possibly communicating from tapchanger. | Oil quality is assessed as acceptable.
33000 | 1981 | 30 | 441 | 40 | 210 | 2294 | 26 | 7 | 20 | 2 | 176 | 15 | 0.075 | 65 |  | 12.7 | 0.021 | DGA is assessed as acceptable. Acetylene gas possibly communicating from tapchanger. | Oil quality is assessed as acceptable.
33000 | 1981 | 30 | 555 | 48 | 273 | 2535 | 23 | 8 | 22 | 10 | 219 | 19 | 0.066 | 75 |  | 10 | 0.024 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1981 | 30 | 547 | 40 | 417.5 | 3288.4 | 18 | 7.9 | 16.9 | 10.3 | 76.4 | 18 | 0.081 | 75 |  | 6 | 0.041 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1981 | 30 | 716 | 53 | 573.3 | 4776 | 30.8 | 8.7 | 14.9 | 7.3 | 81 | 18 | 0.095 | 54 |  | 7.2934 | 0.03608 | DGA is assessed as acceptable. | Other test results are assessed as acceptable.
33000 | 1981 | 30 | 458.3 | 50 | 353.8 | 3621.6 | 17.4 | 5.2 | 11.4 | 4 | 66.5 | 14 | 0.088 | 75 |  | 5 | 0.043 | The test results are assessed as relatively stable.
33000 | 1981 | 30 | 365.9 | 58 | 299.4 | 3068.4 | 10.9 | 3.7 | 7.1 | 3.8 | 41 | 18 | 0.096 | 53 |  | 5 | 0.046 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1981 | 30 | 344.9 | 40 | 250.5 | 2971.2 | 24.9 | 4.6 | 9 | 2.3 | 53.6 | 16 | 0.096 | 65 |  | 7 | 0.03481 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1981 | 30 | 248.2 | 27.1 | 171.4 | 2061.1 | 11.6 | 4.3 | 10.5 | 4.7 | 45.7 | 16 | 0.097 | 58 |  | 8 | 0.029 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1981 | 30 | 269.4 | 45 | 175.7 | 2152.7 | 14.1 | 4.6 | 9.8 | 1.6 | 63.6 | 16 | 0.102 | 74 |  | 7 | 0.035 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable. Non-corrosive IEC. Non-corrosive ASTM 1B.
33000 | 1981 | 30 | 216.6 | 41 | 129.3 | 1728.7 | 12.1 | 3.6 | 8.3 | 0.9 | 62.4 | 14 | 0.103 | 76 |  | 7 | 0.033 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable. Non-corrosive IEC. Non-corrosive ASTM 2C.
33000 | 1981 | 30 | 872 | 41.81 | 621 | 2449 | 102 | 33 | 24 | 28 | 64 | 11 | 0.107 | 65 |  | 10 | 0.03 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1981 | 30 | 709 | 41.81 | 448 | 1543 | 72 | 46 | 24 | 19 | 100 | 28 | 0.124 | 41 |  | 8 | 0.033 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable. PCB contaminated oil.
33000 | 1981 | 30 | 1425 | 45 | 990 | 3706 | 154 | 96 | 43 | 59 | 83 | 35 | 0.174 | 51 |  | 4.4 | 0.057 | DGA suggests slight overheating. High CO increased acidity;low O2; accelerated ageing. | Moisture content is high. Other oil quality results are assessed as acceptable. PCB content below 2mg/kg.
33000 | 1981 | 30 | 1384 | 50 | 1050 | 6057 | 102 | 69 | 54 | 30 | 79 | 53 | 0.209 | 55 |  | 5.2 | 0.048 | Carbon oxides and acidity are high for transformers age. Suggests transformer is heavily loaded. | Moisture content is high. Other oil quality results are assessed as acceptable. PCB contaminated oil.
33000 | 1981 | 30 | 1103 | 38 | 800 | 5553 | 88 | 19 | 58 | 19 | 119 | 24 | 0.289 | 75 |  | 3.8 | 0.065 | DGA is assessed as acceptable. | Acidity level is high.
33000 | 1981 | 30 | 1233 | 64 | 831 | 7526 | 96 | 19 | 81 | 32 | 174 | 41 | 0.294 | 75 |  | 5 | 0.041 | DGA is assessed as acceptable. | Moisture and oil acidity are high.
33000 | 1981 | 30 | 1248.5 | 50 | 860.2 | 5108.9 | 80.8 | 16.1 | 80.6 | 36.6 | 174.2 | 31 | 0.299 | 43 |  | 4 | 0.049 | DGA is assessed as acceptable. | Other test results are assessed as stable.
33000 | 1981 | 30 | 897.4 | 54 | 659.2 | 5550.5 | 59.6 | 11.6 | 36.2 | 16.1 | 114.7 | 33 | 0.322 | 32 |  | 5 | 0.046 | DGA is assessed as acceptable. | Acidity level is high. Other test results are assessed as acceptable.
33000 | 1981 | 30 | 1181.8 | 60 | 945.9 | 8382.2 | 81.1 | 13.4 | 34.1 | 14.6 | 92.7 | 51 | 0.349 | 24.5 |  | 4 | 0.048 | DGA is assessed as acceptable. | Moisture content of sample is high. Breakdown voltage of sample is low. Acidity level of sample is high.
33000 | 1981 | 30 | 482.3 | 40 | 327.7 | 3565.8 | 40.3 | 6.4 | 16 | 4.1 | 87.8 | 26 | 0.337 | 49 |  | 5 | 0.048 | DGA is assessed as acceptable. | Acidity level is high. Resistivity is low. Other oil quality results are assessed as acceptable.
33000 | 1981 | 30 | 543.6 | 42 | 302 | 3430.6 | 28.4 | 6.6 | 26.6 | 3.5 | 176.5 | 24 | 0.316 | 57 |  | 4 | 0.051 | DGA is assessed as acceptable. | Acidity level is high. Other oil quality results are assessed as acceptable.
33000 | 1981 | 30 | 415.5 | 50 | 307.7 | 3377.3 | 22.9 | 4.7 | 12 | 1.9 | 66.3 | 23 | 0.36 | 66 |  | 4 | 0.057 | DGA is assessed as acceptable. | Acidity level is high. Other oil quality results are assessed as acceptable.
33000 | 1981 | 30 | 264 | 40 | 192.5 | 2107.8 | 17.1 | 4 | 6.6 | 1.6 | 42.2 | 19 | 0.364 | 76 |  | 3 | 0.074 | DGA is assessed as acceptable. | Acidity level is high. Other oil quality results are assessed as acceptable.
33000 | 1981 | 30 | 150 | 45 | 120 | 2773 | 0 | 1 | 29 | 0 | 0 | 19 | 0.042 | 67 |  | 30 | 0.014 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1981 | 30 | 380 | 45 | 284 | 1866 | 21 | 5 | 9 | 2 | 59 | 11 | 0.048 | 63 |  | 21.3 | 0.012 | DGA is assessed as acceptable. Acetylene gas possibly communicating from tapchanger. | Oil quality is assessed as acceptable.
33000 | 1981 | 30 | 538 | 54 | 332 | 2408 | 42 | 7 | 20 | 3 | 134 | 14 | 0.055 | 43 |  | 15.7 | 0.016 | DGA is assessed as acceptable. Acetylene gas possibly communicating from tapchanger. | Oil quality is assessed as acceptable.
33000 | 1981 | 30 | 582 | 43 | 283 | 2597 | 38 | 6 | 23 | 2 | 230 | 9 | 0.062 | 61 |  | 12.3 | 0.024 | DGA is assessed as acceptable. Acetylene gas possibly communicating from tapchanger. | Oil quality is assessed as acceptable.
33000 | 1981 | 30 | 575 | 40 | 295 | 2595 | 24 | 8 | 20 | 8 | 220 | 22 | 0.084 | 70 |  | 8.7 | 0.028 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1981 | 30 | 680.8 | 36 | 529.9 | 4656.8 | 19.7 | 17 | 22.2 | 16.1 | 75.9 | 33 | 0.091 | 33 |  | 3 | 0.066 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1981 | 30 | 720.4 | 49 | 564.7 | 4933 | 30.6 | 8.3 | 16 | 7.9 | 92.9 | 20 | 0.109 | 59 |  | 7.404 | 0.03608 | 2-furfural and carbon oxide levels are trending upwards suggesting advanced state of insulation degradation. | Oil quality is assessed as acceptable.
33000 | 1981 | 30 | 448.6 | 45 | 341.9 | 3702.1 | 14.9 | 4.7 | 11.7 | 4 | 71.4 | 14 | 0.097 | 63 |  | 6 | 0.042 | The test results are assessed as relatively stable.
33000 | 1981 | 30 | 396.3 | 52 | 326.2 | 3319.4 | 10.8 | 3.9 | 7.5 | 3.8 | 44.1 | 17 | 0.104 | 75 |  | 5 | 0.046 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1981 | 30 | 372.2 | 24 | 280.7 | 3436.9 | 18.6 | 5.3 | 10.4 | 2.8 | 54.4 | 21 | 0.111 | 66 |  | 6 | 0.03829 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1981 | 30 | 245.8 | 25.5 | 170.9 | 2031 | 10.1 | 3.8 | 8.5 | 1 | 51.5 | 15 | 0.114 | 52 |  | 6 | 0.035 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1981 | 30 | 314.3 | 62 | 220.5 | 2741.3 | 12.7 | 5.4 | 9.9 | 2.1 | 63.7 | 16 | 0.117 | 75 |  | 8 | 0.028 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable. Non-corrosive IEC. Non-corrosive ASTM 1B.
33000 | 1981 | 30 | 211.8 | 56 | 135.4 | 1883.9 | 10.9 | 3.3 | 6.5 | 0.9 | 54.8 | 14 | 0.117 | 92 |  | 8 | 0.03 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable. Non-corrosive IEC. Non-corrosive ASTM 2C.
33000 | 1981 | 30 | 183 | 22 | 140 | 1601 | 0 | 3 | 33 | 0 | 7 | 17 | 0.074 | 71 |  | 15 | 0.018 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1981 | 30 | 263 | 25 | 152 | 1271 | 0 | 3 | 10 | 1 | 97 | 11 | 0.026 | 56 |  | 16 | 0.018 | DGA is assessed as acceptable. Acetylene gas possibly communicating from tapchanger. | Oil quality is assessed as acceptable.
33000 | 1981 | 30 | 458 | 37 | 272 | 1876 | 0 | 5 | 17 | 1 | 163 | 16 | 0.053 | 68 |  | 11.6 | 0.023 | DGA is assessed as acceptable. Acetylene gas possibly communicating from tapchanger. | Oil quality is assessed as acceptable.
33000 | 1981 | 30 | 485 | 25 | 258 | 1912 | 41 | 6 | 19 | 2 | 159 | 24 | 0.055 | 47 |  | 10.7 | 0.026 | DGA is assessed as acceptable. Acetylene gas possibly communicating from tapchanger. | Oil quality is assessed as acceptable.
33000 | 1981 | 30 | 559 | 46 | 300 | 2446 | 24 | 8 | 20 | 2 | 205 | 15 | 0.056 | 69 |  | 6.1 | 0.037 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1981 | 30 | 568.8 | 40 | 480.3 | 3450.1 | 16.7 | 9 | 13.5 | 7.7 | 41.6 | 20 | 0.066 | 70 |  | 4 | 0.057 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1981 | 30 | 707.9 | 53 | 565.1 | 4805.6 | 25.9 | 10 | 16.5 | 8.6 | 81.8 | 27 | 0.079 | 59 |  | 4.4811 | 0.05753 | 2-furfural and carbon oxide levels are trending upwards suggesting advanced state of insulation degradation. | Oil quality is assessed as acceptable.
33000 | 1981 | 30 | 459.5 | 48 | 356.3 | 3683.3 | 14.8 | 5.2 | 12 | 6.4 | 64.8 | 15 | 0.077 | 74 |  | 3 | 0.068 | The test results are assessed as relatively stable. | Oil quality is assessed as acceptable.
33000 | 1981 | 30 | 428 | 55 | 344.5 | 3482.5 | 9.2 | 5.3 | 12.6 | 6.4 | 50 | 19 | 0.076 | 70 |  | 3 | 0.069 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1981 | 30 | 280.2 | 20 | 215 | 2685.9 | 10.8 | 4.2 | 8.6 | 2.9 | 38.7 | 20 | 0.081 | 65 |  | 3 | 0.071 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1981 | 30 | 269.4 | 22.1 | 203.4 | 2250.8 | 9.9 | 3.7 | 9.2 | 1.4 | 41.8 | 15 | 0.086 | 58 |  | 4 | 0.058 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1981 | 30 | 288.7 | 58 | 213.5 | 2301.4 | 11.4 | 4.5 | 9.7 | 3.1 | 46.5 | 17 | 0.089 | 75 |  | 4 | 0.062 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable. Non-corrosive IEC. Non-corrosive ASTM 3B.
33000 | 1981 | 30 | 560.8 | 52 | 25.4 | 1521.8 | 131.5 | 25.7 | 41.5 | 7.3 | 329.4 | 14 | 0.003 | 74 |  | 343 | 0.002 | Dissolved gas levels are increased. DGA suggests low energy discharge has occurred. | Oil quality is assessed as acceptable. Non-corrosive IEC. Non-corrosive ASTM 3A.
33000 | 1981 | 30 | 187.5 | 54 | 107.7 | 1775.5 | 6.8 | 3.2 | 7.8 | 1 | 61 | 15 | 0.091 | 67 |  | 3 | 0.074 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1981 | 30 | 184 | 41.81 | 38 | 1500 | 36 | 5 | 12 | 2 | 91 | 7 | 0.035 | 65 |  | 15 | 0.032 | C2H2 from tapchanger; otherwise test results satisfactory. | Oil quality is assessed as acceptable.
33000 | 1981 | 30 | 482 | 34 | 209 | 1569 | 51 | 8 | 20 | 4 | 190 | 23 | 0.046 | 50 |  | 20.6 | 0.013 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable. PCB contaminated oil.
33000 | 1981 | 30 | 556 | 41 | 324 | 2265 | 29 | 10 | 21 | 7 | 165 | 25 | 0.058 | 54 |  | 13.1 | 0.02 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable. PCB content below 2mg/kg.
33000 | 1981 | 30 | 854 | 50 | 514 | 4044 | 44 | 14 | 26 | 16 | 240 | 30 | 0.07 | 50 |  | 8.2 | 0.03 | Test results satisfactory. Acetylene possibly from tapchanger. | Oil quality is assessed as acceptable. PCB contaminated oil.
33000 | 1981 | 30 | 521 | 51 | 372 | 3328 | 26 | 7 | 13 | 3 | 100 | 17 | 0.087 | 62 |  | 5.4 | 0.042 | DGA is assessed as acceptable. Acetylene gas possibly from tapchanger. | Other test results are assessed as acceptable.
33000 | 1981 | 30 | 531 | 56 | 363 | 3823 | 28 | 7 | 18 | 9 | 106 | 23 | 0.093 | 52 |  | 7.1 | 0.034 | DGA is assessed as acceptable. Acetylene gas possibly from tapchanger. | Other test results are assessed as acceptable.
33000 | 1981 | 30 | 639.9 | 58 | 455.8 | 4196.4 | 25.9 | 6.8 | 21.3 | 6.7 | 123.4 | 27 | 0.102 | 43 |  | 6 | 0.04 | The test results are relatively stable. | Oil quality is assessed as acceptable.
33000 | 1981 | 30 | 589.4 | 52 | 436.1 | 4475.7 | 34.8 | 5.4 | 15.9 | 6.9 | 90.3 | 29 | 0.102 | 37 |  | 7 | 0.036 | DGA is assessed as acceptable. | Other test results are assessed as acceptable.
33000 | 1981 | 30 | 794.4 | 60 | 641.1 | 6041.4 | 29.3 | 7.7 | 16.1 | 7.3 | 92.9 | 38 | 0.111 | 31 |  | 5 | 0.043 | DGA is assessed as acceptable. | Moisture content of sample is high. Other test results are assessed as acceptable at present.
33000 | 1981 | 30 | 320.4 | 40 | 203.7 | 2647.3 | 19.8 | 5 | 12.8 | 3 | 76.1 | 15 | 0.113 | 62 |  | 7 | 0.033 | DGA is assessed as acceptable. | Resistivity is low but stable. Other oil quality results are assessed as acceptable.
33000 | 1981 | 30 | 328.4 | 40 | 197.6 | 2003.3 | 16.6 | 5.1 | 15.5 | 2.1 | 91.5 | 15 | 0.1 | 66 |  | 5 | 0.045 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1981 | 30 | 251.6 | 47 | 172.7 | 2031.4 | 12.5 | 3.8 | 9.2 | 1.5 | 51.9 | 15 | 0.118 | 64 |  | 6 | 0.034 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1981 | 30 | 182.8 | 40 | 119.6 | 1449.9 | 11.6 | 3.8 | 5.6 | 1 | 41.2 | 16 | 0.118 | 92 |  | 7 | 0.034 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1981 | 30 | 3718.1 | 40 | 55.7 | 1174 | 1933.1 | 139.8 | 170.1 | 16.6 | 1402.8 | 19 | 0.005 | 55 |  | 446 | 0.001 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable. Particle contamination load is high.
33000 | 1979 | 32 | 115 | 41.81 | 107 | 1255 | 6 | 1 | 1 | 0 | 0 | 7 | 0.03 | 69 |  | 11.3 | 0.028 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1979 | 32 | 1310 | 17 | 156 | 1970 | 413 | 124 | 237 | 19 | 361 | 11 | 0.032 | 46 |  | 17 | 0.019 | Dissolved gas analysis suggests power arcing has occurred.
33000 | 1979 | 32 | 12.6 | 22 | 10.3 | 83.2 | 0 | 2 | 0.2 | 0.1 | 0 | 6 | 0.016 | 63 |  | 17 | 0.022 | The test results are assessed as acceptable at present.
33000 | 1979 | 32 | 13.3 | 26 | 12.3 | 130.4 | 0 | 0.5 | 0.4 | 0.1 | 0 | 11 | 0.018 | 75 |  | 15 | 0.025 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1979 | 32 | 411.8 | 39 | 375.8 | 1292.2 | 0 | 2.5 | 32.9 | 0.6 | 0 | 7 | 0.018 | 74 |  | 8 | 0.058 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1979 | 32 | 359.5 | 38 | 302.9 | 1678 | 4.1 | 2.5 | 49.5 | 0.5 | 0 | 8 | 0.033 | 75 |  | 8 | 0.057 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1979 | 32 | 634.8 | 15 | 482.6 | 2313.7 | 77.5 | 27.2 | 22.7 | 24.8 | 0 | 7 | 0.046 | 100 |  | 4 | 0.09 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable. Corrosive IEC. Corrosive ASTM 4B.
33000 | 1979 | 32 | 698 | 17 | 521.5 | 2891.1 | 99.7 | 46.1 | 12.5 | 18.2 | 0 | 10 | 0.071 | 91 |  | 4 | 0.084 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1979 | 32 | 693.9 | 12 | 580.7 | 3454.3 | 91.1 | 7.3 | 8.2 | 6.6 | 0 | 7 | 0.089 | 82 |  | 4 | 0.064 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1978 | 33 | 19.8 | 23 | 16.3 | 646.3 | 1.8 | 1.1 | 0.4 | 0.2 | 0 | 28 | 0.026 | 38 |  | 31 | 0.007 | DGA is assessed as acceptable. | Breakdown voltage is low. Other oil quality results are assessed as acceptable.
33000 | 1978 | 33 | 141.8 | 25 | 34 | 682.3 | 3.7 | 16.2 | 14.9 | 73 | 0 | 25 | 0.028 | 41 |  | 12 | 0.022 | DGA suggests mild oil overheating (<300C) has occurred. | Oil quality is assessed as acceptable.
33000 | 1978 | 33 | 86.6 | 21 | 79.8 | 1970.3 | 2.3 | 2.7 | 0.5 | 1.3 | 0 | 8 | 0.011 | 76 |  | 56 | 0.006 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1978 | 33 | 20.9 | 41.81 | 19.9 | 771.7 | 0 | 0.8 | 0.2 | 0 | 0 | 30 | 0.017 | 20 |  | 31 | 0.009 | DGA is assessed as acceptable. | Breakdown voltage is low. Possible sample contamination. Other oil quality results are assessed as acceptable.
33000 | 1978 | 33 | 22.7 | 24.1 | 15.5 | 703.4 | 1.1 | 1.7 | 0.6 | 3.8 | 0 | 22 | 0.02 | 36 |  | 32 | 0.008 | DGA is assessed as acceptable. | Breakdown voltage is slightly low. Other oil quality results are assessed as acceptable.
33000 | 1978 | 33 | 37.2 | 26 | 22.9 | 690.5 | 4.1 | 3.6 | 1.2 | 5.4 | 0 | 34 | 0.022 | 19 |  | 16 | 0.018 | DGA is assessed as acceptable. | Breakdown voltage is low. Other oil quality results are assessed as acceptable.
33000 | 1978 | 33 | 25.2 | 41.81 | 20 | 790.4 | 3.8 | 0.9 | 0.3 | 0.2 | 0 | 36 | 0.018 | 24 |  | 30 | 0.008 | DGA is assessed as acceptable. | Breakdown voltage is low. Other oil quality results are assessed as acceptable.
33000 | 1978 | 33 | 17 | 41.81 | 12.3 | 771.4 | 2.6 | 0.9 | 0.9 | 0.2 | 0.1 | 25 | 0.033 | 38 |  | 24 | 0.01 | DGA is assessed as acceptable. | Breakdown voltage is low. Other oil quality results are assessed as acceptable.
33000 | 1978 | 33 | 15 | 41.81 | 12 | 436 | 0 | 2 | 0 | 1 | 0 | 12 | 0.013 | 70 |  | 47 | 0.005 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1978 | 33 | 281.9 | 22 | 199.3 | 3980.2 | 5.1 | 20.6 | 7.4 | 49.5 | 0 | 11 | 0.009 | 97 |  | 179 | 0.005 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1978 | 33 | 9 | 41.81 | 8 | 534 | 0 | 1 | 0 | 0 | 0 | 20 | 0.015 | 72 |  | 150.8 | 0.003 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1978 | 33 | 14.4 | 27 | 12.9 | 835 | 0 | 1.1 | 0.3 | 0.1 | 0 | 22 | 0.016 | 66 |  | 59 | 0.005 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1978 | 33 | 27 | 25 | 21.8 | 720.7 | 1.4 | 0.8 | 3 | 0 | 0 | 19 | 0.048 | 83 |  | 11 | 0.023 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1978 | 33 | 23.1 | 20 | 16.9 | 686 | 1.9 | 0.9 | 3.4 | 0 | 0 | 21 | 0.048 | 81 |  | 11 | 0.027 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1978 | 33 | 300.9 | 16 | 186.8 | 3963.1 | 8.7 | 41 | 5.2 | 59.2 | 0 | 10 | 0.008 | 55 |  | 192 | 0.005 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1978 | 33 | 476 | 12 | 364.7 | 4723.4 | 4.3 | 36.7 | 14.1 | 56.2 | 0 | 6 | 0.009 | 76 |  | 131 | 0.005 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1977 | 34 | 527 | 30 | 163 | 1225 | 113 | 16 | 40 | 1 | 194 | 24 | 0.054 | 47 |  | 20 | 0.036 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1977 | 34 | 215 | 44 | 121 | 1349 | 9 | 6 | 20 | 1 | 58 | 24 | 0.042 | 50 |  | 14.1 | 0.021 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1977 | 34 | 279 | 46 | 144 | 1561 | 38 | 6 | 19 | 0 | 72 | 21 | 0.048 | 57 |  | 14.6 | 0.02 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1977 | 34 | 337.7 | 62 | 146.3 | 1430.9 | 52.2 | 8.4 | 26.5 | 3.4 | 100.9 | 19 | 0.052 | 44 |  | 6 | 0.04 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1977 | 34 | 527.4 | 50 | 384.3 | 3671.9 | 41.2 | 8.2 | 24.5 | 3.4 | 65.8 | 28 | 0.051 | 45 |  | 10.2185 | 0.029106 | 2-furfural and carbon oxide levels are trending upwards. Other test results are assessed as acceptable.
33000 | 1977 | 34 | 340.3 | 26 | 191.9 | 2222.5 | 49.9 | 7.9 | 18.7 | 2 | 69.9 | 23 | 0.044 | 39 |  | 5 | 0.047 | Dissolved gas analysis is assessed as acceptable. Acetylene gas possibly communicating from tapchanger. | Oil quality is assessed as acceptable.
33000 | 1977 | 34 | 410.9 | 42 | 244.3 | 2726.6 | 24.6 | 7.2 | 23.8 | 1.4 | 109.6 | 23 | 0.049 | 28 |  | 8 | 0.032 | DGA is assessed as acceptable. | Breakdown voltage is low. Other oil quality results are assessed as acceptable.
33000 | 1977 | 34 | 345.1 | 49 | 169.1 | 1990.3 | 51.7 | 8.1 | 23.3 | 0.5 | 92.4 | 27 | 0.056 | 30 |  | 6 | 0.037 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1977 | 34 | 438.6 | 44 | 209.4 | 2312.3 | 48.7 | 9.2 | 22.3 | 0.5 | 148.5 | 23 | 0.061 | 60 |  | 8 | 0.03 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1977 | 34 | 362.6 | 45 | 198.8 | 2097.4 | 38.6 | 8.2 | 24.5 | 0.7 | 91.8 | 19 | 0.049 | 72 |  | 9 | 0.035 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable. Corrosive IEC. Corrosive ASTM 4B.
33000 | 1977 | 34 | 136.2 | 35 | 82.5 | 1250.3 | 14.3 | 2.4 | 8.4 | 0.6 | 28 | 18 | 0.055 | 65 |  | 9 | 0.028 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable. Corrosive IEC. Corrosive ASTM 4B.
33000 | 1977 | 34 | 115.5 | 38 | 65.6 | 1140.6 | 16.4 | 2.1 | 7.8 | 0.3 | 23.3 | 18 | 0.051 | 66 |  | 9 | 0.027 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1977 | 34 | 435 | 43 | 204 | 2119 | 92 | 10 | 21 | 1 | 107 | 19 | 0.029 | 47 |  | 36.3 | 0.009 | Acetylene level quite high. Probably from tapchanger ?
33000 | 1977 | 34 | 598 | 42 | 317 | 3182 | 83 | 12 | 33 | 2 | 151 | 24 | 0.043 | 45 |  | 29.3 | 0.011 | See previous comment otherwise test results satisfactory.
33000 | 1977 | 34 | 767 | 50 | 443 | 4076 | 69 | 18 | 53 | 2 | 182 | 20 | 0.04 | 43 |  | 8.9 | 0.036 | Test results satisfactory. Acetylene gas possibly from tapchanger.
33000 | 1977 | 34 | 773 | 57 | 326 | 2946 | 78 | 20 | 45 | 2 | 302 | 25 | 0.034 | 42 |  | 17.1 | 0.019 | 2-Furfural level is above 1PPM. Other test results are assessed as acceptable. Acetylene gas possibly from tapchanger.
33000 | 1977 | 34 | 385 | 44 | 154 | 1610 | 39 | 11 | 31 | 4 | 146 | 11 | 0.053 | 75 |  | 13 | 0.02 | 2-furfural is trending upwards. Other test results are assessed as acceptable. RECOMMEND RESAMPLE IN 1 YEAR TO MONITOR TREND.
33000 | 1977 | 34 | 407.7 | 53 | 173.7 | 1559.8 | 52 | 10.2 | 31.4 | 0.9 | 139.5 | 25 | 0.039 | 35 |  | 6 | 0.051 | Test results are relatively stabe. | Oil quality is assessed as acceptable.
33000 | 1977 | 34 | 258.4 | 44 | 113.6 | 1609.2 | 22.1 | 5.8 | 22.1 | 3.7 | 91.1 | 9 | 0.035 | 75 |  | 12 | 0.021 | DGA is assessed as acceptable. | Other test results are relatively stable.
33000 | 1977 | 34 | 568.5 | 54 | 359.1 | 3183.8 | 74.1 | 9.1 | 23.9 | 5.2 | 97.1 | 24 | 0.043 | 36 |  | 13 | 0.02 | DGA is assessed as acceptable. | Other test results are assessed as acceptable.
33000 | 1977 | 34 | 448.2 | 46 | 270.8 | 2682.8 | 32.9 | 8.3 | 22.8 | 2.8 | 110.6 | 23 | 0.035 | 47 |  | 9 | 0.033 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1977 | 34 | 487.5 | 45 | 284 | 3159.1 | 41.3 | 8.6 | 27.9 | 1.4 | 124.3 | 22 | 0.045 | 44 |  | 8 | 0.044 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1977 | 34 | 358 | 40 | 215 | 2508 | 18.9 | 5.8 | 22.5 | 1.5 | 94.3 | 18 | 0.044 | 44 |  | 10 | 0.028 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1977 | 34 | 349.4 | 56 | 248.9 | 2931 | 17.5 | 4.7 | 15 | 0.7 | 62.6 | 22 | 0.042 | 42 |  | 10 | 0.032 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable. Corrosive IEC. Corrosive ASTM 4B.
33000 | 1977 | 34 | 232.7 | 41.81 | 152.6 | 1972.5 | 17.1 | 6.9 | 8.6 | 2.1 | 45.4 | 22 | 0.035 | 60 |  | 8 | 0.039 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1977 | 34 | 263.1 | 48 | 72.8 | 1378.1 | 43.4 | 7.7 | 16.8 | 0 | 122.4 | 19 | 0.035 | 52 |  | 11 | 0.024 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1977 | 34 | 364.9 | 28 | 113 | 1748.9 | 36.5 | 12.8 | 25.2 | 1.5 | 175.9 | 22 | 0.032 | 50 |  | 11 | 0.028 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1977 | 34 | 464 | 41.81 | 142 | 1295 | 80 | 11 | 22 | 0 | 209 | 22 | 0.037 | 72 |  | 17.2 | 0.016 | Test results are assessed as acceptable. Acetylene gas is possibly from tapchanger. | Oil quality is assessed as acceptable.
33000 | 1977 | 34 | 557.6 | 30 | 204.4 | 2501.5 | 75.6 | 15.6 | 32 | 3.9 | 226.1 | 15 | 0.046 | 51 |  | 12 | 0.02 | The test results are assessed as acceptable. Acetylene gas possibly from tapchanger. | Oil quality is assessed as acceptable.
33000 | 1977 | 34 | 706 | 40 | 432.5 | 4042.3 | 88.7 | 14 | 24.5 | 5 | 141.3 | 32 | 0.042 | 24 |  | 14 | 0.017 | Dissolved gas analysis is assessed as acceptable. | Moisture content of sample is slightly high. Breakdown voltage of sample is low.
33000 | 1977 | 34 | 281.9 | 32 | 114.6 | 1825.2 | 41.7 | 8.6 | 14.8 | 3.3 | 98.9 | 44 | 0.031 | 22 |  | 12 | 0.021 | DGA is assessed as acceptable. | Moisture content is high. Breakdown voltage is low. Other oil quality results are assessed as acceptable.
33000 | 1977 | 34 | 125.9 | 32 | 77.1 | 1281.7 | 9.3 | 4.1 | 8.3 | 13.7 | 13.4 | 43 | 0.033 | 21 |  | 16 | 0.016 | DGA is assessed as acceptable. | Breakdown voltage is low. Moisture content is high. Other oil quality results are assessed as acceptable.
33000 | 1977 | 34 | 100.2 | 34 | 59 | 1026.4 | 13.1 | 3.2 | 4.3 | 4.5 | 16.1 | 20 | 0.037 | 51 |  | 13 | 0.022 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1977 | 34 | 81.9 | 45 | 62.2 | 1148.1 | 7.5 | 0.8 | 2.5 | 1.1 | 7.8 | 25 | 0.037 | 23 |  | 13 | 0.02 | DGA is assessed as acceptable. | Breakdown voltage is low. Other oil quality results are acceptable.
33000 | 1977 | 34 | 518.5 | 38 | 114.4 | 2052.8 | 53.5 | 33.5 | 65.3 | 230.1 | 21.7 | 71 | 0.03 | 24 |  | 15 | 0.02 | DGA suggests mild oil overheating (<300C) has occurred. | Breakdown voltage is low. Other oil quality results are assessed as acceptable. Oil is cloudy in appearance.
33000 | 1977 | 34 | 131.6 | 34 | 72.7 | 1398.9 | 17.7 | 4 | 5.4 | 7.1 | 24.7 | 53 | 0.028 | 12 |  | 16 | 0.014 | DGA is assessed as acceptable. | Breakdown voltage is low. Other oil quality results are assessed as acceptable.
33000 | 1977 | 34 | 111.3 | 30 | 61.2 | 1204.3 | 17.4 | 2.6 | 4 | 1.2 | 24.9 | 25 | 0.027 | 58 |  | 13 | 0.019 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1977 | 34 | 105.5 | 30 | 59.1 | 1184.2 | 14.5 | 2.5 | 3.7 | 0.4 | 25.3 | 15 | 0.03 | 64 |  | 13 | 0.019 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1977 | 34 | 694 | 26 | 300 | 1091 | 149 | 63 | 36 | 104 | 42 | 20 | 0.042 | 72 |  | 5 | 0.116 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1977 | 34 | 1235 | 37 | 481 | 1367 | 314 | 103 | 59 | 153 | 125 | 24 | 0.054 | 50 |  | 3.4 | 0.14 | Increase in gas level. Possibly from tap changer? If not possible TX problem.
33000 | 1977 | 34 | 1306 | 38 | 630 | 2942 | 208 | 67 | 60 | 101 | 240 | 28 | 0.097 | 58 |  | 3.3 | 0.121 | Increase in gas levels. Possibly from tap changer? If not possible TX problem.
33000 | 1977 | 34 | 1419 | 40 | 919 | 4501 | 171 | 37 | 102 | 56 | 134 | 34 | 0.1 | 55 |  | 4.3 | 0.083 | Some gas levels remain high. RECOMMEND RESAMPLE IN 1 YEAR.
33000 | 1977 | 34 | 1458 | 42 | 926 | 4611 | 135 | 35 | 90 | 23 | 249 | 38 | 0.116 | 66 |  | 6.3 | 0.06 | Moisture content of oil high. Gas levels stable. RECOMMEND RESAMPLE IN 2 YEARS.
33000 | 1977 | 34 | 1564 | 65 | 995 | 4393 | 121 | 55 | 61 | 16 | 316 | 56 | 0.135 | 29 |  | 4.2 | 0.061 | Moisture content of oil high. Dielectric strength slightly low. Other test results satisfactory. Acetylene gas possibly from tapchanger.
33000 | 1977 | 34 | 1401 | 38 | 1023 | 5309 | 107 | 59 | 55 | 17 | 140 | 25 | 0.148 | 35 |  | 4.8 | 0.048 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1977 | 34 | 988.5 | 41.81 | 680.6 | 6519.9 | 77.4 | 36.6 | 56.5 | 28.8 | 108.6 | 63 | 0.219 | 26 |  | 4 | 0.061 | DGA is assessed as acceptable. | Oil quality is poor.
33000 | 1977 | 34 | 1606.7 | 50 | 1023.8 | 10149.9 | 298.3 | 73 | 68.6 | 31.8 | 111.2 | 78 | 0.256 | 17 |  | 4 | 0.063 | Carbon oxide levels are high. | Moisture content of sample is very high. Breakdown voltage is low. Acidity level of sample is high.
33000 | 1977 | 34 | 1221.7 | 50 | 731.4 | 8379.3 | 195.3 | 60 | 62 | 25.4 | 147.6 | 67 | 0.251 | 25 |  | 4 | 0.051 | Dissolved gas analysis and oil quality results are consistent with main tank sample. | Oil quality is poor.
33000 | 1977 | 34 | 999.3 | 54 | 707 | 6464.6 | 94.2 | 26.3 | 43.8 | 19.1 | 108.9 | 75 | 0.234 | 19 |  | 5 | 0.054 | Dissolved gas levels are reduced slightly. | Oil quality is poor.
33000 | 1977 | 34 | 747 | 35 | 509.6 | 5825.8 | 85.3 | 17.2 | 31.7 | 10.4 | 92.8 | 48 | 0.233 | 19 |  | 5 | 0.046 | Dissolved gas levels are relatively stable. | Oil quality is poor.
33000 | 1977 | 34 | 781.7 | 46 | 450.5 | 5075.4 | 130.7 | 20 | 36 | 6.8 | 137.7 | 64 | 0.216 | 27 |  | 4 | 0.062 | DGA is assessed as acceptable. | Oil quality is poor.
33000 | 1977 | 34 | 738.3 | 30 | 379.8 | 4516.2 | 114.8 | 24.2 | 40.7 | 8.3 | 170.5 | 42 | 0.245 | 28 |  | 3 | 0.071 | DGA is assessed as acceptable. | Oil quality is poor.
33000 | 1977 | 34 | 784.8 | 41 | 547.4 | 6409.8 | 82.7 | 16.7 | 35 | 4.1 | 98.9 | 51 | 0.267 | 23 |  | 5 | 0.047 | DGA is assessed as acceptable. | Oil quality is poor.
33000 | 1977 | 34 | 519.3 | 36 | 416.1 | 5781.8 | 40 | 7.4 | 13.6 | 3.6 | 38.6 | 46 | 0.229 | 35 |  | 5 | 0.047 | DGA is assessed as acceptable. | Oil quality is poor. Corrosive IEC. Corrosive ASTM 4A.
33000 | 1977 | 34 | 155 | 41.81 | 106 | 1595 | 0 | 2 | 34 | 0 | 13 | 14 | 0.356 | 57 |  | 35 | 0.0125 | Test results satisfactory. | ACIDITY LEVEL SHOULD BE NOTED.
33000 | 1977 | 34 | 220 | 50 | 130 | 1911 | 15 | 3 | 28 | 3 | 41 | 16 | 0.066 | 47 |  | 10.6 | 0.026 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1977 | 34 | 178 | 106 | 128 | 1883 | 0 | 2 | 20 | 1 | 27 | 39 | 0.095 | 58 |  | 6 | 0.046 | Test results satisfactory. | Moisture content slightly high; possibly sample contamination.
33000 | 1977 | 34 | 166 | 75 | 107 | 2228 | 0 | 3 | 20 | 1 | 35 | 31 | 0.091 | 56 |  | 8.4 | 0.031 | Test results satisfactory before oil change. | Oil quality is assessed as acceptable. PCB contaminated oil.
33000 | 1977 | 34 | 3 | 20 | 0 | 559 | 0 | 1 | 1 | 0 | 1 | 16 | 0.013 | 65 |  | 31.7 | 0.019 | Test results satisfactory after oil change. | Oil quality is assessed as acceptable. PCB contaminated oil.
33000 | 1977 | 34 | 438 | 47 | 131 | 3554 | 46 | 11 | 46 | 1 | 203 | 23 | 0.029 | 65 |  | 17.6 | 0.0145 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1977 | 34 | 310 | 58 | 140 | 3342 | 2 | 3 | 37 | 1 | 127 | 18 | 0.043 | 24 |  | 12.8 | 0.026 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1977 | 34 | 250 | 41.81 | 159 | 2403 | 10 | 4 | 26 | 2 | 49 | 18 | 0.056 | 72 |  | 11.4 | 0.028 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1977 | 34 | 327 | 49 | 190 | 3337 | 9 | 4 | 42 | 10 | 72 | 15 | 0.056 | 75 |  | 9 | 0.032 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1977 | 34 | 264.9 | 50 | 91.9 | 1747.9 | 21 | 8.6 | 39.7 | 6.7 | 97 | 19 | 0.052 | 59 |  | 8 | 0.035 | DGA is assessed as acceptable. Acetylene possibly from tapchanger. | Oil quality is assessed as acceptable.
33000 | 1977 | 34 | 274.1 | 70 | 175.6 | 2862.2 | 11.7 | 5.7 | 26.6 | 3.2 | 51.3 | 44 | 0.07 | 24 |  | 7 | 0.04 | DGA is assessed as acceptable. | Moisture content is high. Breakdown voltage is low. Other oil quality results are assessed as acceptable.
33000 | 1977 | 34 | 502 | 64 | 299.3 | 4961.5 | 18.4 | 10 | 52.9 | 3.1 | 118.3 | 40 | 0.083 | 21 |  | 8 | 0.036 | DGA is assessed as acceptable. | Moisture content is high. Breakdown voltage is low. Other oil quality results are assessed as acceptable.
33000 | 1977 | 34 | 356.9 | 52 | 263.5 | 4879.1 | 13.2 | 5.5 | 32.6 | 2 | 40.1 | 28 | 0.096 | 38 |  | 5 | 0.053 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1977 | 34 | 316.9 | 49 | 221.2 | 3338.3 | 12.9 | 4.6 | 31.4 | 2.5 | 44.3 | 23 | 0.108 | 49 |  | 5 | 0.046 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1977 | 34 | 237.1 | 81 | 154.4 | 2227.9 | 7.1 | 3.4 | 30 | 4.7 | 37.5 | 32 | 0.118 | 28 |  | 5 | 0.055 | DGA is assessed as acceptable. | Breakdown voltage is low. Other oil quality results are assessed as acceptable. Corrosive IEC. Non-corrosive ASTM 3B.
33000 | 1977 | 34 | 292.1 | 50 | 224.2 | 3040 | 12.1 | 3.9 | 25 | 0 | 26.9 | 69 | 0.119 | 18 |  | 6 | 0.045 | DGA is assessed as acceptable. | Breakdown voltage is low. Other oil quality results are assessed as acceptable.
33000 | 1977 | 34 | 213.1 | 60 | 148.4 | 2498.2 | 9.9 | 3.5 | 20.4 | 0.1 | 30.8 | 54 | 0.12 | 11 |  | 6 | 0.041 | DGA is assessed as acceptable. | Breakdown voltage is low. Other oil quality results are assessed as acceptable.
33000 | 1977 | 34 | 193 | 41.81 | 142 | 1425 | 0 | 2 | 31 | 0 | 18 | 15 | 0.036 | 59.8 |  | 11 | 0.0294 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1977 | 34 | 239 | 37 | 135 | 2123 | 0 | 3 | 28 | 1 | 72 | 29 | 0.077 | 52 |  | 10.3 | 0.025 | DGA is assessed as acceptable. | Moisture content slightly high; possibly sample contamination.
33000 | 1977 | 34 | 294 | 58 | 204 | 3178 | 2 | 3 | 29 | 1 | 55 | 28 | 0.119 | 60 |  | 4.9 | 0.045 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1977 | 34 | 335 | 52 | 248 | 2756 | 10 | 5 | 26 | 2 | 44 | 27 | 0.139 | 62 |  | 4.2 | 0.06 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1977 | 34 | 294 | 44 | 211 | 2863 | 14 | 4 | 30 | 4 | 31 | 20 | 0.148 | 75 |  | 4 | 0.064 | Test results are relatively stable. | Oil quality is assessed as acceptable.
33000 | 1977 | 34 | 266 | 50 | 136.2 | 2104.8 | 18.5 | 6.8 | 33.9 | 5.2 | 65.4 | 22 | 0.145 | 58 |  | 4 | 0.064 | The test results are assessed as relatively stable. Acetylene gas possibly from tapchanger. | Oil quality is assessed as acceptable.
33000 | 1977 | 34 | 372.5 | 59 | 276.9 | 3275.2 | 17.1 | 6.1 | 26.1 | 2.8 | 43.5 | 38 | 0.182 | 39 |  | 3 | 0.071 | DGA is assessed as acceptable. | Moisture content is high. Oil quality is deteriorating.
33000 | 1977 | 34 | 588.3 | 62 | 401.1 | 5747.5 | 24.5 | 10.3 | 45.2 | 2.1 | 105.1 | 47 | 0.21 | 17 |  | 4 | 0.069 | DGA is assessed as acceptable. | Oil quality is poor.
33000 | 1977 | 34 | 324.5 | 52 | 191 | 2795.6 | 15.9 | 6.9 | 35 | 8.8 | 66.9 | 20 | 0.193 | 75 |  | 3 | 0.072 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable at present.
33000 | 1977 | 34 | 272.2 | 47 | 166.4 | 2209.6 | 10.8 | 5.9 | 26.3 | 5.2 | 57.6 | 26 | 0.223 | 75 |  | 3 | 0.078 | DGA is assessed as acceptable. | Acidity level is high. Other oil quality results are assessed as acceptable. Corrosive IEC. Non-corrosive ASTM 3A.
33000 | 1977 | 34 | 106.8 | 52 | 59.6 | 1720.4 | 4.9 | 2.7 | 12.6 | 0.8 | 26.2 | 22 | 0.21 | 69 |  | 2 | 0.093 | DGA is assessed as acceptable. | Acidity level is high. Other oil quality results are assessed as acceptable.
33000 | 1977 | 34 | 232 | 30 | 118 | 1436 | 23 | 5 | 12 | 1 | 73 | 13 | 0.035 | 71 |  | 30 | 0.0133 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1977 | 34 | 361 | 40 | 99 | 1082 | 42 | 11 | 21 | 1 | 187 | 22 | 0.075 | 52 |  | 9.8 | 0.023 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1977 | 34 | 653 | 56 | 416 | 4435 | 25 | 11 | 47 | 8 | 146 | 20 | 0.09 | 41 |  | 4.9 | 0.063 | Dissolved gas analysis is assessed as acceptable. Acetylene gas possibly communicating from tapchanger. | Oil quality is assessed as acceptable.
33000 | 1977 | 34 | 355 | 41.81 | 314 | 5398 | 5 | 4 | 6 | 4 | 22 | 52 | 0.177 | 24 |  | 5.1287 | 0.04763 | 2-furfural level is high suggesting advanced state of insulation degradation. Moisture content of sample is high. Breakdown voltage of sample is low. Acidity level of sample is high. Dissolved gas analysis is assessed as acceptable. RECOMMEND RESAMPL
33000 | 1977 | 34 | 199.3 | 50 | 165.4 | 3143.2 | 8.6 | 3 | 5.9 | 2 | 14.4 | 26 | 0.15 | 64 |  | 4 | 0.061 | 2-furfural level is high suggesting advanced state of insulation degradation. Other test results are assessed as acceptable. RECOMMEND RESAMPLE IN 1 YEAR TO MONITOR CONDITION.
33000 | 1977 | 34 | 301.5 | 65 | 250.7 | 4331.5 | 14.4 | 5 | 8.2 | 2 | 21.2 | 49 | 0.161 | 26 |  | 3 | 0.064 | Dissolved gas analysis is assessed as acceptable. | Moisture content is high. Breakdown voltage is low. Oil sample was cloudy in appearance.
33000 | 1977 | 34 | 250.6 | 50 | 195.7 | 4023 | 11.9 | 4.5 | 8.9 | 2.6 | 27 | 27 | 0.168 | 52 |  | 3 | 0.066 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1977 | 34 | 438.4 | 51 | 382.5 | 7821.1 | 15.3 | 5.7 | 8.4 | 1.7 | 24.8 | 32 | 0.19 | 32 |  | 4 | 0.062 | DGA is assessed as acceptable. | Moisture content is slightly high. Acidity level is increased. Other oil quality results are assessed as acceptable.
33000 | 1977 | 34 | 448.6 | 58 | 354.8 | 6733.8 | 21.5 | 7.6 | 13.4 | 2.6 | 48.7 | 32 | 0.202 | 38 |  | 4 | 0.057 | DGA is assessed as acceptable. | Moisture content is slightly high. Acidity level is high. Other oil quality results are assessed as acceptable.
33000 | 1977 | 34 | 227.2 | 45 | 190.2 | 3014.8 | 8.7 | 3.2 | 5.2 | 1.2 | 18.7 | 30 | 0.197 | 38 |  | 4 | 0.063 | DGA is assessed as acceptable. | Acidity level is high but stable. Breakdown voltage is low.
33000 | 1977 | 34 | 167.2 | 50 | 123.2 | 2335 | 7.8 | 5 | 7 | 1.8 | 22.4 | 28 | 0.207 | 60 |  | 4 | 0.053 | DGA is assessed as acceptable. | Acidity level is high. Other oil quality results are assessed as acceptable. Corrosive IEC. Non-corrosive ASTM 3B.
33000 | 1977 | 34 | 186 | 31 | 76 | 1235 | 0 | 3 | 12 | 1 | 94 | 10 | 0.023 | 67 |  | 15 | 0.029 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1977 | 34 | 441 | 40 | 100 | 1262 | 42 | 12 | 32 | 2 | 253 | 15 | 0.056 | 64 |  | 11.4 | 0.023 | Test results are assessed as acceptable. Acetylene gas possibly from tapchanger. | Oil quality is assessed as acceptable.
33000 | 1977 | 34 | 300 | 50 | 205 | 3005 | 14 | 4 | 15 | 8 | 54 | 19 | 0.085 | 75 |  | 3 | 0.089 | DGA is assessed as acceptable. | Other test results are assessed as acceptable.
33000 | 1977 | 34 | 359.5 | 65 | 179.3 | 1815.2 | 17.9 | 6.5 | 23.3 | 10 | 122.5 | 18 | 0.092 | 75 |  | 3 | 0.108 | DGA is assessed as acceptable. | Other test results are assessed as acceptable.
33000 | 1977 | 34 | 329.7 | 40 | 120.8 | 2529.4 | 16.2 | 6.9 | 26.8 | 6.6 | 152.4 | 22 | 0.095 | 63 |  | 3 | 0.089 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1977 | 34 | 305.1 | 40 | 176.3 | 2912.6 | 13.8 | 8.2 | 12.5 | 0.8 | 93.5 | 20 | 0.103 | 75 |  | 2 | 0.109 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1977 | 34 | 261.1 | 46 | 187.3 | 2427.8 | 9.7 | 3.7 | 8.8 | 1.4 | 50.2 | 16 | 0.102 | 65 |  | 2 | 0.132 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1977 | 34 | 215.9 | 40 | 158.7 | 2016.7 | 8.2 | 2.7 | 8 | 1.3 | 37 | 16 | 0.15 | 57 |  | 2 | 0.13 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1977 | 34 | 154.1 | 43 | 110.9 | 1941.1 | 5 | 2.4 | 6.4 | 0.7 | 28.7 | 15 | 0.133 | 75 |  | 2 | 0.113 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1977 | 34 | 190.6 | 48 | 148.3 | 2751.8 | 5.9 | 2.1 | 5.5 | 1.2 | 27.6 | 15 | 0.15 | 87 |  | 2 | 0.138 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable. Non-corrosive IEC. Non-corrosive ASTM 3A.
33000 | 1977 | 34 | 315.6 | 51 | 250.1 | 2387.8 | 12.5 | 20.6 | 7.5 | 0.5 | 24.4 | 22 | 0.154 | 80 |  | 2 | 0.121 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1977 | 34 | 140.2 | 48 | 112.6 | 1465.6 | 5.8 | 2.8 | 3 | 1.4 | 14.6 | 18 | 0.15 | 80 |  | 2 | 0.106 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1977 | 34 | 0 | 41.81 | [7 empty] | 13 | 0.019 | 46 |  | 25 | 0.011 | DGA is assessed as acceptable.
33000 | 1977 | 34 | 196 | 33 | 104 | 1319 | 0 | 3 | 31 | 1 | 57 | 17 | 0.038 | 56 |  | 14 | 0.0248 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1977 | 34 | 457 | 37 | 79 | 1481 | 38 | 7 | 54 | 2 | 277 | 14 | 0.041 | 65 |  | 17.9 | 0.019 | Acetylene (C2H2) gas probably from tapchanger. Test results satisfactory.
33000 | 1977 | 34 | 523 | 32 | 112 | 1511 | 24 | 8 | 64 | 2 | 313 | 28 | 0.045 | 20 |  | 11.6 | 0.02 | Test results are assessed as acceptable. Acetylene was possibly from tapchanger. | Oil quality is assessed as acceptable.
33000 | 1977 | 34 | 464.6 | 40 | 162.3 | 2911.3 | 11.8 | 3.6 | 79.3 | 8.5 | 199.1 | 20 | 0.06 | 31 |  | 6 | 0.036 | The test results are assessed as acceptable. Acetylene gas possibly from tapchanger. | Oil quality is assessed as acceptable.
33000 | 1977 | 34 | 307.3 | 42 | 147.1 | 1968.5 | 13.3 | 11.9 | 52.9 | 7.8 | 74.3 | 40 | 0.058 | 22 |  | 5 | 0.045 | DGA is assessed as acceptable. | Moisture content is high. Breakdown voltage is low. Possible sample contamination. Other oil quality results are assessed as acceptable.
33000 | 1977 | 34 | 320 | 35 | 117.2 | 2052.4 | 4.9 | 18.5 | 85.7 | 11 | 82.7 | 12 | 0.064 | 75 |  | 7 | 0.032 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1977 | 34 | 257.9 | 35 | 137.5 | 1739.6 | 12.3 | 5.2 | 29.7 | 0.3 | 72.9 | 13 | 0.062 | 74 |  | 6 | 0.035 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1977 | 34 | 214.8 | 36 | 134.8 | 1821.8 | 4.3 | 3 | 25.6 | 0 | 47.1 | 16 | 0.077 | 53 |  | 5 | 0.042 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1977 | 34 | 268.1 | 24 | 158.7 | 2017.3 | 10.4 | 4.9 | 27.1 | 1.1 | 65.9 | 45 | 0.078 | 16 |  | 6 | 0.038 | DGA is assessed as acceptable. | Breakdown voltage is low.
33000 | 1977 | 34 | 242.6 | 21 | 180.7 | 2338.8 | 5.6 | 2.6 | 22.8 | 1 | 29.9 | 22 | 0.087 | 25 |  | 5 | 0.046 | DGA is assessed as acceptable. | Breakdown voltage is low. Other oil quality results are assessed as acceptable. Corrosive IEC. Non-corrosive ASTM 2D.
33000 | 1977 | 34 | 304.3 | 46 | 216 | 2288.2 | 7.9 | 16.7 | 25.2 | 0.4 | 38.1 | 27 | 0.087 | 37 |  | 4 | 0.067 | DGA is assessed as acceptable. | Breakdown voltage is low. Other oil quality results are assessed as acceptable.
33000 | 1977 | 34 | 189.9 | 41.81 | 137.5 | 2157.4 | 4.5 | 2.9 | 18.5 | 0 | 26.5 | 52 | 0.085 | 29 |  | 6 | 0.042 | DGA is assessed as acceptable. | Breakdown voltage is low. Other oil quality results are assessed as acceptable.
33000 | 1977 | 34 | 171.3 | 30 | 105.7 | 1341.7 | 7 | 3.8 | 14.9 | 0.3 | 39.6 | 11 | 0.078 | 67 |  | 6 | 0.04 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1977 | 34 | 0 | 41.81 | [7 empty] | 10 | 0.021 | 55 |  | 35 | 0.011 | Test results satisfactory.
33000 | 1977 | 34 | 553 | 31 | 222 | 1306 | 246 | 27 | 23 | 15 | 20 | 40 | 0.037 | 24 |  | 15 | 0.02 | Moisture slightly high.Electric strength low. H2 level slightly high.
33000 | 1977 | 34 | 468 | 40 | 227 | 1954 | 40 | 4 | 44 | 1 | 152 | 16 | 0.041 | 62 |  | 12.8 | 0.026 | Acetylene (C2H2) probably from tapchanger. Test results satisfactory.
33000 | 1977 | 34 | 667 | 40 | 267 | 2078 | 40 | 7 | 61 | 2 | 290 | 49 | 0.043 | 35 |  | 11.3 | 0.022 | Moisture content of oil is quite high. Dissolved gas analysis suggests hot spot in oil. Other test results are assessed as acceptable. RECOMMEND RESAMPLE IN 1 YEAR TO MONITOR ETHYLENE.
33000 | 1977 | 34 | 692 | 60 | 267 | 1972 | 23 | 10 | 69 | 2 | 321 | 28 | 0.046 | 26 |  | 12.4 | 0.019 | Gas levels have remained fairly stable. Other test results are assessed as acceptable. RECOMMEND RESAMPLE IN 1 YEAR TO MONITOR
33000 | 1977 | 34 | 353 | 45 | 141 | 1434 | 10 | 7 | 43 | 0 | 152 | 21 | 0.04 | 56 |  | 9.6 | 0.027 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1977 | 34 | 184.8 | 28 | 102.3 | 1834 | 8.4 | 3.4 | 21 | 1.5 | 48.2 | 58 | 0.04 | 14 |  | 8 | 0.03 | DGA is assessed as acceptable. | Moisture content is high. Breakdown voltage is low. Other oil quality results are assessed as acceptable. Possible sample contamination.
33000 | 1977 | 34 | 147.4 | 55 | 92.8 | 1689.8 | 1.7 | 2.2 | 19.5 | 0.7 | 30.5 | 31 | 0.059 | 30 |  | 6 | 0.041 | DGA is assessed as acceptable. | Breakdown voltage is low. Moisture content is high. Other oil quality results are assessed as acceptable.
33000 | 1977 | 34 | 202.7 | 41.81 | 125.5 | 2136.4 | 7.8 | 3.7 | 21.2 | 1.1 | 43.4 | 56 | 0.06 | 15 |  | 9 | 0.03 | DGA is assessed as acceptable. | Breakdown voltage is low. Other oil quality results are assessed as acceptable.
33000 | 1977 | 34 | 185.3 | 41.81 | 139.8 | 2040.4 | 2.9 | 2 | 17.8 | 1 | 21.8 | 25 | 0.057 | 19 |  | 6 | 0.036 | DGA is assessed as acceptable. | Breakdown voltage is low. Other oil quality results are assessed as acceptable. Corrosive IEC. Corrosive ASTM 4A.
33000 | 1977 | 34 | 203 | 45 | 125.8 | 2570.5 | 6.3 | 2.4 | 23.9 | 1.4 | 43.2 | 67 | 0.067 | 11 |  | 5 | 0.044 | DGA is assessed as acceptable. | Breakdown voltage is low. Other oil quality results are assessed as acceptable. Sample was cloudy in appearance.
33000 | 1977 | 34 | 153.6 | 25 | 106.1 | 2398.9 | 4.4 | 1.9 | 16.3 | 0.6 | 24.3 | 57 | 0.061 | 33 |  | 6 | 0.036 | DGA is assessed as acceptable. | Breakdown voltage is low. Other oil quality results are assessed as acceptable.
33000 | 1977 | 34 | 145.4 | 41.81 | 97.9 | 2123.1 | 3.7 | 2.4 | 16.5 | 0.5 | 24.4 | 64 | 0.061 | 17 |  | 7 | 0.034 | DGA is assessed as acceptable. | Breakdown voltage is low. Other oil quality results are assessed as acceptable.
33000 | 1977 | 34 | 118.3 | 35 | 68.2 | 1736.2 | 0 | 2.9 | 14.3 | 0.4 | 32.5 | 22 | 0.055 | 72 |  | 8 | 0.032 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1977 | 34 | 310 | 38 | 154 | 1761 | 45 | 8 | 18 | 4 | 81 | 15 | 0.05 | 54 |  | 20 | 0.016 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1977 | 34 | 404 | 56 | 209 | 4138 | 19 | 9 | 23 | 7 | 137 | 19 | 0.092 | 68 |  | 4.6 | 0.058 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1977 | 34 | 319 | 47 | 188 | 2754 | 0 | 6 | 14 | 2 | 109 | 24 | 0.107 | 62 |  | 3.9 | 0.058 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1977 | 34 | 534 | 56 | 295 | 3833 | 35 | 9 | 21 | 2 | 172 | 17 | 0.113 | 53 |  | 3.6 | 0.061 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1977 | 34 | 723 | 72 | 422 | 6206 | 24 | 11 | 30 | 2 | 234 | 44 | 0.132 | 38 |  | 6.8 | 0.035 | Carbon oxide gas levels are increasing. Other test results are assessed as acceptable at present. Acetylene gas possibly from tapchanger. | Oil quality is assessed as acceptable.
33000 | 1977 | 34 | 428 | 56 | 257 | 5712 | 4 | 5 | 20 | 3 | 139 | 14 | 0.143 | 25 |  | 5 | 0.058 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1977 | 34 | 296 | 60 | 273 | 4102 | 0 | 1 | 5 | 2 | 15 | 40 | 0.211 | 28 |  | 3.9815 | 0.06061 | DGA is assessed as acceptable. | Moisture content of sample is high. Breakdown voltage of sample is low. Acidity level of sample is high.
33000 | 1977 | 34 | 172.4 | 51 | 141.5 | 2511 | 8.4 | 3.2 | 5.1 | 1.9 | 12.3 | 25 | 0.184 | 73 |  | 3 | 0.069 | The test results are assessed as relatively stable.
33000 | 1977 | 34 | 243.2 | 59 | 202.7 | 3351.4 | 11 | 3.7 | 5.7 | 2 | 18.1 | 36 | 0.19 | 32 |  | 3 | 0.081 | DGA is assessed as acceptable. | Moisture content is high. Other oil quality results are assessed as acceptable.
33000 | 1977 | 34 | 179 | 39 | 129 | 3356 | 9 | 4 | 8 | 2 | 27 | 23 | 0.209 | 41 |  | 4 | 0.06 | DGA is assessed as acceptable. | Acidity level is high but stable. Other oil quality results are assessed as acceptable.
33000 | 1977 | 34 | 146.7 | 52 | 107.7 | 2159 | 6.7 | 2.9 | 5.6 | 0.5 | 23.3 | 25 | 0.216 | 70 |  | 4 | 0.053 | DGA is assessed as acceptable. | Acidity level is high but stable. Other oil quality results are assessed as acceptable.
33000 | 1977 | 34 | 117.9 | 48 | 100.2 | 2131 | 0 | 1.9 | 3.7 | 0 | 12.1 | 20 | 0.25 | 67 |  | 4 | 0.05 | DGA is assessed as acceptable. | Acidity level is high. Other oil quality results are assessed as acceptable.
33000 | 1977 | 34 | 77.1 | 38 | 57.6 | 1567.6 | 0 | 1.9 | 3.3 | 0.8 | 13.5 | 14 | 0.208 | 68 |  | 4 | 0.065 | DGA is assessed as acceptable. | Acidity level is high. Other oil quality results are assessed as acceptable. Corrosive IEC. Non-corrosive ASTM 3B.
33000 | 1977 | 34 | 162 | 40 | 78 | 1068 | 20 | 4 | 11 | 1 | 48 | 12 | 0.038 | 55 |  | 15 | 0.026 | Test results satisfactory. | Oil quality is assessed as acceptable.
33000 | 1977 | 34 | 360 | 65 | 222 | 3682 | 15 | 5 | 14 | 2 | 102 | 27 | 0.075 | 55 |  | 10.6 | 0.025 | Test results satisfactory. | Oil quality is assessed as acceptable.
33000 | 1977 | 34 | 230 | 28 | 132 | 3310 | 14 | 5 | 12 | 2 | 65 | 16 | 0.083 | 66 |  | 7.3 | 0.041 | Test results satisfactory. | Oil quality is assessed as acceptable.
33000 | 1977 | 34 | 463 | 54 | 256 | 3571 | 26 | 8 | 23 | 2 | 148 | 19 | 0.088 | 40 |  | 4.1 | 0.065 | Test results are assessed as acceptable. Acetylene gas possibly from tapchanger. | Oil quality is assessed as acceptable.
33000 | 1977 | 34 | 2 | 20 | 2 | 142 | 0 | 0 | 0 | 0 | 0 | 7 | 0.011 | 35 |  | 89.3 | 0.01 | Test results are assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1977 | 34 | 101.1 | 44 | 65.4 | 1654.8 | 0.3 | 4.2 | 11.3 | 0 | 19.9 | 9 | 0.026 | 75 |  | 15 | 0.021 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1977 | 34 | 141 | 42 | 83.5 | 1556 | 8.2 | 2.1 | 14.9 | 0.7 | 31.6 | 10 | 0.027 | 75 |  | 15 | 0.021 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1977 | 34 | 126.4 | 40 | 63.7 | 1494 | 18.2 | 2 | 11.8 | 0.2 | 30.5 | 11 | 0.031 | 75 |  | 16 | 0.018 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1977 | 34 | 110.8 | 42 | 73.1 | 1607.8 | 3.4 | 1.5 | 11.7 | 0.4 | 20.7 | 10 | 0.03 | 68 |  | 8 | 0.049 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable. Corrosive IEC. Corrosive ASTM 4A.
33000 | 1977 | 34 | 150.4 | 45 | 119.8 | 1466.3 | 7.3 | 1.3 | 10.4 | 0.5 | 11.1 | 32 | 0.031 | 23 |  | 27 | 0.012 | DGA is assessed as acceptable. | Breakdown voltage is low. Other oil quality results are assessed as acceptable.
33000 | 1977 | 34 | 83.6 | 46 | 48.3 | 942.6 | 6.3 | 1.5 | 7.6 | 0.5 | 19.4 | 10 | 0.03 | 77 |  | 16 | 0.019 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1977 | 34 | 121 | 41.81 | 103 | 1533 | 15 | 1 | 1 | 1 | 0 | 13 | 0.073 | 63 |  | 9.7 | 0.021 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1977 | 34 | 163.2 | 21.1 | 145.3 | 1721.3 | 14 | 1.4 | 1.5 | 1 | 0 | 12 | 0.091 | 64 |  | 7.8 | 0.032 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1977 | 34 | 123.8 | 40 | 111.9 | 1772.5 | 9.3 | 1.4 | 1 | 0.2 | 0 | 12 | 0.102 | 75 |  | 7 | 0.03 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1977 | 34 | 109.8 | 17 | 107.6 | 1466.4 | 0 | 1.2 | 0.8 | 0.2 | 0 | 16 | 0.102 | 75 |  | 8 | 0.032 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable. Corrosive IEC. Non-corrosive ASTM 3A.
33000 | 1977 | 34 | 107.8 | 23 | 100.3 | 1475 | 5.1 | 1.3 | 0.7 | 0.4 | 0 | 12 | 0.115 | 83 |  | 7 | 0.031 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable. Non-corrosive IEC. Non-corrosive ASTM 3A.
33000 | 1977 | 34 | 103.7 | 17 | 100.9 | 1523.8 | 0 | 1 | 1.5 | 0.3 | 0 | 13 | 0.122 | 92 |  | 13 | 0.033 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1977 | 34 | 790 | 45 | 87 | 1131 | 175 | 42 | 85 | 3 | 398 | 15 | 0.044 | 56 |  | 45 | 0.015 | C2H2 level abnormally high. Further investigation suggested.
33000 | 1977 | 34 | 191 | 34 | 95 | 750 | 50 | 4 | 12 | 0 | 30 | 8 | 0.027 | 63 |  | 20 | 0.02 | Test results satisfactory. Oil changed during repair.
33000 | 1977 | 34 | 632 | 52 | 105 | 1001 | 229 | 26 | 46 | 1 | 225 | 14 | 0.035 | 61 |  | 25.4 | 0.015 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1977 | 34 | 593 | 55 | 194 | 2590 | 182 | 47 | 115 | 6 | 49 | 28 | 0.039 | 50 |  | 26.1 | 0.011 | Ethylene gas level quite high. Possible oil hot spot. | Oil quality is assessed as acceptable.
33000 | 1977 | 34 | 754 | 72 | 233 | 2491 | 132 | 26 | 83 | 13 | 267 | 20 | 0.032 | 64 |  | 11.1 | 0.025 | Hydrocarbon gas levels relatively stable. Test results are assessed as accetpable. | Oil quality is assessed as acceptable.
33000 | 1977 | 34 | 401.2 | 40 | 233.1 | 2982.8 | 68.9 | 18.3 | 0 | 0.6 | 80.3 | 18 | 0.032 | 47 |  | 19.6 | 0.018 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1977 | 34 | 602.5 | 45 | 297.5 | 2967.2 | 106.9 | 16.5 | 37.1 | 1.5 | 143 | 18 | 0.032 | 54 |  | 16 | 0.016 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1977 | 34 | 388 | 40 | 218.5 | 2654.8 | 44.3 | 10 | 28.8 | 0.9 | 85.5 | 15 | 0.041 | 75 |  | 17 | 0.017 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable. Corrosive IEC. Corrosive ASTM 4B.
33000 | 1977 | 34 | 274.4 | 50 | 132 | 1903.3 | 40.2 | 9.5 | 28.7 | 1.2 | 62.8 | 14 | 0.041 | 57 |  | 12 | 0.021 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1977 | 34 | 927 | 20 | 245 | 1484 | 231 | 47 | 99 | 3 | 302 | 17 | 0.075 | 58 |  | 8 | 0.038 | Combustible gas levels abnormally high further investigation suggested. | Oil quality is assessed as acceptable.
33000 | 1977 | 34 | 717 | 34 | 276 | 1804 | 162 | 29 | 71 | 2 | 177 | 10 | 0.074 | 69 |  | 9 | 0.031 | Gas levels stable; other results satisfactory.
33000 | 1977 | 34 | 1049 | 38 | 297 | 1901 | 330 | 37 | 87 | 2 | 296 | 21 | 0.075 | 54 |  | 9.3 | 0.028 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1977 | 34 | 1147 | 50 | 288 | 2215 | 163 | 51 | 112 | 4 | 529 | 21 | 0.082 | 59 |  | 6 | 0.046 | Acetylene gas level high. Possibly from tapchanger. | Oil quality is assessed as acceptable.
33000 | 1977 | 34 | 1164 | 41.81 | 219 | 2207 | 145 | 62 | 136 | 5 | 597 | 20 | 0.085 | 47 |  | 10.1 | 0.025 | Test results are assessed as acceptable. Acetylene gas possibly from tapchanger. | Oil quality is assessed as acceptable.
33000 | 1977 | 34 | 833 | 54 | 273 | 2117 | 145 | 30 | 85 | 13 | 287 | 19 | 0.079 | 75 |  | 5.6 | 0.045 | Test results are assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1977 | 34 | 596.3 | 38 | 318.1 | 3298.4 | 77.8 | 22 | 50.9 | 1 | 126.5 | 16 | 0.093 | 75 |  | 6.4 | 0.041 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1977 | 34 | 662.3 | 46 | 350.4 | 3044.2 | 89 | 17 | 42.2 | 1.4 | 162.3 | 20 | 0.084 | 65 |  | 6 | 0.035 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1977 | 34 | 508.4 | 79 | 279.6 | 2843.2 | 54.8 | 12.8 | 37.3 | 2.2 | 121.7 | 17 | 0.098 | 75 |  | 6 | 0.041 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable. Corrosive IEC. Corrosive ASTM 4B.
33000 | 1977 | 34 | 321.2 | 36 | 194.6 | 2017.4 | 35.7 | 7.6 | 25.2 | 0.5 | 57.6 | 17 | 0.095 | 54 |  | 7 | 0.035 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1977 | 34 | 257.5 | 38 | 129.6 | 1385.8 | 37.8 | 6.5 | 21.6 | 1.1 | 60.9 | 15 | 0.073 | 75 |  | 7 | 0.034 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1977 | 34 | 431 | 35 | 108 | 1029 | 76 | 20 | 49 | 2 | 176 | 10 | 0.042 | 56 |  | 8 | 0.057 | C2H2 level quite high;tapchanger? Otherwise test results satisfactory. | Oil quality is assessed as acceptable.
33000 | 1977 | 34 | 564 | 46 | 135 | 1070 | 66 | 22 | 60 | 2 | 279 | 11 | 0.044 | 59 |  | 15.3 | 0.023 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1977 | 34 | 1104 | 55 | 184 | 1271 | 212 | 62 | 100 | 3 | 543 | 18 | 0.058 | 70 |  | 16.4 | 0.02 | Acetylene gas level quite high. Possibly from tapchanger; otherwise test results satisfactory.
33000 | 1977 | 34 | 826 | 38 | 159 | 1405 | 204 | 37 | 70 | 3 | 353 | 15 | 0.052 | 72 |  | 19.9 | 0.015 | Test results are assessed as acceptable. Acetylene gas possibly from tap changer. | Oil quality is assessed as acceptable.
33000 | 1977 | 34 | 1102.0359 | 53.5 | 236.9657 | 2655.2082 | 264.8513 | 53.1851 | 105.0161 | 14.9159 | 427.1018 | 18 | 0.034 | 59 |  | 14 | 0.02 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1977 | 34 | 687.7 | 44 | 328.5 | 3960.6 | 108.3 | 21.5 | 53.9 | 2.6 | 172.9 | 22 | 0.039 | 75 |  | 16 | 0.018 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1977 | 34 | 571.3 | 35 | 199.4 | 2335.1 | 90.3 | 20.3 | 46.5 | 1.5 | 213.3 | 14 | 0.042 | 75 |  | 14 | 0.019 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1977 | 34 | 559.7 | 33 | 228 | 1751.2 | 101.7 | 26.1 | 38.6 | 1.5 | 163.8 | 15 | 0.039 | 54 |  | 15 | 0.02 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable. Corrosive IEC. Corrosive ASTM 4A.
33000 | 1977 | 34 | 426.3 | 20 | 207.3 | 2576.4 | 59.1 | 14.7 | 29.4 | 1.6 | 114.2 | 16 | 0.085 | 56 |  | 15 | 0.018 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1977 | 34 | 344.1 | 20 | 163.4 | 1874.4 | 62.6 | 10.3 | 23.6 | 0.8 | 83.4 | 40 | 0.037 | 24 |  | 19 | 0.015 | DGA is assessed as acceptable. | Breakdown voltage is low. Other oil quality results are assessed as acceptable.
33000 | 1977 | 34 | 541 | 41.81 | 258 | 2306 | 115 | 17 | 35 | 4 | 112 | 20 | 0.037 | 52 |  | 14 | 0.021 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1977 | 34 | 467 | 32 | 112 | 948 | 93 | 22 | 47 | 1 | 192 | 9 | 0.047 | 67 |  | 10 | 0.041 | Test results satisfactory. Acetylene gas possibly from tapchanger. | Oil quality is assessed as acceptable.
33000 | 1977 | 34 | 599 | 40 | 120 | 1005 | 137 | 18 | 49 | 1 | 274 | 15 | 0.055 | 62 |  | 18.6 | 0.017 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1977 | 34 | 1069 | 40 | 201 | 1353 | 287 | 47 | 94 | 3 | 437 | 18 | 0.055 | 55 |  | 20.7 | 0.019 | Test results satisfactory. Acetylene gas possibly from tapchanger.
33000 | 1977 | 34 | 1747 | 40 | 1123 | 9938 | 315 | 65 | 110 | 1 | 133 | 16 | 0.057 | 72 |  | 17.3 | 0.018 | Step increase in carbon oxide gas levels and 2-furfural. Other test results are assessed as acceptable.
33000 | 1977 | 34 | 837 | 46 | 389 | 3075 | 123 | 33 | 76 | 3 | 213 | 19 | 0.049 | 31 |  | 14.6 | 0.018 | Carbon oxide gas levels have reduced. Test results are assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1977 | 34 | 1018 | 42 | 390 | 2449 | 274 | 49 | 67 | 2 | 236 | 15 | 0.051 | 75 |  | 15.9 | 0.016 | Gas levels have remained fairly stable. Test results are assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1977 | 34 | 541.7 | 38 | 309.3 | 3476.3 | 67.3 | 13.3 | 40.2 | 1.8 | 109.8 | 22 | 0.054 | 66 |  | 12 | 0.023 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1977 | 34 | 630.6 | 45 | 428.1 | 4763.7 | 56.3 | 12.2 | 34.6 | 1.3 | 98.1 | 29 | 0.05 | 30 |  | 12 | 0.021 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1977 | 34 | 745.9 | 60 | 530.1 | 4948.7 | 64.2 | 22.2 | 37.8 | 1.6 | 90 | 27 | 0.053 | 30 |  | 15 | 0.019 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable. Corrosive IEC. Corrosive ASTM 4A.
33000 | 1977 | 34 | 498.1 | 60 | 369.7 | 4247.6 | 32.9 | 8.2 | 30.5 | 1.6 | 55.2 | 27 | 0.041 | 29 |  | 14 | 0.018 | DGA is assessed as acceptable. | Breakdown voltage is low. Other oil quality results are assessed as acceptable.
33000 | 1977 | 34 | 578.6 | 55 | 389.7 | 3844.6 | 61.1 | 12 | 33.3 | 1.1 | 81.4 | 31 | 0.064 | 33 |  | 9 | 0.03 | DGA is assessed as acceptable. | Breakdown voltage is low. Other oil quality results are assessed as acceptable.
33000 | 1976 | 35 | 374 | 41.81 | 132 | 1205 | 77 | 14 | 19 | 2 | 130 | 12 | 0.047 | 43 |  | 20 | 0.014 | Test results satisfactory C2H2 from tapchanger?
33000 | 1976 | 35 | 475 | 41.81 | 259 | 1948 | 33 | 9 | 23 | 2 | 149 | 14 | 0.046 | 64 |  | 6 | 0.042 | Gas levels fairly stable. Test results satisfactory.
33000 | 1976 | 35 | 287 | 41.81 | 173 | 1223 | 0 | 6 | 16 | 3 | 89 | 33 | 0.076 | 51 |  | 9.4 | 0.032 | Moisture level of sample high.Suspect sample contamination.RESAMPLE FOR CONFIRMATION?
33000 | 1976 | 35 | 284 | 41.81 | 199 | 1471 | 38 | 4 | 8 | 2 | 33 | 15 | 0.077 | 70 |  | 12.1 | 0.025 | Test results satisfactory.
33000 | 1976 | 35 | 206 | 41.81 | 160 | 1231 | 15 | 4 | 6 | 4 | 17 | 17 | 0.076 | 67 |  | 9.6 | 0.025 | Test results satisfactory.
33000 | 1976 | 35 | 203 | 41.81 | 163 | 1393 | 19 | 3 | 4 | 1 | 13 | 20 | 0.059 | 55 |  | 12.7 | 0.021 | Test results are assessed as acceptable.
33000 | 1976 | 35 | 191 | 41.81 | 154 | 1302 | 16 | 3 | 4 | 2 | 12 | 41 | 0.061 | 20 |  | 12.4 | 0.019 | Moisture content of oil high. Dielectric strength low; possibly sample contamination. Other test results are assessed as acceptable.
33000 | 1976 | 35 | 18.3 | 28 | 16 | 655 | 0 | 0.6 | 1.4 | 0.1 | 0.2 | 14 | 0.023 | 65 |  | 18 | 0.019 | The test results are assessed as acceptable. EX SOUTHPORT.
33000 | 1976 | 35 | 6 | 40 | 6 | 134.7 | 0 | 0 | 0 | 0 | 0 | 6 | 0.01 | 75 |  | 145 | 0.007 | The test results are assessed as acceptable. EX SOUTHPORT.
33000 | 1976 | 35 | 332 | 41.81 | 82 | 1020 | 64 | 13 | 22 | 1 | 150 | 16 | 0.027 | 36 |  | 150 | 0.0044 | Test results satisfactory C2H2 from tapchanger?
33000 | 1976 | 35 | 333 | 41.81 | 151 | 1335 | 35 | 10 | 19 | 1 | 117 | 17 | 0.026 | 60 |  | 48.1 | 0.01016 | Test results satisfactory.
33000 | 1976 | 35 | 189 | 41.81 | 97 | 958 | 0 | 7 | 13 | 1 | 71 | 40 | 0.031 | 22 |  | 46.2 | 0.009 | Moisture level of sample high.Suspect sample contamination.RESAMPLE FOR CONFIRMATION?
33000 | 1976 | 35 | 154 | 41.81 | 88 | 1019 | 30 | 2 | 6 | 1 | 27 | 26 | 0.041 | 47 |  | 42.8 | 0.01 | Test results satisfactory.
33000 | 1976 | 35 | 107 | 41.81 | 79 | 1031 | 9 | 2 | 3 | 0 | 14 | 18 | 0.029 | 36 |  | 53.9 | 0.006 | Test results are assessed as acceptable.
33000 | 1976 | 35 | 104 | 41.81 | 74 | 1148 | 12 | 2 | 3 | 1 | 12 | 30 | 0.02 | 55 |  | 50.6 | 0.007 | Test results are assessed as acceptable.
33000 | 1976 | 35 | 4.7 | 25 | 3.5 | 209.6 | 0 | 0.5 | 0.6 | 0.1 | 0 | 17 | 0.01 | 37 |  | 46 | 0.016 | The test results are assessed as acceptable.
33000 | 1976 | 35 | 5.5 | 25 | 5.3 | 116.7 | 0 | 0.2 | 0 | 0 | 0 | 5 | 0.01 | 75 |  | 59 | 0.01 | The test results are assessed as acceptable.
33000 | 1976 | 35 | 4.8 | 23 | 4.2 | 196.1 | 0 | 0.6 | 0 | 0 | 0 | 8 | 0.01 | 75 |  | 39 | 0.012 | The test results are assessed as acceptable.
33000 | 1976 | 35 | 4.4 | 23 | 3.6 | 214.6 | 0 | 0.4 | 0.3 | 0.1 | 0 | 19 | 0.01 | 46 |  | 55 | 0.015 | The test results are assessed as acceptable.
33000 | 1976 | 35 | 262 | 29 | 63 | 690 | 64 | 10 | 20 | 1 | 104 | 14 | 0.032 | 55 |  | 55 | 0.012 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1976 | 35 | 525 | 40 | 88 | 962 | 58 | 16 | 39 | 2 | 322 | 15 | 0.021 | 59 |  | 56.4 | 0.008 | Acetylene level high. Possible from tapchanger? | Oil quality is assessed as acceptable.
33000 | 1976 | 35 | 778 | 35 | 76 | 1072 | 119 | 23 | 63 | 2 | 495 | 12 | 0.021 | 69 |  | 40.1 | 0.011 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1976 | 35 | 758 | 44 | 93 | 1206 | 53 | 22 | 69 | 3 | 518 | 12 | 0.022 | 75 |  | 31 | 0.015 | Dissolved gas analysis is assessed as acceptable. Acetylene gas possibly communicating from tapchanger. | Oil quality is assessed as acceptable.
33000 | 1976 | 35 | 613.2 | 48 | 103.8 | 1193.3 | 104.7 | 21.6 | 52.5 | 7.8 | 322.8 | 14 | 0.014 | 53 |  | 30.6 | 0.014 | Dissolved gas analysis is assessed as acceptable. Acetylene gas possibly communicating from tapchanger. | Oil quality is assessed as acceptable.
33000 | 1976 | 35 | 428.2 | 45 | 94 | 1446.4 | 69.9 | 15.1 | 42.5 | 1.4 | 205.3 | 14 | 0.016 | 57 |  | 20 | 0.017 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1976 | 35 | 395.7 | 40 | 105.7 | 1395.4 | 75.2 | 12.8 | 29.2 | 1.3 | 171.5 | 14 | 0.021 | 57 |  | 25 | 0.015 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1976 | 35 | 297.5 | 51 | 133.5 | 1770.4 | 42 | 8 | 17.5 | 0.8 | 95.7 | 22 | 0.018 | 40 |  | 28 | 0.011 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1976 | 35 | 439.3 | 60 | 254.5 | 2600.1 | 55.9 | 10.1 | 18 | 0 | 100.8 | 24 | 0.031 | 68 |  | 31 | 0.009 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1976 | 35 | 459 | 37 | 210 | 2118 | 102 | 12 | 23 | 12 | 100 | 14 | 0.021 | 41 |  | 50 | 0.0077 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1976 | 35 | 614 | 37 | 341 | 3180 | 90 | 11 | 31 | 5 | 136 | 15 | 0.034 | 61 |  | 8 | 0.037 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1976 | 35 | 524 | 45 | 319 | 3254 | 43 | 8 | 34 | 1 | 119 | 22 | 0.057 | 42 |  | 14 | 0.021 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1976 | 35 | 800 | 62 | 218 | 2098 | 98 | 25 | 56 | 2 | 401 | 27 | 0.056 | 75 |  | 7.7 | 0.029 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1976 | 35 | 610 | 38 | 383 | 3180 | 31 | 11 | 42 | 4 | 139 | 15 | 0.078 | 72 |  | 7 | 0.037 | 2-furfural level is high and trending upwards. Other test results are assessed as acceptable. RECOMMEND RESAMPLE IN 1 YEAR TO MONITOR TREND.
33000 | 1976 | 35 | 716.9 | 52 | 513.5 | 4169.4 | 46.2 | 11.6 | 30.5 | 5.3 | 109.8 | 28 | 0.068 | 48 |  | 5 | 0.045 | 2-furfural level is high and trending upwards suggesting advanced state of insulation degradation. Other test results are assessed as acceptable. RECOMMEND RESAMPLE IN 1 YEAR TO MONITOR CONDITION.
33000 | 1976 | 35 | 1053.9 | 51 | 800.4 | 6625 | 80.5 | 13.3 | 35.5 | 6.6 | 117.6 | 33 | 0.082 | 39 |  | 5.7805 | 0.04719 | 2-furfural and carbon oxide levels are high and trending upwards suggesting advanced state of insulation degradation. Moisture content of sample is high. RECOMMEND RESAMPLE IN 1 YEAR TO MONITOR CONDITION.
33000 | 1976 | 35 | 586.7 | 52 | 460.7 | 4270.8 | 43.9 | 8 | 14.4 | 3.7 | 56 | 36 | 0.072 | 32 |  | 6 | 0.039 | DGA is assessed as acceptable. | Moisture content is high. Other oil quality results are assessed as acceptable.
33000 | 1976 | 35 | 384.6 | 49 | 251.4 | 2989.6 | 34.7 | 7.3 | 14.6 | 1.9 | 74.7 | 22 | 0.091 | 71 |  | 4 | 0.053 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1976 | 35 | 420.8 | 38 | 235 | 2525 | 52.4 | 9.5 | 16.3 | 1.5 | 106.1 | 22 | 0.084 | 51 |  | 5 | 0.046 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1976 | 35 | 330.8 | 38 | 181.6 | 2091.4 | 43.5 | 6.8 | 11.8 | 0.9 | 86.2 | 27 | 0.084 | 30 |  | 5 | 0.047 | DGA is assessed as acceptable. | Breakdown voltage is low. Other oil quality results are assessed as acceptable.
33000 | 1976 | 35 | 114 | 30 | 72 | 1085 | 0 | 3 | 13 | 1 | 25 | 10 | 0.022 | 69 |  | 13 | 0.0249 | Test results satisfactory.
33000 | 1976 | 35 | 355 | 44 | 126 | 1445 | 47 | 9 | 27 | 1 | 145 | 14 | 0.035 | 72 |  | 22.6 | 0.013 | Increased acetylene(C2H2) level.From tap changer?
33000 | 1976 | 35 | 634 | 40 | 128 | 1444 | 115 | 20 | 48 | 1 | 322 | 18 | 0.042 | 69 |  | 17.4 | 0.016 | Test results satisfactory. Acetylene gas possibly from tapchanger.
33000 | 1976 | 35 | 15 | 41.81 | 7 | 225 | 0 | 1 | 2 | 2 | 3 | 15 | 0.01 | 55 |  | 136 | 0.005 | Test results satisfactory.
33000 | 1976 | 35 | 549 | 41.81 | 109 | 1286 | 120 | 24 | 39 | 1 | 256 | 18 | 0.01 | 45 |  | 129.2 | 0.004 | Test results are assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1976 | 35 | 463.6 | 41.81 | 143.7 | 2580.2 | 66.1 | 17.2 | 46.8 | 1.5 | 188.3 | 17 | 0.01 | 37 |  | 46 | 0.009 | DGA is assessed as acceptable. Acetylene gas possibly communicating from tapchanger. | Other test results are assessed as acceptable.
33000 | 1976 | 35 | 458.9 | 56 | 238.5 | 2917.6 | 76.7 | 11 | 31.3 | 4.9 | 96.5 | 37 | 0.01 | 24 |  | 77 | 0.007 | DGA is assessed as acceptable. | Moisture content of sample is high. Breakdown voltage of sample is low. Other test results are assessed as acceptable.
33000 | 1976 | 35 | 372.2 | 45 | 100.6 | 1593.9 | 55.4 | 12.8 | 30.9 | 4.2 | 168.3 | 18 | 0.01 | 55 |  | 64 | 0.008 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1976 | 35 | 382.3 | 24.7 | 108 | 1612 | 68 | 13 | 34 | 0.3 | 159 | 13 | 0.022 | 52 |  | 54 | 0.006 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable. PCB contaminated oil.
33000 | 1976 | 35 | 200.1 | 40 | 61.4 | 1171.9 | 26.9 | 6.4 | 19.5 | 0.7 | 85.2 | 12 | 0.005 | 56 |  | 34 | 0.011 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable. Corrosive IEC. Corrosive ASTM 4B.
33000 | 1976 | 35 | 100.9 | 42 | 44.4 | 1026.8 | 10.6 | 2.7 | 10.6 | 0 | 32.6 | 14 | 0.007 | 50 |  | 37 | 0.008 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1976 | 35 | 122 | 41 | 58 | 1237.4 | 10.6 | 3.4 | 12.4 | 0 | 37.6 | 15 | 0.007 | 42 |  | 26 | 0.011 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1976 | 35 | 108 | 35 | 67 | 1006 | 0 | 4 | 11 | 1 | 25 | 11 | 0.024 | 55 |  | 13 | 0.026 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1976 | 35 | 331 | 43 | 113 | 1277 | 60 | 9 | 21 | 3 | 125 | 15 | 0.051 | 69 |  | 17.7 | 0.017 | Increased acetylene (C2H2) level.From tap changer?
33000 | 1976 | 35 | 476 | 41.81 | 107 | 935 | 99 | 16 | 31 | 1 | 222 | 26 | 0.032 | 73 |  | 18.8 | 0.015 | Test results satisfactory. Acetylene gas possibly from tapchanger.
33000 | 1976 | 35 | 388 | 30 | 69 | 1038 | 61 | 14 | 34 | 2 | 208 | 14 | 0.043 | 49 |  | 17.9 | 0.016 | Test results are assessed as acceptable. Acetylene gas possibly from tapchanger. | Oil quality is assessed as acceptable.
33000 | 1976 | 35 | 583.8 | 41.81 | 234.2 | 2901.8 | 66.5 | 16.1 | 45.6 | 1.4 | 220 | 16 | 0.05 | 74 |  | 9 | 0.025 | The test results are assessed as acceptable. Acetylene gas possibly from tapchanger. | Oil quality is assessed as acceptable.
33000 | 1976 | 35 | 604.2 | 59 | 335.6 | 3435.2 | 81.5 | 11.7 | 33.8 | 7 | 134.6 | 31 | 0.054 | 33 |  | 10 | 0.025 | DGA is assessed as acceptable. | Moisture content of sample is slightly high. Other test results are assessed as acceptable.
33000 | 1976 | 35 | 381.9 | 44 | 163.9 | 1980.4 | 17.9 | 9.8 | 27.4 | 5.1 | 157.8 | 20.5 | 0.055 | 75 |  | 10.1 | 0.028 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1976 | 35 | 509.7 | 46 | 199.7 | 2662 | 65.3 | 14.2 | 35.2 | 3.1 | 192.2 | 22 | 0.087 | 65 |  | 7 | 0.036 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1976 | 35 | 245.3 | 40 | 119.6 | 1577.7 | 27.9 | 6.7 | 14.4 | 1.1 | 75.6 | 15 | 0.062 | 75 |  | 6 | 0.041 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable. Corrosive IEC. Corrosive ASTM 4B.
33000 | 1976 | 35 | 239.3 | 46 | 118.3 | 1582.5 | 22.5 | 7.9 | 12.7 | 1.1 | 76.8 | 18 | 0.067 | 75 |  | 8 | 0.035 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable. Corrosive IEC. Corrosive ASTM 4B.
33000 | 1976 | 35 | 247.5 | 64 | 91 | 1228.2 | 44.8 | 6.4 | 13.6 | 0 | 91.7 | 21 | 0.056 | 75 |  | 5 | 0.045 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1976 | 35 | 168.3 | 52 | 89.2 | 1415.2 | 18.1 | 4.4 | 7.1 | 0.4 | 49.1 | 20 | 0.059 | 55 |  | 6 | 0.036 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1976 | 35 | 117.5 | 42 | 60 | 1243.3 | 7.6 | 2.4 | 6.2 | 0 | 41.3 | 17 | 0.061 | 93 |  | 7 | 0.036 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1976 | 35 | 137.3 | 43 | 87.6 | 1678.1 | 9.1 | 2.4 | 5.6 | 0 | 32.6 | 19 | 0.058 | 60 |  | 5 | 0.053 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1976 | 35 | 485 | 24 | 76 | 871 | 93 | 16 | 45 | 2 | 253 | 10 | 0.029 | 68 |  | 20 | 0.019 | DGA is assessed as acceptable. Acetylene gas possibly communicating from tapchanger. | Oil quality is assessed as acceptable.
33000 | 1976 | 35 | 1499 | 36 | 177 | 1433 | 252 | 62 | 116 | 4 | 888 | 17 | 0.036 | 65 |  | 28.2 | 0.012 | Increased ethylene suggests possible hot spot. Acetylene level high probably from tapchanger. | Oil quality is assessed as acceptable.
33000 | 1976 | 35 | 1632 | 50 | 250 | 1739 | 250 | 64 | 128 | 4 | 936 | 23 | 0.029 | 54 |  | 11.9 | 0.03 | Gas levels increasing slightly. Acetylene gas possibly from tapchanger. | Oil quality is assessed as acceptable.
33000 | 1976 | 35 | 1289 | 44 | 221 | 1835 | 238 | 43 | 93 | 3 | 691 | 15 | 0.027 | 53 |  | 30.6 | 0.011 | Gas levels have remained fairly stable. | Oil quality is assessed as acceptable.
33000 | 1976 | 35 | 557 | 50 | 247 | 2421 | 68 | 12 | 45 | 2 | 183 | 19 | 0.032 | 75 |  | 21.2 | 0.014 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1976 | 35 | 767 | 46 | 312 | 2870 | 100 | 24 | 67 | 6 | 258 | 12 | 0.037 | 53 |  | 18 | 0.017 | DGA is assessed as acceptable at present. | Oil quality is assessed as acceptable.
33000 | 1976 | 35 | 842 | 43 | 409.4 | 4026 | 130.2 | 23.5 | 54.9 | 9.3 | 214.7 | 21 | 0.037 | 74 |  | 20.429 | 0.01848 | 2-furfural and carbon oxide levels are trending upwards. Other test results are assessed as acceptable. RECOMMEND RESAMPLE IN 2 YEARS TO MONITOR CONDITION.
33000 | 1976 | 35 | 579.2 | 38 | 180.6 | 2733.1 | 103.8 | 17.9 | 48.6 | 10.6 | 217.7 | 17 | 0.032 | 64 |  | 21 | 0.014 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1976 | 35 | 666.2 | 52 | 266.6 | 2905.6 | 98.5 | 17.4 | 45.8 | 4 | 233.9 | 26 | 0.029 | 41 |  | 19 | 0.015 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1976 | 35 | 599.8 | 53 | 292.2 | 2878.7 | 74.1 | 14.6 | 38 | 1.3 | 179.6 | 25 | 0.038 | 38 |  | 14 | 0.02 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1976 | 35 | 669.5 | 58 | 322.5 | 3210.2 | 78.6 | 17 | 40.2 | 2.7 | 208.5 | 25 | 0.034 | 25 |  | 13 | 0.022 | DGA is assessed as acceptable. | Breakdown voltage is low. Other oil quality results are assessed as acceptable.
33000 | 1976 | 35 | 485.1 | 43 | 159.1 | 1772 | 101.6 | 13.7 | 34.8 | 0.4 | 175.5 | 23 | 0.037 | 43 |  | 12 | 0.025 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1976 | 35 | 293.3 | 46 | 156.7 | 1718 | 33.6 | 8.5 | 20.7 | 0.6 | 73.2 | 19 | 0.032 | 39 |  | 15 | 0.016 | Dissolved gas levels have increased when compared to 9:30am sample. | Oil quality is assessed as acceptable.
33000 | 1976 | 35 | 229.3 | 48 | 151.1 | 1801.1 | 19.6 | 3.8 | 15.1 | 0.3 | 39.4 | 25 | 0.033 | 45 |  | 16 | 0.016 | Dissolved gas levels are reduced. | Oil quality is assessed as acceptable.
33000 | 1976 | 35 | 791 | 41.81 | 130 | 1000 | 125 | 40 | 66 | 4 | 426 | 31 | 0.043 | 40 |  | 22.8 | 0.013 | Test results satisfactory. Acetylene gas possibly from tapchanger. | Oil quality is assessed as acceptable.
33000 | 1976 | 35 | 561 | 55 | 141 | 1305 | 80 | 18 | 30 | 1 | 291 | 17 | 0.03 | 66 |  | 25.4 | 0.012 | Test results are assessed as acceptable. Acetylene gas possibly from tapchanger. | Oil quality is assessed as acceptable.
33000 | 1976 | 35 | 737.5 | 60 | 203.1 | 2722.8 | 93.1 | 25.3 | 54 | 11.5 | 350.5 | 13 | 0.037 | 75 |  | 15 | 0.015 | The test results are assessed as acceptable. Acetylene gas possibly from tapchanger. | Oil quality is assessed as acceptable.
33000 | 1976 | 35 | 857.1 | 60 | 461 | 4286.7 | 115.3 | 21 | 37.4 | 11.4 | 211 | 25 | 0.043 | 42 |  | 16 | 0.016 | The test results are assessed as acceptable. Acetylene gas possibly communicating from tapchanger. | Oil quality is assessed as acceptable.
33000 | 1976 | 35 | 363.1 | 32 | 117.8 | 1923.2 | 48.2 | 13.1 | 24.5 | 4.7 | 154.8 | 19 | 0.032 | 42 |  | 15 | 0.018 | DGA is assessed as acceptable. Acetylene gas possibly communicating from tapchanger. | Oil quality is assessed as acceptable.
33000 | 1976 | 35 | 109.8 | 31 | 69.6 | 1110.4 | 8.9 | 1.6 | 3.3 | 0.2 | 26.2 | 14 | 0.035 | 75 |  | 15 | 0.017 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1976 | 35 | 94 | 36 | 55.9 | 974.6 | 14.6 | 2.6 | 2.8 | 0.4 | 17.7 | 15 | 0.037 | 64 |  | 16 | 0.018 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1976 | 35 | 69.7 | 48 | 46.5 | 1064.2 | 7.7 | 2.3 | 2.2 | 0.7 | 10.3 | 16 | 0.034 | 52 |  | 10 | 0.023 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1976 | 35 | 137.2 | 38 | 72.1 | 1404.5 | 18.6 | 4.6 | 5.4 | 0.3 | 36.2 | 23 | 0.03 | 39 |  | 19 | 0.012 | DGA is assessed as acceptable. | Breakdown voltage is low. Other oil quality results are assessed as acceptable.
33000 | 1976 | 35 | 771 | 30 | 355 | 3883 | 128 | 21 | 54 | 2 | 211 | 22 | 0.047 | 46 |  | 21.5 | 0.014 | Acetylene level high. Probably from tapchanger?
33000 | 1976 | 35 | 769 | 55 | 387 | 4162 | 84 | 19 | 54 | 2 | 223 | 25 | 0.046 | 44 |  | 16.6 | 0.018 | Dissolved gas analysis is assessed as acceptable. Oil quality is assessed as acceptable.
33000 | 1976 | 35 | 1140 | 50 | 565 | 5359 | 85 | 29 | 80 | 3 | 378 | 23 | 0.058 | 46 |  | 14.3 | 0.025 | Dissolved gas analysis is assessed as acceptable. Oil quality is assessed as acceptable. Acetylene gas possibly from tapchanger.
33000 | 1976 | 35 | 885 | 25 | 451 | 4075 | 102 | 18 | 47 | 2 | 265 | 29 | 0.046 | 65 |  | 14.8 | 0.03 | Dissolved gas analysis is assessed as acceptable. Acetylene gas possibly from tapchanger. | Oil quality is assessed as acceptable.
33000 | 1976 | 35 | 1159 | 55 | 429 | 3688 | 105 | 36 | 70 | 3 | 516 | 26 | 0.05 | 38 |  | 14.4 | 0.017 | 2-Furfural level is above 1PPM. Other test results are assessed as acceptable. Acetylene gas possibly from tapchanger.
33000 | 1976 | 35 | 1075.1 | 70 | 225 | 2734 | 140.8 | 41.6 | 95.5 | 3.3 | 568.9 | 25 | 0.059 | 29 |  | 6 | 0.045 | 2-furfural level in oil is relatively stable. RECOMMEND RESAMPLE IN 2 YEARS TO MONITOR TREND.
33000 | 1976 | 35 | 1079.9 | 55 | 283.8 | 2749.7 | 133.6 | 43.7 | 81 | 7.8 | 530 | 26 | 0.049 | 31 |  | 11 | 0.025 | Dissolved gas analysis is assessed as acceptable. Acetylene gas possibly communicating from tapchanger. | Oil quality is assessed as acceptable.
33000 | 1976 | 35 | 641.9 | 45 | 279.4 | 2747.3 | 84.4 | 16.5 | 43.3 | 2 | 216.3 | 21 | 0.056 | 32 |  | 9 | 0.035 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1976 | 35 | 624 | 43 | 248.5 | 2905.7 | 88.7 | 17.8 | 45.7 | 1 | 222.3 | 30 | 0.054 | 27 |  | 8 | 0.032 | DGA is assessed as acceptable. | Breakdown voltage is slightly low. Other oil quality results are assessed as acceptable.
33000 | 1976 | 35 | 486.7 | 38 | 244 | 2789.7 | 34.1 | 10.8 | 34.9 | 1.8 | 161.1 | 21 | 0.061 | 47 |  | 10 | 0.025 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1976 | 35 | 612.5 | 52 | 234.5 | 2521.2 | 94.6 | 20.1 | 34.7 | 1.6 | 227 | 28 | 0.054 | 34 |  | 9 | 0.027 | DGA is assessed as acceptable. | Breakdown voltage is low. Other oil quality results are assessed as acceptable.
33000 | 1976 | 35 | 416 | 52 | 119.1 | 1605.9 | 78.5 | 15.5 | 27.6 | 1.3 | 174 | 24 | 0.046 | 50 |  | 10 | 0.025 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1976 | 35 | 319.3 | 41.81 | 163.7 | 1976.3 | 16.4 | 13.1 | 11.5 | 2.8 | 111.8 | 18 | 0.046 | 81 |  | 9 | 0.029 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1976 | 35 | 349.1 | 41.81 | 130.2 | 1995.7 | 57.6 | 9.4 | 19.5 | 1.2 | 131.2 | 21 | 0.045 | 52 |  | 9 | 0.029 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1976 | 35 | 309.5 | 48 | 101.8 | 1715 | 37.6 | 9.2 | 21.2 | 1 | 138.7 | 19 | 0.048 | 62 |  | 11 | 0.021 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1976 | 35 | 348.8 | 50 | 82 | 1514.1 | 55.4 | 11.8 | 25.1 | 0 | 174.5 | 22 | 0.047 | 49 |  | 8 | 0.031 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1976 | 35 | 426 | 25 | 61 | 657 | 81 | 16 | 71 | 6 | 191 | 25 | 0.023 | 25 |  | 12 | 0.031 | Dissolved gas analysis is assessed as acceptable. Acetylene gas possibly communicating from tapchanger. | Oil quality is assessed as acceptable.
33000 | 1976 | 35 | 774 | 32 | 179 | 1858 | 133 | 29 | 56 | 2 | 375 | 25 | 0.031 | 37 |  | 32.3 | 0.011 | Dissolved gas analysis is assessed as acceptable. Acetylene gas possibly communicating from tapchanger. | Oil quality is assessed as acceptable.
33000 | 1976 | 35 | 899 | 40 | 227 | 2088 | 158 | 25 | 57 | 2 | 430 | 21 | 0.027 | 29 |  | 26.7 | 0.011 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1976 | 35 | 584 | 42 | 304 | 3110 | 63 | 15 | 46 | 4 | 152 | 20 | 0.039 | 66 |  | 20 | 0.017 | DGA is assessed as acceptable at present. | Oil quality is assessed as acceptable.
33000 | 1976 | 35 | 632 | 38 | 383.2 | 3946.7 | 78.4 | 13 | 36 | 6 | 115.4 | 19 | 0.039 | 62 |  | 15 | 0.016 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1976 | 35 | 390.3 | 36 | 181.9 | 2419.7 | 63.1 | 10 | 28.3 | 5.7 | 101.3 | 19 | 0.035 | 48 |  | 19 | 0.015 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1976 | 35 | 441.3 | 50 | 243.3 | 2540.8 | 57.3 | 9.6 | 26.2 | 2 | 102.9 | 32 | 0.031 | 37 |  | 18 | 0.015 | Dissolved gas analysis is assessed as acceptable. | Moisture content is slightly high. Other oil quality results are assessed as acceptable.
33000 | 1976 | 35 | 678.4 | 54 | 437.1 | 4471.3 | 66.1 | 11.5 | 32.6 | 0.8 | 130.3 | 21 | 0.042 | 36 |  | 17.2 | 0.02 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1976 | 35 | 471.4 | 54 | 265 | 2849.7 | 54.7 | 10 | 27.9 | 0 | 113.8 | 26 | 0.039 | 29 |  | 16 | 0.019 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1976 | 35 | 583 | 57 | 348.5 | 4343.7 | 58.8 | 11 | 30 | 1.2 | 133.5 | 26 | 0.035 | 26 |  | 13 | 0.023 | DGA is assessed as acceptable. | Breakdown voltage is assessed as acceptable. Other oil quality results are assessed as acceptable.
33000 | 1976 | 35 | 313 | 45 | 143.7 | 1782.8 | 49.1 | 7.5 | 22.8 | 2 | 87.9 | 23 | 0.036 | 14 |  | 15 | 0.018 | DGA is assessed as acceptable. | Breakdown voltage is low. Other oil quality results are assessed as acceptable.
33000 | 1976 | 35 | 293 | 35 | 96 | 1313 | 54 | 11 | 24 | 7 | 101 | 13 | 0.017 | 64 |  | 90 | 0.0049 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1976 | 35 | 367 | 33 | 148 | 1643 | 51 | 9 | 22 | 2 | 135 | 11 | 0.022 | 63 |  | 15 | 0.028 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1976 | 35 | 442 | 40 | 206 | 2063 | 52 | 9 | 26 | 1 | 148 | 16 | 0.028 | 37 |  | 40.1 | 0.009 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1976 | 35 | 677 | 60 | 130 | 1427 | 122 | 28 | 46 | 1 | 350 | 19 | 0.03 | 68 |  | 28.1 | 0.011 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1976 | 35 | 500 | 46 | 307 | 2660 | 31 | 11 | 36 | 4 | 111 | 14 | 0.035 | 72 |  | 22 | 0.013 | 2-furfural level is trending upwards. Other test results are assessed as acceptable. RECOMMEND RESAMPLE IN 2 YEARS TO MONITOR TREND.
33000 | 1976 | 35 | 542.9 | 59 | 371.9 | 3384.2 | 41.5 | 10.8 | 26.7 | 4.3 | 87.7 | 22 | 0.024 | 43 |  | 15 | 0.02 | 2-furfural level is high suggesting advanced state of insulation degradation. Other test results are assessed as acceptable. Acetylene gas possibly from tapchanger. RECOMMEND RESAMPLE IN 1 YEAR TO MONITOR CONDITION.
33000 | 1976 | 35 | 828.2 | 55 | 609.4 | 5678.7 | 72.1 | 11 | 35.8 | 5.2 | 94.7 | 36 | 0.037 | 65 |  | 18.1831 | 0.020548 | 2-furfural level is high and trending upwards suggesting advanced state of insulation degradation. Other test results are assessed as acceptable. RECOMMEND RESAMPLE IN 1 YEAR TO MONITOR TREND.
33000 | 1976 | 35 | 429 | 58 | 309.6 | 3587.9 | 42 | 7.2 | 16.9 | 2.5 | 50.8 | 32 | 0.033 | 30 |  | 22 | 0.012 | DGA is assessed as acceptable. | Moisture content is slightly high. Other oil quality results are assessed as acceptable.
33000 | 1976 | 35 | 274.5 | 52 | 146.5 | 2418.8 | 28.2 | 7 | 20.3 | 0 | 72.5 | 33 | 0.038 | 18 |  | 20 | 0.016 | DGA is assessed as acceptable. | Moisture content is high. Breakdown voltage is low. Possible sample contamination. Other oil quality results are assessed as acceptable.
33000 | 1976 | 35 | 327.6 | 46 | 139.8 | 2450.2 | 44.5 | 9.5 | 24.6 | 1 | 108.2 | 29 | 0.033 | 36 |  | 19 | 0.014 | DGA is assessed as acceptable. | Breakdown voltage is improved but slightly low. Other oil quality results are assessed as acceptable.
33000 | 1976 | 35 | 281 | 42 | 121.3 | 1534.5 | 37.3 | 6.5 | 17.7 | 0.6 | 97.6 | 24 | 0.036 | 36 |  | 16 | 0.015 | DGA is assessed as acceptable. | Breakdown voltage is low. Other oil quality results are assessed as acceptable.
33000 | 1976 | 35 | 233.5 | 60 | 110.7 | 2425.3 | 30.7 | 5.3 | 16.9 | 0.7 | 69.2 | 29 | 0.033 | 21 |  | 18 | 0.016 | DGA is assessed as acceptable. | Breakdown voltage is low. Other oil quality results are assessed as acceptable. Corrosive IEC. Corrosive ASTM 4A.
33000 | 1976 | 35 | 218.7 | 47 | 104.8 | 1548.2 | 25 | 6 | 14.1 | 0.8 | 68 | 23 | 0.028 | 50 |  | 21 | 0.014 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable. Corrosive IEC. Corrosive ASTM 4A.
33000 | 1976 | 35 | 243.2 | 40 | 137.2 | 1833.8 | 27.4 | 8 | 12.2 | 0.5 | 57.9 | 23 | 0.028 | 47 |  | 18 | 0.013 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable. Corrosive IEC. Corrosive ASTM 4A
33000 | 1976 | 35 | 41.3 | 13 | 32.6 | 992.8 | 5 | 1.6 | 1.8 | 0.3 | 0 | 29 | 0.049 | 49 |  | 15 | 0.016 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1976 | 35 | 27 | 41.81 | 23 | 1001 | 3 | 1 | 0 | 0 | 0 | 29 | 0.016 | 36 |  | 49 | 0.01 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1976 | 35 | 0 | 20 | 0 | 411 | 0 | 0 | 0 | 0 | 0 | 23 | 0.021 | 33 |  | 47.6 | 0.008 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1976 | 35 | 54.2 | 20 | 40.7 | 1000 | 6.4 | 2.4 | 2.5 | 2.2 | 0 | 26 | 0.084 | 72 |  | 10 | 0.022 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1976 | 35 | 8.4 | 15 | 7.7 | 642.4 | 0 | 0.7 | 0 | 0 | 0 | 21 | 0.013 | 49 |  | 135 | 0.002 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1976 | 35 | 1 | 41.81 | 0 | 458 | 0 | 1 | 0 | 0 | 0 | 20 | 0.017 | 68 |  | 36.7 | 0.012 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1976 | 35 | 25.1 | 23 | 19.4 | 870.7 | 2.8 | 1.3 | 0.4 | 1.2 | 0 | 20 | 0.074 | 40 |  | 12 | 0.02 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1976 | 35 | 27.6 | 19 | 19.7 | 871 | 2.6 | 1.7 | 0.4 | 3.2 | 0 | 19 | 0.067 | 58 |  | 14 | 0.017 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1976 | 35 | 37.1 | 20 | 23.9 | 827.1 | 4.8 | 2.9 | 2.1 | 3.4 | 0 | 18 | 0.042 | 71 |  | 26 | 0.01 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1976 | 35 | 55 | 41.81 | 47 | 831 | 4 | 2 | 1 | 1 | 0 | 16 | 0.098 | 51 |  | 13 | 0.017 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1976 | 35 | 632 | 62 | 411 | 4379 | 79 | 13 | 30 | 3 | 96 | 29 | 0.279 | 60 |  | 1.9 | 0.16 | Acidity; resistivity and loss tangent of oil quite poor. Acetylene level notable.
33000 | 1976 | 35 | 416 | 26 | 297 | 3095 | 32 | 7 | 18 | 2 | 60 | 16 | 0.288 | 72 |  | 2 | 0.165 | DGA satisfactory. | Oil quality is assessed as acceptable.
33000 | 1976 | 35 | 278 | 29 | 238 | 2417 | 0 | 3 | 11 | 2 | 24 | 20 | 0.297 | 53 |  | 2.2 | 0.116 | Test results satisfactory. | Oil quality is assessed as acceptable.
33000 | 1976 | 35 | 325 | 35 | 263 | 2970 | 0 | 6 | 25 | 2 | 29 | 70 | 0.298 | 9 |  | 2.8 | 0.089 | DGA is assessed as acceptable. | High moisture content and very low dielectric strength of oil sample.
33000 | 1976 | 35 | 139 | 43 | 101 | 1297 | 4 | 0 | 27 | 0 | 7 | 23 | 0.047 | 57 |  | 11 | 0.027 | Test results satisfactory. Has transformer oil been processed/changed? | Oil quality is assessed as acceptable.
33000 | 1976 | 35 | 174 | 41.81 | 114 | 1277 | 19 | 4 | 30 | 0 | 7 | 36 | 0.05 | 33 |  | 13.1 | 0.022 |  | Moisture content of oil is high; other test results are assessed as acceptable.
33000 | 1976 | 35 | 175.9 | 44 | 122 | 1698.4 | 0 | 1.6 | 46.1 | 1.2 | 5 | 10 | 0.054 | 67 |  | 8 | 0.05 | The test results are assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1976 | 35 | 145.3 | 31 | 117.5 | 1640.1 | 0 | 1.4 | 24.7 | 0.2 | 1.5 | 15 | 0.058 | 75 |  | 8 | 0.037 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1976 | 35 | 118.6 | 28 | 99.4 | 1551.4 | 0 | 1 | 17.3 | 0.7 | 0.2 | 20 | 0.063 | 36 |  | 8 | 0.034 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1976 | 35 | 108 | 16 | 89.5 | 1121.7 | 0 | 1.2 | 16.8 | 0.2 | 0.3 | 18 | 0.065 | 66 |  | 8 | 0.035 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable. Corrosive IEC. Corrosive ASTM 4A.
33000 | 1976 | 35 | 979 | 22 | 141 | 1182 | 396 | 38 | 61 | 3 | 340 | 7 | 0.024 | 71 |  | 10 | 0.043 | D.G.A. suggests arcing/sparking. Tap changer involvement? | Oil quality is assessed as acceptable.
33000 | 1976 | 35 | 1078 | 36 | 156 | 1190 | 243 | 53 | 83 | 3 | 540 | 16 | 0.039 | 43 |  | 8.4 | 0.033 | DGA similar to previous. | Oil quality good.
33000 | 1976 | 35 | 2299 | 30 | 180 | 1205 | 450 | 134 | 198 | 7 | 1330 | 9 | 0.046 | 51 |  | 10.8 | 0.037 | Acetylene gas level extremely high. From tapchanger? | Oil quality is assessed as acceptable.
33000 | 1976 | 35 | 894 | 35 | 140 | 1081 | 305 | 36 | 55 | 2 | 356 | 14 | 0.046 | 65 |  | 16.1 | 0.017 | Test results are assessed as acceptable. Acetylene gas possibly from tap changer. | Oil quality is assessed as acceptable.
33000 | 1976 | 35 | 866 | 41.81 | 136 | 1102 | 277 | 36 | 56 | 2 | 359 | 19 | 0.042 | 57 |  | 13.1 | 0.022 | Test results are assessed as acceptable. Acetylene gas possibly from tapchanger. | Oil quality is assessed as acceptable.
33000 | 1976 | 35 | 1091.6534 | 38 | 235.6823 | 2594.8483 | 240.6001 | 40.7103 | 102.9025 | 14.2609 | 457.4973 | 7 | 0.039 | 72 |  | 11 | 0.025 | The test results are assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1976 | 35 | 720 | 36 | 297.8 | 2471.6 | 137.3 | 25 | 49.4 | 5.5 | 205 | 15 | 0.035 | 71 |  | 10 | 0.029 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1976 | 35 | 802 | 39 | 327.7 | 2896.2 | 144.3 | 24.7 | 51.2 | 2 | 252.1 | 13 | 0.041 | 72 |  | 11 | 0.024 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1976 | 35 | 851.8 | 46 | 398.7 | 3657.6 | 140.9 | 25.1 | 48.8 | 3.5 | 234.8 | 18 | 0.055 | 92 |  | 12 | 0.023 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1976 | 35 | 553.1 | 60 | 324.8 | 3369.4 | 75.4 | 13.4 | 25.8 | 2.7 | 111 | 33 | 0.057 | 33 |  | 9 | 0.029 | DGA is assessed as acceptable. | Breakdown voltage is low. Other oil quality results are assessed as acceptable.
33000 | 1976 | 35 | 383.3 | 45 | 167.8 | 2038.5 | 68.1 | 14 | 22.9 | 1.6 | 108.9 | 18 | 0.05 | 38 |  | 11 | 0.021 | DGA is assessed as acceptable. | Breakdown voltage is low. Other oil quality results are assessed as acceptable.
33000 | 1976 | 35 | 670 | 31 | 319 | 1875 | 195 | 26 | 53 | 11 | 66 | 8 | 0.068 | 54 |  | 100 | 0.05 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1976 | 35 | 695 | 45 | 228 | 1606 | 198 | 40 | 81 | 5 | 143 | 13 | 0.059 | 56 |  | 3.9 | 0.108 | High hydrocarbon levels. Is tap changer oil mixing? | Oil quality is assessed as acceptable.
33000 | 1976 | 35 | 1319 | 60 | 269 | 1656 | 490 | 57 | 102 | 3 | 398 | 28 | 0.065 | 62 |  | 4 | 0.11 | Acetylene gas level very high. Possibly from tapchanger? | Oil quality is assessed as acceptable.
33000 | 1976 | 35 | 475 | 41.81 | 84 | 2100 | 113 | 24 | 68 | 2 | 184 | 19 | 0.066 | 30 |  | 5.3 | 0.07 | Test results are assessed as acceptable. Acetylene gas possibly from tapchanger. | Oil quality is assessed as acceptable.
33000 | 1976 | 35 | 1378.7 | 45 | 647.8 | 3726.3 | 290.1 | 53.1 | 108.1 | 20.7 | 258.9 | 20 | 0.082 | 45 |  | 3 | 0.099 | The test results are relatively stable and are assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1976 | 35 | 1106.5 | 46 | 637.7 | 4131.3 | 199.3 | 54.6 | 57.4 | 24.5 | 133 | 25 | 0.077 | 50 |  | 6 | 0.045 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1976 | 35 | 1155 | 48 | 658 | 4487 | 254 | 50 | 51 | 19 | 123 | 40 | 0.114 | 55 |  | 6 | 0.041 | DGA is assessed as acceptable. | Moisture content is high. Other oil quality results are assessed as acceptable.
33000 | 1976 | 35 | 947 | 49 | 352 | 3676 | 245 | 40 | 63 | 15 | 232 | 28 | 0.119 | 34 |  | 5 | 0.045 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1976 | 35 | 1387.4 | 70 | 748 | 6483.3 | 253.8 | 59.5 | 69.7 | 19 | 237.4 | 47 | 0.128 | 17 |  | 6 | 0.039 | DGA is assessed as acceptable. | Breakdown voltage is low. Other oil quality results are assessed as acceptable.
33000 | 1976 | 35 | 1026.9 | 58 | 457.7 | 5545.4 | 159.6 | 45.8 | 69.2 | 16.6 | 278 | 27 | 0.125 | 75 |  | 6 | 0.042 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable. Corrosive IEC. Corrosive ASTM 4A.
33000 | 1976 | 35 | 866.6 | 61 | 558.3 | 5855.5 | 130.1 | 20.4 | 37.6 | 9.6 | 110.6 | 44 | 0.157 | 35 |  | 6 | 0.033 | DGA is assessed as acceptable. | Breakdown voltage is low. Other oil quality results are assessed as acceptable.
33000 | 1976 | 35 | 785.2 | 48 | 522.6 | 5464.2 | 136.1 | 18.3 | 16.6 | 5.7 | 85.9 | 27 | 0.141 | 54 |  | 5 | 0.047 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1976 | 35 | 749.9 | 49 | 474.7 | 4900.4 | 91.9 | 25.1 | 36.2 | 14 | 108 | 39 | 0.146 | 25 |  | 4 | 0.057 | DGA is assessed as acceptable. | Breakdown voltage is low. Other oil quality results are assessed as acceptable.
33000 | 1976 | 35 | 495.1 | 43 | 270.2 | 3834 | 64.6 | 12 | 25.9 | 3.5 | 118.9 | 27 | 0.148 | 76 |  | 6 | 0.04 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1975 | 36 | 127 | 40 | 118 | 1340 | 6 | 1 | 1 | 1 | 0 | 13 | 0.048 | 74 |  | 12.4 | 0.019 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1975 | 36 | 360.2 | 55 | 315.7 | 3757 | 34.1 | 3.2 | 4.7 | 2.5 | 0 | 32 | 0.063 | 34 |  | 8 | 0.031 | DGA is assessed as acceptable. | Moisture content of sample is slightly high. Other test results are assessed as acceptable.
33000 | 1975 | 36 | 200.7 | 23 | 182.4 | 2436.9 | 13.1 | 1.9 | 1.9 | 1.4 | 0 | 20 | 0.062 | 75 |  | 7 | 0.029 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1975 | 36 | 205.1 | 20.8 | 185.1 | 2403.7 | 14.6 | 1.8 | 2.1 | 1.5 | 0 | 16 | 0.071 | 75 |  | 8 | 0.031 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1975 | 36 | 81 | 37 | 79 | 1609 | 0 | 1 | 1 | 0 | 0 | 14 | 0.084 | 75 |  | 7 | 0.032 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1975 | 36 | 99.7 | 33 | 89.3 | 1502.3 | 8 | 1.2 | 0.9 | 0.3 | 0 | 18 | 0.08 | 75 |  | 8 | 0.031 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable. Corrosive IEC. Non-corrosive ASTM 2C.
33000 | 1975 | 36 | 67.9 | 21 | 60.7 | 1177.9 | 5 | 1 | 0.8 | 0.4 | 0 | 12 | 0.084 | 58 |  | 7 | 0.031 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable. Corrosive IEC. Non-corrosive ASTM 3B.
33000 | 1975 | 36 | 75.1 | 20 | 72.4 | 1308.5 | 0 | 1.1 | 1.4 | 0.2 | 0 | 15 | 0.089 | 60 |  | 7 | 0.032 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1975 | 36 | 195 | 25 | 185 | 1188 | 0 | 2 | 6 | 2 | 0 | 19 | 0.04 | 52 |  | 3.5 | 0.135 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1975 | 36 | 343 | 41.81 | 314 | 3323 | 20 | 3 | 4 | 2 | 0 | 21 | 0.071 | 75 |  | 7.8 | 0.033 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1975 | 36 | 219.1 | 52 | 189.1 | 2938.4 | 22.5 | 1.9 | 4.1 | 1.5 | 0 | 28 | 0.097 | 44 |  | 7 | 0.036 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1975 | 36 | 153 | 23 | 138.6 | 2490.2 | 9.7 | 1.5 | 2.2 | 1 | 0 | 25 | 0.085 | 61 |  | 6 | 0.036 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1975 | 36 | 186.3 | 19.3 | 169.5 | 2775.2 | 11 | 1.7 | 2.7 | 1.4 | 0 | 15 | 0.091 | 75 |  | 6 | 0.034 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1975 | 36 | 104.8 | 40 | 102 | 2370 | 0 | 1 | 1.8 | 0 | 0 | 13 | 0.133 | 75 |  | 5 | 0.045 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1975 | 36 | 126.6 | 36 | 112.1 | 2137.5 | 8 | 1.8 | 2 | 1.1 | 1.6 | 14 | 0.104 | 66 |  | 7 | 0.037 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable. Corrosive IEC. Non-corrosive ASTM 3B.
33000 | 1975 | 36 | 71.1 | 22 | 65.1 | 1815.3 | 2.6 | 1.2 | 1.4 | 0.8 | 0 | 9 | 0.11 | 76 |  | 6 | 0.037 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable. Corrosive IEC. Non-corrosive ASTM 3B.
33000 | 1975 | 36 | 70.5 | 20 | 66.9 | 1726.7 | 0 | 1.1 | 2 | 0.5 | 0 | 16 | 0.127 | 83 |  | 5 | 0.042 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1975 | 36 | 264 | 35 | 218 | 1489 | 16 | 2 | 25 | 0 | 3 | 7 | 0.016 | 67 |  | 20 | 0.0395 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1975 | 36 | 230 | 49 | 195 | 1336 | 0 | 2 | 27 | 1 | 5 | 17 | 0.028 | 50 |  | 17 | 0.019 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1975 | 36 | 371 | 36 | 300 | 1856 | 44 | 2 | 25 | 0 | 0 | 20 | 0.036 | 57 |  | 13.7 | 0.043 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1975 | 36 | 337 | 41.81 | 285 | 1973 | 21 | 2 | 29 | 0 | 0 | 22 | 0.041 | 74 |  | 17.3 | 0.015 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1975 | 36 | 391.9 | 45 | 340.3 | 2976 | 12 | 2.2 | 35.9 | 1 | 0.5 | 16 | 0.05 | 58 |  | 12 | 0.02 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1975 | 36 | 456.7 | 42 | 412.1 | 3934 | 9.1 | 3.5 | 29.9 | 2.1 | 0 | 24 | 0.057 | 62 |  | 14 | 0.019 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1975 | 36 | 647 | 55 | 597.8 | 5705.2 | 16.5 | 3.9 | 28.8 | 0 | 0 | 25 | 0.05 | 50 |  | 6 | 0.039 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1975 | 36 | 438.8 | 50 | 399.5 | 3139.6 | 13 | 2.3 | 23.4 | 0.6 | 0 | 22 | 0.066 | 52 |  | 12 | 0.022 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1975 | 36 | 35 | 24 | 31 | 445 | 0 | 0 | 4 | 0 | 0 | 19 | 0.032 | 61.8 |  | 40 | 0.017 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1975 | 36 | 223 | 41.81 | 181 | 1089 | 13 | 2 | 25 | 2 | 0 | 9 | 0.078 | 53 |  | 20 | 0.0497 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1975 | 36 | 216 | 44 | 192 | 1235 | 0 | 2 | 21 | 1 | 0 | 54 | 0.032 | 21 |  | 21.2 | 0.016 | Moisture content of sample high.Oil failed electric breakdown test. Possibly contaminated sample.
33000 | 1975 | 36 | 359 | 38 | 299 | 1818 | 29 | 2 | 28 | 1 | 0 | 19 | 0.033 | 60 |  | 16.9 | 0.025 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1975 | 36 | 313 | 41.81 | 266 | 1794 | 21 | 2 | 24 | 0 | 0 | 20 | 0.042 | 53 |  | 17.2 | 0.02 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1975 | 36 | 378.2 | 40 | 329.7 | 2863 | 9.4 | 2 | 35.6 | 0.9 | 0.6 | 17 | 0.046 | 63 |  | 10 | 0.025 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1975 | 36 | 526.8 | 36 | 477.1 | 4590.1 | 12.2 | 3.8 | 31.9 | 1.6 | 0.2 | 23 | 0.052 | 49 |  | 11 | 0.024 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1975 | 36 | 387.2 | 43 | 351.5 | 3337.3 | 8.4 | 2.3 | 25 | 0 | 0 | 21 | 0.06 | 46 |  | 9 | 0.027 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1975 | 36 | 3495.5 | 35 | 93.1 | 880.3 | 1333.2 | 98 | 152.4 | 7.9 | 1810.9 | 22 | 0.01 | 56 |  | 167 | 0.004 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1975 | 36 | 402.5 | 48 | 365.8 | 3116.9 | 11.1 | 2.1 | 23 | 0.5 | 0 | 23 | 0.058 | 63 |  | 11 | 0.026 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1975 | 36 | 391 | 43 | 352.4 | 3240 | 9.1 | 3 | 25.1 | 0.6 | 0.8 | 23 | 0.062 | 37 |  | 8 | 0.029 | DGA is assessed as acceptable. | Breakdown voltage is low. Other oil quality results are assessed as acceptable.
33000 | 1975 | 36 | 304 | 42 | 145 | 2451 | 13 | 7 | 30 | 2 | 107 | 13 | 0.068 | 58 |  | 8 | 0.052 | C2H2 Quite high. Tap changer? Other test results satisfactory.
33000 | 1975 | 36 | 657 | 50 | 319 | 2736 | 63 | 14 | 46 | 2 | 213 | 43 | 0.075 | 34 |  | 9.1 | 0.029 | Acetylene gas level quite high. Possibly from tapchanger? Moisture content of sample is high.
33000 | 1975 | 36 | 485 | 35 | 97 | 1961 | 27 | 13 | 58 | 2 | 288 | 16 | 0.067 | 64 |  | 11.1 | 0.03 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1975 | 36 | 710 | 41.81 | 260 | 3529 | 26 | 12 | 64 | 2 | 346 | 25 | 0.067 | 46 |  | 8.1 | 0.029 | Test results are assessed as acceptable. Acetylene gas possibly from tapchanger. | Oil quality is assessed as acceptable.
33000 | 1975 | 36 | 425.6 | 48 | 230.4 | 4335.6 | 33.5 | 7.5 | 29.8 | 4.6 | 119.8 | 16 | 0.091 | 41 |  | 5 | 0.043 | 2-furfural level is trending upwards. Other test results are assessed as acceptable. RECOMMEND RESAMPLE IN 1 YEAR TO MONITOR CONDITION.
33000 | 1975 | 36 | 414.7 | 44 | 214 | 4403.3 | 29.2 | 7.8 | 27.3 | 6.2 | 130.2 | 21 | 0.097 | 60 |  | 5 | 0.046 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1975 | 36 | 301 | 45 | 197.1 | 3474.2 | 16.5 | 8 | 9.6 | 0.3 | 69.5 | 14 | 0.096 | 70 |  | 4.3 | 0.06 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1975 | 36 | 264.8 | 30 | 200.7 | 2972 | 14.1 | 8.8 | 8.5 | 3.4 | 29.3 | 14 | 0.112 | 75 |  | 2 | 0.102 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1975 | 36 | 233.3 | 38 | 194.7 | 3253.8 | 7.6 | 3.6 | 5.2 | 1.2 | 21 | 18 | 0.114 | 75 |  | 4 | 0.061 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable. Corrosive IEC. Corrosive ASTM 4A.
33000 | 1975 | 36 | 195.7 | 40 | 158.2 | 3340.7 | 13.5 | 3.9 | 6.1 | 1.4 | 12.6 | 24 | 0.144 | 69 |  | 4 | 0.05 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1975 | 36 | 205.6 | 38 | 152.3 | 2942.4 | 10.9 | 3.7 | 6.9 | 1.1 | 30.7 | 25 | 0.114 | 72 |  | 5 | 0.047 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1975 | 36 | 730 | 50 | 348 | 2116 | 189 | 26 | 57 | 2 | 108 | 17 | 0.075 | 67 |  | 5 | 0.0958 | Test results satisfactory at present. | Oil quality is assessed as acceptable.
33000 | 1975 | 36 | 763 | 46 | 397 | 2520 | 120 | 26 | 74 | 2 | 144 | 13 | 0.089 | 71 |  | 4 | 0.109 | Test results satisfactory. | Oil quality is assessed as acceptable.
33000 | 1975 | 36 | 1048 | 46 | 400 | 2331 | 186 | 39 | 92 | 3 | 328 | 22 | 0.107 | 55 |  | 6.1 | 0.05 | Test results satisfactory. Acetylene gas possibly from tapchanger. | Oil quality is assessed as acceptable.
33000 | 1975 | 36 | 881 | 42 | 432 | 2828 | 111 | 26 | 67 | 2 | 243 | 15 | 0.088 | 72 |  | 6.5 | 0.038 | Test results are assessed as acceptable. Acetylene gas possibly from tapchanger. | Oil quality is assessed as acceptable.
33000 | 1975 | 36 | 794.3 | 44 | 478.4 | 4160.5 | 100.8 | 17.9 | 72.1 | 6.6 | 118.5 | 22 | 0.092 | 64 |  | 4 | 0.07 | Acetylene gas possibly from tapchanger. | Other test results are assessed as acceptable.
33000 | 1975 | 36 | 912.4 | 44 | 692.9 | 4361.1 | 67.7 | 16.4 | 38 | 4 | 93.4 | 26 | 0.096 | 75 |  | 5 | 0.052 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1975 | 36 | 990.9 | 58 | 638.6 | 4283.2 | 147.7 | 23.3 | 38.7 | 0 | 142.6 | 36 | 0.113 | 31 |  | 3 | 0.095 | DGA is assessed as acceptable. | Moisture content is high. Other oil quality results are assessed as acceptable.
33000 | 1975 | 36 | 855.2 | 54 | 589.4 | 4392.5 | 92.2 | 17.3 | 33.1 | 1.5 | 121.7 | 28 | 0.125 | 32 |  | 5 | 0.045 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1975 | 36 | 848.4 | 48 | 515.5 | 4567.5 | 126.5 | 22.6 | 37.6 | 2.2 | 144 | 32 | 0.154 | 37 |  | 4 | 0.0595 | DGA is assessed as acceptable. | Moisture content is slightly high. Other oil quality results are assessed as acceptable at present.
33000 | 1975 | 36 | 520.9 | 42 | 314.3 | 3350.2 | 74.6 | 11.4 | 22.1 | 1.8 | 96.7 | 28 | 0.101 | 27 |  | 4 | 0.064 | DGA is assessed as acceptable. | Breakdown voltage is low.
33000 | 1975 | 36 | 343.3 | 54 | 196.5 | 2126.2 | 46 | 8.4 | 16.6 | 1.6 | 74.2 | 26 | 0.098 | 36 |  | 6 | 0.041 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable. Corrosive IEC. Corrosive ASTM 4A.
33000 | 1975 | 36 | 452.6 | 47 | 277.9 | 3568.8 | 74.8 | 9.3 | 16.2 | 2 | 72.4 | 32 | 0.118 | 38 |  | 6 | 0.041 | DGA is assessed as acceptable. | Breakdown voltage is low. Other oil quality results are assessed as acceptable. Corrosive IEC. Corrosive ASTM 4B.
33000 | 1975 | 36 | 304.2 | 55 | 163.9 | 2249.2 | 42.7 | 8.1 | 15 | 2.3 | 72.2 | 26 | 0.097 | 74 |  | 7 | 0.034 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1974 | 37 | 84 | 25 | 81 | 923 | 0 | 1 | 1 | 0 | 1 | 9 | 0.096 | 74 |  | 50 | 0.016 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1974 | 37 | 195 | 45 | 178 | 2240 | 9 | 4 | 2 | 2 | 0 | 15 | 0.032 | 52 |  | 35.9 | 0.01 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1974 | 37 | 168 | 46 | 162 | 2007 | 0 | 3 | 2 | 1 | 0 | 8 | 0.026 | 69 |  | 17.1 | 0.023 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1974 | 37 | 315.6 | 48 | 289.3 | 1103.3 | 14.7 | 3.6 | 4.5 | 3.3 | 0.2 | 9 | 0.032 | 65 |  | 13 | 0.022 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1974 | 37 | 484.6 | 51 | 450.1 | 4200.7 | 25 | 3.7 | 4 | 1.6 | 0.2 | 37 | 0.039 | 25 |  | 8 | 0.027 | Carbon oxide levels are trending upwards. | Moisture content of sample is high. Breakdown voltage of sample is low. Other test results are assessed as acceptable.
33000 | 1974 | 37 | 378.6 | 44 | 353 | 4236.9 | 15.2 | 6.6 | 3.3 | 0.5 | 0 | 14 | 0.045 | 64 |  | 8.3 | 0.035 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1974 | 37 | 307.1 | 44 | 281.8 | 3855.9 | 14.5 | 3.6 | 4.9 | 0.8 | 1.5 | 54 | 0.052 | 31 |  | 7 | 0.032 | DGA is assessed as acceptable. | Moisture content is high. Other oil quality results are assessed as acceptable.
33000 | 1974 | 37 | 227.7 | 49 | 211.2 | 3794.5 | 8.3 | 3.1 | 4.1 | 1 | 0 | 43 | 0.052 | 18 |  | 8 | 0.028 | DGA is assessed as acceptable. | Moisture content is high. Breakdown voltage is low. Other oil quality results are assessed as acceptable.
33000 | 1974 | 37 | 235.3 | 44 | 217.7 | 2918.2 | 12.6 | 2.4 | 2.2 | 0.4 | 0 | 26 | 0.063 | 28 |  | 8 | 0.036 | DGA is assessed as acceptable. | Breakdown voltage is low. Other oil quality results are assessed as acceptable. Corrosive IEC. Non-corrosive ASTM 3A.
33000 | 1974 | 37 | 192.4 | 48 | 184.7 | 2319.8 | 2.7 | 2.2 | 1.6 | 1.2 | 0 | 22 | 0.06 | 45 |  | 7 | 0.034 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable. Corrosive IEC. Non-corrosive ASTM 3B.
33000 | 1974 | 37 | 179.2 | 40 | 168.5 | 2103.7 | 6.9 | 1.8 | 1.3 | 0.7 | 0 | 14 | 0.066 | 92 |  | 7 | 0.034 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable. Corrosive IEC. Non-corrosive ASTM 3B.
33000 | 1974 | 37 | 136 | 40 | 132.1 | 1839.9 | 0 | 1.4 | 1.9 | 0.6 | 0 | 19 | 0.079 | 71 |  | 7 | 0.033 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1974 | 37 | 61 | 41.81 | 49 | 688 | 0 | 4 | 2 | 5 | 1 | 10 | 0.024 | 74 |  | 30 | 0.0254 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1974 | 37 | 116 | 41.81 | 106 | 1025 | 8 | 2 | 0 | 0 | 0 | 8 | 0.029 | 46 |  | 40.6 | 0.011 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1974 | 37 | 219 | 41.81 | 207 | 1539 | 8 | 3 | 1 | 0 | 0 | 8 | 0.023 | 55 |  | 37.4 | 0.01 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1974 | 37 | 232 | 41.81 | 211 | 1616 | 15 | 3 | 2 | 1 | 0 | 12 | 0.029 | 57 |  | 11.1 | 0.045 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1974 | 37 | 351 | 41.81 | 320 | 2251 | 25 | 3 | 2 | 1 | 0 | 7 | 0.025 | 75 |  | 14.1 | 0.025 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1974 | 37 | 364.8 | 41.81 | 341 | 3482.9 | 11.7 | 3.9 | 5.2 | 1.6 | 1.4 | 7 | 0.043 | 75 |  | 5 | 0.046 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1974 | 37 | 809 | 55 | 757.3 | 5502 | 33.5 | 7.7 | 7.4 | 3.1 | 0 | 14 | 0.058 | 42 |  | 4 | 0.061 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1974 | 37 | 793.4 | 55 | 739.5 | 5417.8 | 30.5 | 10.3 | 8 | 5.1 | 0 | 19 | 0.057 | 50 |  | 4 | 0.056 | The test results are consistent with the main tank sample and are assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1974 | 37 | 308.9 | 29 | 290.2 | 2721.1 | 11.9 | 2.7 | 2.6 | 1.5 | 0 | 10 | 0.058 | 75 |  | 4.8 | 0.058 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1974 | 37 | 310.5 | 41 | 295.8 | 2834.5 | 9.4 | 2.7 | 1.7 | 0.9 | 0 | 12 | 0.075 | 75 |  | 4 | 0.062 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1974 | 37 | 267 | 64 | 255.1 | 2768.7 | 6.4 | 2.5 | 1.7 | 1.3 | 0 | 14 | 0.074 | 75 |  | 4 | 0.062 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable. Corrosive IEC. Non-corrosive ASTM 3B.
33000 | 1974 | 37 | 239.7 | 45 | 226.5 | 2589.1 | 7 | 2.9 | 1.7 | 1.6 | 0 | 11 | 0.083 | 83 |  | 4 | 0.051 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1974 | 37 | 120.2 | 41 | 113.2 | 1614.3 | 3 | 1.5 | 1.8 | 0.7 | 0 | 10 | 0.067 | 90 |  | 6 | 0.038 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1974 | 37 | 132 | 25 | 107 | 989 | 12 | 2 | 4 | 1 | 6 | 8 | 0.033 | 53 |  | 30 | 0.017 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1974 | 37 | 259 | 46 | 240 | 2184 | 7 | 4 | 4 | 3 | 1 | 19 | 0.046 | 70 |  | 10.9 | 0.025 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1974 | 37 | 227 | 44 | 209 | 1815 | 13 | 2 | 2 | 1 | 0 | 13 | 0.057 | 75 |  | 6.5 | 0.035 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1974 | 37 | 368.5 | 46 | 344.6 | 2510.9 | 14.2 | 3.4 | 4.5 | 1.8 | 0 | 9 | 0.073 | 72 |  | 4 | 0.054 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1974 | 37 | 561.8 | 50 | 525.4 | 4541.7 | 25.1 | 4.6 | 4.7 | 1.8 | 0.2 | 12 | 0.084 | 75 |  | 4 | 0.069 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1974 | 37 | 383.6 | 42 | 363.7 | 4404.9 | 10.6 | 6.6 | 2.3 | 0.4 | 0 | 12 | 0.095 | 50 |  | 3.1 | 0.085 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1974 | 37 | 259.7 | 32 | 231 | 2716.3 | 24 | 2.4 | 1.7 | 0.6 | 0 | 10 | 0.103 | 75 |  | 4 | 0.064 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1974 | 37 | 209 | 41 | 197.3 | 2200.9 | 7.5 | 2.2 | 1.4 | 0.6 | 0 | 10 | 0.112 | 75 |  | 4 | 0.074 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable. Corrosive IEC. Non-corrosive ASTM 3B.
33000 | 1974 | 37 | 147.4 | 46 | 142.9 | 1968.8 | 0.2 | 2.1 | 1.4 | 0.8 | 0 | 10 | 0.11 | 75 |  | 3 | 0.066 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable. Corrosive IEC. Corrosive ASTM 4B.
33000 | 1974 | 37 | 159.1 | 38 | 150.4 | 2037.8 | 4.8 | 1.8 | 1.4 | 0.7 | 0 | 10 | 0.113 | 82 |  | 4 | 0.057 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable. Corrosive IEC. Non-corrosive ASTM 3B.
33000 | 1974 | 37 | 118.6 | 38 | 114.8 | 1799.5 | 0 | 1.4 | 1.8 | 0.6 | 0 | 25 | 0.132 | 99 |  | 4 | 0.063 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1974 | 37 | 178 | 41.81 | 165 | 1121 | 7 | 2 | 2 | 0 | 2 | 17 | 0.024 | 48 |  | 2.5 | 0.025 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1974 | 37 | 215 | 40 | 211 | 1786 | 0 | 2 | 1 | 1 | 0 | 14 | 0.032 | 58 |  | 16.4 | 0.016 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1974 | 37 | 276 | 40 | 255 | 1844 | 16 | 2 | 2 | 1 | 0 | 11 | 0.041 | 73 |  | 8.3 | 0.033 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1974 | 37 | 330.5 | 40 | 305.3 | 1520.4 | 17.6 | 3.1 | 2.8 | 1.5 | 0.2 | 8 | 0.046 | 71 |  | 6 | 0.04 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1974 | 37 | 348.1 | 40 | 318.9 | 2453.6 | 23.1 | 2.7 | 2.3 | 1.1 | 0 | 9 | 0.056 | 75 |  | 6 | 0.045 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1974 | 37 | 275.5 | 34 | 234 | 1766 | 37 | 2 | 1 | 1 | 0.5 | 8 | 0.061 | 75 |  | 5 | 0.046 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1974 | 37 | 389.6 | 44 | 364.1 | 3314.4 | 17.8 | 4.4 | 2.2 | 1.1 | 0 | 10 | 0.074 | 75 |  | 5 | 0.056 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable. Corrosive IEC. Non-corrosive ASTM 3B.
33000 | 1974 | 37 | 376.7 | 40 | 356.7 | 4058.4 | 13.2 | 3.4 | 2.1 | 1.3 | 0 | 12 | 0.076 | 73 |  | 4 | 0.062 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable. Corrosive IEC. Non-corrosive ASTM 3B.
33000 | 1974 | 37 | 263.4 | 42 | 245.4 | 3773.9 | 11.8 | 2.4 | 2.7 | 1.1 | 0 | 11 | 0.08 | 77 |  | 4 | 0.058 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable. Corrosive IEC. Non-corrosive ASTM 3B.
33000 | 1974 | 37 | 304.9 | 46 | 278.7 | 3227.4 | 19.5 | 2.4 | 3 | 1.3 | 0 | 14 | 0.093 | 88 |  | 4 | 0.057 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1974 | 37 | 566 | 32 | 320 | 1844 | 127 | 14 | 25 | 1 | 79 | 19 | 0.056 | 56 |  | 20 | 0.017 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1974 | 37 | 423 | 49 | 171 | 1674 | 67 | 13 | 37 | 1 | 134 | 9 | 0.052 | 71 |  | 16 | 0.018 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1974 | 37 | 327 | 63 | 154 | 1622 | 43 | 8 | 31 | 1 | 90 | 13 | 0.049 | 70 |  | 14.3 | 0.021 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1974 | 37 | 714 | 60 | 202 | 1773 | 166 | 27 | 49 | 1 | 269 | 15 | 0.055 | 60 |  | 14.4 | 0.017 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1974 | 37 | 928.6 | 58 | 514.3 | 3273.6 | 162.7 | 21.9 | 57.2 | 0.8 | 171.7 | 20 | 0.059 | 35 |  | 10 | 0.029 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1974 | 37 | 714.4 | 30 | 432 | 3302.7 | 113 | 15.9 | 34 | 3.6 | 115.9 | 14 | 0.061 | 73 |  | 8 | 0.033 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1974 | 37 | 606.8 | 40 | 440.1 | 3430 | 59.7 | 10.3 | 24.9 | 1.2 | 70.6 | 17 | 0.057 | 63 |  | 9 | 0.035 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1974 | 37 | 418.1 | 50 | 294.5 | 2813.7 | 38.2 | 8 | 17.4 | 1.5 | 58.5 | 20 | 0.064 | 39 |  | 8 | 0.035 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1974 | 37 | 658.7 | 45 | 413.6 | 3414.3 | 94.1 | 19.7 | 24.8 | 1.2 | 105.3 | 19 | 0.082 | 75 |  | 6 | 0.046 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable. Corrosive IEC. Corrosive ASTM 4A.
33000 | 1974 | 37 | 513.5 | 42 | 342.1 | 3277.7 | 77.2 | 10.2 | 17.5 | 1.3 | 65.2 | 20 | 0.081 | 71 |  | 6 | 0.041 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1974 | 37 | 492.4 | 47 | 293.1 | 3061.7 | 58.6 | 12 | 19.9 | 1.6 | 107.2 | 16 | 0.073 | 74 |  | 6 | 0.048 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1974 | 37 | 627 | 36 | 333 | 1838 | 154 | 16 | 31 | 1 | 92 | 19 | 0.047 | 43 |  | 10 | 0.034 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1974 | 37 | 425 | 46 | 187 | 1382 | 86 | 15 | 31 | 1 | 105 | 14 | 0.039 | 50 |  | 16.6 | 0.018 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1974 | 37 | 554 | 57 | 258 | 1663 | 118 | 19 | 36 | 1 | 122 | 14 | 0.036 | 66 |  | 13.4 | 0.022 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1974 | 37 | 778 | 53 | 163 | 1447 | 223 | 39 | 54 | 2 | 297 | 20 | 0.048 | 47 |  | 15.8 | 0.017 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1974 | 37 | 812.4 | 55 | 434.8 | 2599.6 | 192.7 | 22.2 | 42.1 | 0.7 | 119.9 | 23 | 0.05 | 46 |  | 10 | 0.028 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1974 | 37 | 706.8 | 38 | 381.1 | 2855.8 | 159.5 | 17.1 | 31.2 | 3 | 114.9 | 20 | 0.057 | 63 |  | 10 | 0.026 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1974 | 37 | 489.1 | 39 | 304 | 3012.5 | 59.1 | 12 | 27.8 | 0.9 | 85.3 | 20 | 0.044 | 75 |  | 8 | 0.037 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1974 | 37 | 326.3 | 48 | 209.6 | 2038.1 | 39.4 | 8.1 | 16 | 0.7 | 52.5 | 20 | 0.045 | 62 |  | 12 | 0.025 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1974 | 37 | 375.4 | 44 | 214.4 | 2234 | 91.4 | 8.3 | 12.6 | 0.6 | 48.1 | 21 | 0.051 | 59 |  | 10 | 0.029 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable. Corrosive IEC. Corrosive ASTM 4A.
33000 | 1974 | 37 | 423.4 | 43 | 233.5 | 2431.7 | 94.3 | 10.9 | 16 | 1 | 67.7 | 22 | 0.052 | 64 |  | 10 | 0.023 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1974 | 37 | 415.7 | 48 | 237.3 | 2097.1 | 72.1 | 12 | 15.1 | 0.8 | 78.4 | 17 | 0.044 | 95 |  | 11 | 0.023 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1974 | 37 | 615 | 40 | 441 | 2321 | 76 | 14 | 30 | 6 | 48 | 19 | 0.128 | 38 |  | 3 | 0.11 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1974 | 37 | 716 | 34 | 406 | 2141 | 101 | 20 | 47 | 3 | 139 | 21 | 0.167 | 57 |  | 3.5 | 0.086 | Increased gas levels; tapchanger? | Oil quality is assessed as acceptable.
33000 | 1974 | 37 | 1089 | 40 | 558 | 2746 | 206 | 26 | 63 | 2 | 234 | 28 | 0.157 | 66 |  | 4.3 | 0.061 | Dissolved gas analysis is assessed as acceptable. Acetylene gas possibly from tapchanger. | Moisture content slightly high. Other test results satisfactory.
33000 | 1974 | 37 | 1618 | 60 | 774 | 4879 | 325 | 49 | 89 | 3 | 378 | 31 | 0.156 | 60 |  | 5 | 0.051 | Dissolved gas analysis is assessed as acceptable. Acetylene gas possibly from tapchanger. | Moisture content of oil slightly high. Other test results satisfactory.
33000 | 1974 | 37 | 1598 | 52 | 794 | 4094 | 131 | 51 | 98 | 5 | 519 | 26 | 0.167 | 70 |  | 3.3 | 0.061 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1974 | 37 | 1296.5 | 52 | 821.1 | 5489.7 | 134.3 | 37 | 54.6 | 9.7 | 239.8 | 30 | 0.206 | 64 |  | 3 | 0.078 | Acetylene gas possibly from tapchanger. | Acidity level of sample is high. Moisture content of sample is high. Other test results are assessed as acceptable.
33000 | 1974 | 37 | 1233.9 | 50 | 842.1 | 6101.1 | 133.9 | 28.7 | 46.2 | 9.9 | 173.1 | 35 | 0.168 | 49 |  | 3 | 0.093 | Carbon oxides are trending upwards. | Moisture content of sample is high.
33000 | 1974 | 37 | 768.1 | 50 | 477.8 | 3980.3 | 118 | 18.2 | 28.4 | 7.1 | 118.6 | 29 | 0.198 | 50 |  | 2.7 | 0.087 | Carbon oxide levels are reduced slightly. Dissolved gas analysis is assessed as acceptable. Acetylene gas possibly communicating from tapchanger. | Moisture content of sample is high. Other oil quality results are assesed as acceptable.
33000 | 1974 | 37 | 1091 | 50 | 649.4 | 5452.2 | 154.1 | 32.6 | 41.3 | 6.5 | 207.1 | 32 | 0.207 | 28 |  | 3 | 0.083 | DGA is assessed as acceptable. | Acidity level is high. Other oil quality results are assessed as acceptable.
33000 | 1974 | 37 | 1714.3 | 60 | 883.1 | 6989 | 254.2 | 44.6 | 68.4 | 4 | 460 | 34 | 0.208 | 34 |  | 2.7 | 0.087 | DGA is assessed as acceptable. | Moisture content is slightly high. Acidity level is high. Other oil quality results are assessed as acceptable.
33000 | 1974 | 37 | 2649 | 70 | 638 | 4399 | 372 | 218 | 506 | 52 | 863 | 30 | 0.228 | 34 |  | 2 | 0.092 | DGA suggests arcing has occurred. Note increase in methane, ethane, ethylene and acetylene gas levels. | Moisture content is slightly high. Acidity level is high. Other oil quality results are assessed as acceptable.
33000 | 1974 | 37 | 463 | 41 | 248 | 1615 | 63 | 10 | 36 | 1 | 105 | 12 | 0.075 | 64 |  | 9 | 0.032 | Test results satisfactory at present. C2H2 level should be noted for future reference. | Oil quality is assessed as acceptable.
33000 | 1974 | 37 | 623 | 47 | 267 | 1656 | 131 | 18 | 46 | 2 | 159 | 9 | 0.082 | 62 |  | 8 | 0.034 | Increased gas levels. Internal sparking or tapchanger? | Other results satisfactory.
33000 | 1974 | 37 | 648 | 44 | 324 | 1721 | 86 | 19 | 47 | 1 | 171 | 20 | 0.085 | 59 |  | 6.5 | 0.043 | Test results satisfactory. Acetylene gas possibly from tapchanger. | Oil quality is assessed as acceptable.
33000 | 1974 | 37 | 1076 | 48 | 409 | 2742 | 132 | 38 | 86 | 3 | 408 | 14 | 0.082 | 74 |  | 5.4 | 0.041 | Test results are assessed as acceptable. Acetylene gas possibly from tapchanger. | Oil quality is assessed as acceptable.
33000 | 1974 | 37 | 1044.5 | 45 | 626.4 | 3712.3 | 113.9 | 28.7 | 50.5 | 11.4 | 213.6 | 20 | 0.1 | 75 |  | 3 | 0.076 | The test results are assessed as acceptable. Acetylene gas possibly from tapchanger. | Oil quality is assessed as acceptable.
33000 | 1974 | 37 | 1187.7 | 52 | 831 | 5322 | 118 | 26.3 | 43.6 | 6 | 162.8 | 24 | 0.085 | 43 |  | 4 | 0.062 | Carbon oxide levels are increasing. | Other test results are assessed as acceptable.
33000 | 1974 | 37 | 949.2 | 56 | 589.8 | 4464.9 | 124.5 | 26 | 34.8 | 5.9 | 168.2 | 26 | 0.114 | 75 |  | 4 | 0.062 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1974 | 37 | 1107.2 | 63 | 607.3 | 4625.7 | 196.5 | 31.1 | 52.5 | 2.4 | 217.4 | 32 | 0.108 | 52 |  | 3 | 0.083 | DGA suggests mild oil overheating has occurred. | Oil quality is assessed as acceptable.
33000 | 1974 | 37 | 835 | 46 | 487 | 3892 | 100 | 19 | 28 | 3 | 198 | 24 | 0.14 | 58 |  | 3 | 0.076 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1974 | 37 | 669.7 | 44 | 437.4 | 3637.6 | 62.3 | 15.5 | 28.2 | 3.4 | 122.9 | 27 | 0.128 | 75 |  | 4 | 0.06 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1974 | 37 | 441.8 | 56 | 303 | 3058.6 | 40.3 | 7.7 | 15.9 | 0.4 | 74.5 | 25 | 0.146 | 45 |  | 3 | 0.08 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable. Corrosive IEC. Corrosive ASTM 4A.
33000 | 1974 | 37 | 397.3 | 40 | 263.5 | 2689 | 54.1 | 7.9 | 11.2 | 1.5 | 59.1 | 14 | 0.14 | 80 |  | 3 | 0.07 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable. Corrosive IEC. Corrosive ASTM 4A.
33000 | 1974 | 37 | 1050 | 38 | 547 | 4158 | 88 | 30 | 133 | 24 | 228 | 28 | 0.254 | 41 |  | 2 | 0.177 | D.G.A. Suggests arcing or persitent sparking - possible diffusion from tapchanger.
33000 | 1974 | 37 | 1031 | 37 | 597 | 5120 | 53 | 18 | 132 | 20 | 211 | 28 | 0.253 | 35 |  | 3 | 0.086 | Arc gases possible diffusion from tapchanger. Gas levels stable.
33000 | 1974 | 37 | 802 | 45 | 503 | 4717 | 51 | 12 | 60 | 4 | 172 | 26 | 0.256 | 73 |  | 2.8 | 0.08 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1974 | 37 | 226 | 36 | 98 | 946 | 54 | 7 | 15 | 2 | 50 | 19 | 0.046 | 41 |  | 23.1 | 0.018 | Test results satisfactory after recent oil change on 07/4/94.
33000 | 1974 | 37 | 400 | 32 | 139 | 2377 | 33 | 11 | 62 | 1 | 154 | 16 | 0.035 | 57 |  | 20.7 | 0.02 | Test results satisfactory. Acetylene gas possibly from tapchanger.
33000 | 1974 | 37 | 289 | 35 | 156 | 2675 | 5 | 3 | 68 | 1 | 56 | 15 | 0.048 | 56 |  | 16 | 0.022 | Test results are assessed as acceptable at present. RECOMMEND RESAMPLE IN 1 YEAR TO MONITOR 2-FURFURAL.
33000 | 1974 | 37 | 275.7 | 22 | 144.6 | 2947 | 13.3 | 3.5 | 64.1 | 4.3 | 45.9 | 10 | 0.045 | 71 |  | 15 | 0.019 | 2-furfural level is high suggesting advanced state of insulation degradation. Other test results are assessed as acceptable. Acetylene gas possibly from tapchanger. RECOMMEND RESAMPLE IN 1 YEAR TO MONITOR CONDITION.
33000 | 1974 | 37 | 251.2 | 30 | 170.3 | 2743.9 | 7.3 | 2.7 | 42.9 | 0.9 | 27.1 | 16 | 0.054 | 75 |  | 9 | 0.031 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1974 | 37 | 200.9 | 29 | 151.5 | 2084.2 | 11.4 | 1.8 | 27.5 | 0.4 | 8.3 | 16 | 0.0598 | 67 |  | 10 | 0.029 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1974 | 37 | 297 | 37 | 231.2 | 2586.7 | 12.8 | 3.3 | 32.3 | 0 | 17.4 | 21 | 0.045 | 60 |  | 8 | 0.037 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1974 | 37 | 253.4 | 52 | 204 | 2574.9 | 4.9 | 2.4 | 32.7 | 0.6 | 8.8 | 17 | 0.058 | 43 |  | 11 | 0.029 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1974 | 37 | 246.3 | 40 | 193.7 | 2963.3 | 3.9 | 1.9 | 36.7 | 0.5 | 9.6 | 21 | 0.065 | 37 |  | 9 | 0.029 | DGA is assessed as acceptable. | Breakdown voltage is slightly low. Other oil quality results are assessed as acceptable. Corrosive IEC. Non-corrosive ASTM 3B.
33000 | 1974 | 37 | 152.5 | 25 | 108.6 | 2456.2 | 2.2 | 1.4 | 31.3 | 0.5 | 8.5 | 24 | 0.067 | 48 |  | 11 | 0.025 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1974 | 37 | 141 | 30 | 98.3 | 2344.8 | 2.4 | 1.5 | 30.1 | 0.6 | 8.1 | 15 | 0.064 | 64 |  | 10 | 0.029 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1973 | 38 | 149 | 27 | 79 | 1157 | 0 | 2 | 11 | 1 | 56 | 24 | 0.046 | 75 |  | 3.5 | 0.0685 | Test results satisfactory.
33000 | 1973 | 38 | 254 | 40 | 114 | 1632 | 23 | 2 | 11 | 1 | 103 | 18 | 0.065 | 45 |  | 5 | 0.044 | Test results satisfactory.
33000 | 1973 | 38 | 633 | 48 | 178 | 2134 | 38 | 11 | 33 | 2 | 371 | 23 | 0.065 | 49 |  | 4.5 | 0.046 | Test results satisfactory. | Oil quality is assessed as acceptable.
33000 | 1973 | 38 | 45 | 56 | 4 | 232 | 24 | 1 | 2 | 0 | 14 | 46 | 0.01 | 26 |  | 62.1 | 0.006 | DGA is assessed as acceptable. | Moisture content of oil high; dielectric strength low; after oil change.
33000 | 1973 | 38 | 141 | 42 | 45 | 636 | 8 | 3 | 5 | 0 | 80 | 16 | 0.01 | 65 |  | 28.9 | 0.009 | Test results now satisfactory. | Oil quality is assessed as acceptable.
33000 | 1973 | 38 | 605 | 36 | 67 | 1272 | 48 | 12 | 35 | 1 | 442 | 10 | 0.01 | 63 |  | 18.3 | 0.016 | Test results are assessed as acceptable. Acetylene gas possibly from tapchanger. | Oil quality is assessed as acceptable.
33000 | 1973 | 38 | 978.2 | 41.81 | 97.5 | 1558.8 | 71.9 | 18.6 | 99.1 | 14 | 677.1 | 9 | 0.01 | 68 |  | 10 | 0.027 | The test results are assessed as acceptable. Acetylene gas possibly from tapchanger. | Oil quality is assessed as acceptable.
33000 | 1973 | 38 | 1055.5 | 38 | 103.4 | 1455.5 | 43.4 | 14.6 | 93.5 | 10.2 | 790.4 | 12 | 0.01 | 75 |  | 10 | 0.023 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1973 | 38 | 759.9 | 40 | 103.9 | 1274.6 | 34.5 | 13.5 | 81.9 | 0.9 | 525.2 | 13 | 0.01 | 72 |  | 9 | 0.024 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1973 | 38 | 648.5 | 44 | 103.3 | 1322.2 | 14.3 | 8 | 89.7 | 3.1 | 430.1 | 12 | 0.014 | 68 |  | 9 | 0.023 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable. Corrosive IEC. Corrosive ASTM 4A.
33000 | 1973 | 38 | 398.1 | 24 | 130 | 1555.3 | 0 | 4.7 | 69.9 | 2 | 191.5 | 14 | 0.011 | 45 |  | 8 | 0.031 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1973 | 38 | 284.3 | 42 | 109.6 | 1329.3 | 14.8 | 11.7 | 72.8 | 12.1 | 63.3 | 17 | 0.007 | 66 |  | 9 | 0.025 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1973 | 38 | 198 | 31 | 138 | 1429 | 0 | 3 | 10 | 5 | 42 | 21 | 0.038 | 65 |  | 4 | 0.0502 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1973 | 38 | 259 | 46 | 128 | 2211 | 0 | 2 | 14 | 1 | 114 | 21 | 0.071 | 42 |  | 4.4 | 0.051 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1973 | 38 | 816 | 54 | 348 | 2720 | 55 | 10 | 44 | 2 | 357 | 21 | 0.083 | 56 |  | 4 | 0.056 | Test results satisfactory. Acetylene gas possibly from tapchanger. | Oil quality is assessed as acceptable.
33000 | 1973 | 38 | 994 | 33 | 347 | 3030 | 53 | 11 | 48 | 2 | 533 | 19 | 0.092 | 68 |  | 2.8 | 0.07 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1973 | 38 | 1082.5 | 41.81 | 308.3 | 3422.3 | 64.2 | 15 | 67.8 | 7.5 | 619.7 | 14 | 0.11 | 67 |  | 2 | 0.091 | The test results are assessed as acceptable. Acetylene gas possibly from tapchanger. | Oil quality is assessed as acceptable.
33000 | 1973 | 38 | 1059.5 | 38 | 339.3 | 2886.7 | 57.9 | 14.4 | 52 | 8.4 | 587.5 | 21 | 0.143 | 69 |  | 2 | 0.093 | DGA is assessed as acceptable. Acetylene gas possibly communicating from tapchanger. | Oil quality is assessed as acceptable.
33000 | 1973 | 38 | 897 | 39 | 320.9 | 2516.9 | 55.7 | 15 | 41.6 | 0.2 | 463.6 | 18 | 0.148 | 66 |  | 2 | 0.091 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1973 | 38 | 616.9 | 43 | 272 | 2485.7 | 27.9 | 9.3 | 34.1 | 2 | 271.6 | 18 | 0.139 | 77 |  | 2 | 0.111 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable. Corrosive IEC. Non-corrosive ASTM 3B.
33000 | 1973 | 38 | 402.9 | 47 | 287.9 | 2650.1 | 13.1 | 4.3 | 14.1 | 2.2 | 81.3 | 18 | 0.162 | 44 |  | 2 | 0.104 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1973 | 38 | 223.7 | 31 | 177.9 | 2166.6 | 6 | 2.6 | 7.3 | 1.4 | 28.5 | 17 | 0.175 | 60 |  | 2 | 0.086 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1973 | 38 | 426.4 | 45 | 268.9 | 2670.9 | 24.1 | 13.3 | 39.9 | 10.4 | 69.8 | 26 | 0.151 | 80 |  | 2 | 0.093 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1973 | 38 | 220 | 30 | 123 | 1590 | 9 | 3 | 13 | 3 | 69 | 14 | 0.048 | 68 |  | 7 | 0.0432 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1973 | 38 | 173 | 34 | 88 | 879 | 0 | 5 | 13 | 4 | 63 | 12 | 0.043 | 63 |  | 7.1 | 0.034 | Test results satisfactory. | Oil quality is assessed as acceptable.
33000 | 1973 | 38 | 58 | 41.81 | 48 | 732 | 0 | 1 | 3 | 0 | 6 | 9 | 0.043 | 72 |  | 5.7 | 0.035 | Test results are assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1973 | 38 | 82.4 | 41.81 | 69.2 | 979.2 | 2.8 | 1.8 | 4.8 | 2 | 1.8 | 7 | 0.052 | 75 |  | 5 | 0.05 | The test results are assessed as acceptable. Acetylene gas possibly from tapchanger. | Oil quality is assessed as acceptable.
33000 | 1973 | 38 | 85.9 | 25.5 | 71.1 | 966.9 | 3.4 | 2.1 | 5.1 | 3.5 | 0.7 | 12 | 0.053 | 75 |  | 5 | 0.05 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1973 | 38 | 35.8 | 41.81 | 32.4 | 852.8 | 0 | 0.5 | 2.5 | 0 | 0.4 | 10 | 0.059 | 75 |  | 5 | 0.04 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1973 | 38 | 6.3 | 25 | 5.7 | 74.8 | 0 | 0.6 | 0 | 0 | 0 | 8 | 0.022 | 62 |  | 12 | 0.024 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1973 | 38 | 19.3 | 23 | 10.5 | 349.9 | 8.3 | 0.5 | 0 | 0 | 0 | 19 | 0.011 | 58 |  | 16 | 0.02 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1973 | 38 | 17.3 | 23 | 10.7 | 99.9 | 6.2 | 0.4 | 0 | 0 | 0 | 9 | 0.02 | 75 |  | 10 | 0.029 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1973 | 38 | 135 | 49 | 131 | 1475 | 0 | 2 | 1 | 1 | 0 | 6 | 0.028 | 56 |  | 50 | 0.009 | Test results satisfactory. | Oil quality is assessed as acceptable.
33000 | 1973 | 38 | 154 | 45 | 152 | 1127 | 0 | 1 | 1 | 0 | 0 | 12 | 0.033 | 30 |  | 20.5 | 0.015 | Test results satisfactory. | Oil quality is assessed as acceptable.
33000 | 1973 | 38 | 246 | 47 | 232 | 1218 | 10 | 2 | 1 | 1 | 0 | 10 | 0.063 | 63 |  | 6.4 | 0.018 | Test results satisfactory. | Oil quality is assessed as acceptable.
33000 | 1973 | 38 | 374 | 40 | 363 | 3016 | 5 | 4 | 1 | 1 | 0 | 11 | 0.061 | 50 |  | 10.5 | 0.033 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1973 | 38 | 206 | 42 | 200 | 2120 | 2 | 2 | 1 | 1 | 0 | 7 | 0.068 | 69 |  | 6.6 | 0.041 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1973 | 38 | 160.6 | 35 | 151.2 | 1997.8 | 4.1 | 1.9 | 2 | 1.4 | 0 | 12 | 0.075 | 75 |  | 5 | 0.048 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1973 | 38 | 218.6 | 38 | 205.9 | 2616.6 | 7.9 | 2.4 | 1.4 | 1 | 0 | 9 | 0.086 | 75 |  | 5.2 | 0.05 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1973 | 38 | 243.7 | 38 | 230.2 | 2730.4 | 9.3 | 2.1 | 1 | 1.1 | 0 | 10 | 0.092 | 69 |  | 3 | 0.105 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1973 | 38 | 273.2 | 46 | 260.3 | 2527 | 4.7 | 6.6 | 1 | 0.6 | 0 | 11 | 0.097 | 75 |  | 5 | 0.05 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable. Corrosive IEC. Non-corrosive ASTM 2C.
33000 | 1973 | 38 | 270.1 | 42 | 255.9 | 2563.2 | 6.6 | 3.2 | 3.2 | 1.2 | 0 | 15 | 0.093 | 86 |  | 5 | 0.046 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable. Corrosive IEC. Non-corrosive ASTM 3B.
33000 | 1973 | 38 | 126.1 | 34 | 122.5 | 1891.1 | 0 | 1.4 | 1.6 | 0.6 | 0 | 18 | 0.093 | 52 |  | 6 | 0.04 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1973 | 38 | 123 | 30 | 118 | 1297 | 0 | 2 | 1 | 0 | 2 | 8 | 0.028 | 44.2 |  | 50 | 0.0084 | Test results satisfactory. | Oil quality is assessed as acceptable.
33000 | 1973 | 38 | 134 | 45 | 130 | 1253 | 0 | 2 | 1 | 1 | 0 | 17 | 0.027 | 38 |  | 20.5 | 0.014 | Test results satisfactory. | Oil quality is assessed as acceptable.
33000 | 1973 | 38 | 288 | 50 | 271 | 1709 | 13 | 2 | 1 | 1 | 0 | 16 | 0.073 | 53 |  | 7.8 | 0.016 | Test results satisfactory. | Oil quality is assessed as acceptable.
33000 | 1973 | 38 | 351 | 40 | 340 | 3130 | 4 | 4 | 2 | 1 | 0 | 11 | 0.062 | 46 |  | 11 | 0.035 | Test results satisfactory. | Oil quality is assessed as acceptable.
33000 | 1973 | 38 | 231 | 44 | 223 | 2528 | 3 | 2 | 2 | 1 | 0 | 9 | 0.074 | 75 |  | 5 | 0.056 | 2 furfural has increased significantly. Other tests are assessed as acceptable.
33000 | 1973 | 38 | 203 | 32 | 186.4 | 2731.2 | 7.1 | 2.4 | 5 | 2.1 | 0 | 12 | 0.093 | 75 |  | 4 | 0.061 | 2-furfural level is high suggesting advanced state of insulation degradation. Other test results are assessed as acceptable.
33000 | 1973 | 38 | 211.9 | 34 | 199.1 | 2410.4 | 7.3 | 1.9 | 2.3 | 1.3 | 0 | 10 | 0.098 | 75 |  | 4.8 | 0.055 | 2-furfural level is high but stable. Other test results are assessed as acceptable. RECOMMEND RESAMPLE IN 1 YEAR TO MONITOR CONDITION.
33000 | 1973 | 38 | 235.8 | 38 | 220.3 | 3036.9 | 9.3 | 2.8 | 2.2 | 1.2 | 0 | 9 | 0.096 | 46 |  | 4.1 | 0.063 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1973 | 38 | 270.8 | 37 | 257.3 | 3064.8 | 8.7 | 2.4 | 1.5 | 0.9 | 0 | 10 | 0.135 | 75 |  | 4 | 0.056 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1973 | 38 | 249.1 | 40 | 237.4 | 2618.7 | 6.9 | 2.8 | 1.2 | 0.8 | 0 | 10 | 0.115 | 75 |  | 4 | 0.066 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable. Corrosive IEC. Non-corrosive ASTM 3B.
33000 | 1973 | 38 | 279.1 | 43 | 266.4 | 2608.4 | 8.8 | 2.1 | 0.9 | 0.9 | 0 | 14 | 0.111 | 78 |  | 4 | 0.062 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable. Corrosive IEC. Non-corrosive ASTM 3B.
33000 | 1973 | 38 | 116.7 | 34 | 111.9 | 2072.1 | 0 | 1.5 | 2.6 | 0.7 | 0 | 18 | 0.102 | 75 |  | 5 | 0.045 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1973 | 38 | 107 | 52 | 93 | 880 | 11 | 1 | 1 | 1 | 0 | 9 | 0.051 | 66 |  | 12 | 0.028 | Test results satisfactory. | Oil quality is assessed as acceptable.
33000 | 1973 | 38 | 126 | 57 | 123 | 1258 | 0 | 1 | 1 | 1 | 0 | 12 | 0.086 | 40 |  | 8.5 | 0.032 | Test results satisfactory. | Oil quality is assessed as acceptable.
33000 | 1973 | 38 | 188 | 45 | 183 | 1440 | 0 | 2 | 1 | 1 | 1 | 25 | 0.081 | 55 |  | 9 | 0.031 | Test results satisfactory. | Oil quality is assessed as acceptable.
33000 | 1973 | 38 | 299 | 40 | 291 | 2371 | 3 | 3 | 1 | 1 | 0 | 11 | 0.079 | 47 |  | 8.7 | 0.035 | Test results satisfactory. | Oil quality is assessed as acceptable.
33000 | 1973 | 38 | 137 | 46 | 118 | 1866 | 15 | 2 | 1 | 1 | 0 | 8 | 0.086 | 75 |  | 4.6 | 0.048 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1973 | 38 | 112.3 | 37 | 108.4 | 2096.6 | 0 | 1.6 | 1.2 | 1.1 | 0 | 11 | 0.093 | 75 |  | 5 | 0.05 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1973 | 38 | 156 | 34 | 146.2 | 1977.6 | 6 | 1.3 | 1.5 | 1 | 0 | 10 | 0.1 | 75 |  | 5.1 | 0.053 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1973 | 38 | 145.8 | 36 | 137 | 2243.4 | 5 | 1.9 | 1.1 | 0.8 | 0 | 9 | 0.095 | 75 |  | 4.9 | 0.053 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1973 | 38 | 152.6 | 40 | 144.4 | 2137.3 | 5.6 | 1.6 | 0.7 | 0.3 | 0 | 10 | 0.132 | 75 |  | 5 | 0.049 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1973 | 38 | 199.1 | 43 | 186.1 | 2037.8 | 5.3 | 6 | 0.9 | 0.8 | 0 | 11 | 0.11 | 75 |  | 5 | 0.053 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable. Corrosive IEC. Non-corrosive ASTM 3B.
33000 | 1973 | 38 | 153.1 | 37 | 141 | 1901.8 | 6.8 | 2.5 | 1.9 | 0.9 | 0 | 15 | 0.095 | 70 |  | 6 | 0.041 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable. Corrosive IEC. Non-corrosive ASTM 3B.
33000 | 1973 | 38 | 170.1 | 44 | 162.1 | 1995.5 | 4.7 | 1.8 | 0.8 | 0.7 | 0 | 13 | 0.102 | 83 |  | 4 | 0.051 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable. Corrosive IEC. Non-corrosive ASTM 3B.
33000 | 1973 | 38 | 83.2 | 36 | 80 | 1519.8 | 0 | 1.2 | 1.6 | 0.4 | 0 | 17 | 0.103 | 64 |  | 5 | 0.043 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1973 | 38 | 232 | 48 | 210 | 1366 | 0 | 1 | 21 | 0 | 0 | 13 | 0.045 | 41 |  | 7.5 | 0.042 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1973 | 38 | 389.7 | 44 | 332.6 | 3679.9 | 6.2 | 1.6 | 48.4 | 0.9 | 0 | 15 | 0.058 | 52 |  | 5 | 0.066 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1973 | 38 | 340.7 | 49 | 305.9 | 2379.8 | 5.1 | 2.1 | 26.8 | 0.8 | 0 | 19 | 0.041 | 23 |  | 5 | 0.054 | DGA is assessed as acceptable. | Breakdown voltage is low. Oil quality is assessed as acceptable. Possible sample contamination.
33000 | 1973 | 38 | 255.7 | 34 | 230.4 | 1780.3 | 3.4 | 1.6 | 20.3 | 0 | 0 | 11 | 0.06 | 75 |  | 4 | 0.056 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1973 | 38 | 197.7 | 48 | 174.9 | 1366.6 | 4.6 | 1.5 | 15.5 | 0.3 | 0.9 | 14 | 0.086 | 86 |  | 4 | 0.078 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1973 | 38 | 31 | 41.81 | 30 | 807 | 0 | 1 | 0 | 0 | 0 | 30 | 0.018 | 46 |  | 6.1 | 0.069 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1973 | 38 | 37.2 | 25 | 33.2 | 785.5 | 1.8 | 1.7 | 0.4 | 0.1 | 0 | 22 | 0.031 | 46 |  | 30 | 0.008 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1973 | 38 | 557 | 41.81 | 508 | 3736 | 19 | 17 | 3 | 10 | 0 | 14 | 0.01 | 53 |  | 56.6 | 0.011 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1973 | 38 | 834 | 45 | 502 | 3142 | 83 | 13 | 36 | 2 | 198 | 14 | 0.106 | 69 |  | 15 | 0.0236 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1973 | 38 | 425 | 32 | 173 | 1815 | 81 | 8 | 21 | 1 | 141 | 9 | 0.101 | 61 |  | 6 | 0.0474 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1973 | 38 | 701 | 39 | 316 | 1988 | 45 | 15 | 37 | 2 | 286 | 16 | 0.116 | 66 |  | 7.2 | 0.038 | DGA results satisfactory. Acetylene gas possibly from tapchanger. | Oil quality is assessed as acceptable.
33000 | 1973 | 38 | 526 | 31 | 286 | 2413 | 55 | 9 | 19 | 2 | 155 | 11 | 0.112 | 74 |  | 5.1 | 0.041 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1973 | 38 | 884.4 | 48 | 435.1 | 3863.9 | 101.8 | 17.4 | 40.1 | 2.5 | 287.5 | 12 | 0.135 | 68 |  | 4 | 0.06 | DGA results are assessed as acceptable. Acetylene gas possibly from tapchanger. | Oil quality is assessed as acceptable.
33000 | 1973 | 38 | 858.1 | 68 | 527.4 | 4341.1 | 93.3 | 16.9 | 27.7 | 8.6 | 184.2 | 30 | 0.134 | 27 |  | 3 | 0.064 | DGA is assessed as acceptable. | Breakdown voltage is low. Possible sample contamination. Other oil quality results are assessed as acceptable.
33000 | 1973 | 38 | 892.5 | 50 | 570 | 4542.9 | 93.1 | 16.7 | 27.8 | 5.8 | 179.1 | 27 | 0.129 | 75 |  | 3 | 0.079 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1973 | 38 | 549 | 51 | 348.7 | 4091.7 | 23.2 | 10.3 | 28.8 | 2.4 | 135.6 | 22 | 0.119 | 69 |  | 4 | 0.058 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1973 | 38 | 735.3 | 68 | 609.5 | 5833.3 | 27.4 | 6.8 | 16.1 | 1.1 | 74.4 | 35 | 0.148 | 29 |  | 4 | 0.061 | DGA is assessed as acceptable | Moisture content is slightly high. Breakdown voltage is slightly low. Other oil quality results are assessed as acceptable.
33000 | 1973 | 38 | 673 | 50 | 220 | 1709 | 168 | 28 | 50 | 2 | 205 | 20 | 0.051 | 67 |  | 17 | 0.0209 | C2H2 level quite high; otherwise test results satisfactory. | Oil quality is assessed as acceptable.
33000 | 1973 | 38 | 642 | 47 | 197 | 1824 | 124 | 22 | 54 | 2 | 243 | 9 | 0.049 | 58 |  | 6 | 0.0624 | Gas levels stable. Test results satisfactory. | Oil quality is assessed as acceptable.
33000 | 1973 | 38 | 946 | 47 | 257 | 2049 | 152 | 40 | 91 | 9 | 397 | 15 | 0.045 | 62 |  | 17.2 | 0.019 | Test results satisfactory. Acetylene gas possibly from tapchanger. | Oil quality is assessed as acceptable. PCB contaminated oil.
33000 | 1973 | 38 | 1139 | 38 | 421 | 3504 | 133 | 33 | 100 | 1 | 451 | 17 | 0.045 | 69 |  | 11.5 | 0.03 | Test results are assessed as acceptable. Acetylene level gas possibly from tapchanger. | Oil quality is assessed as acceptable.
33000 | 1973 | 38 | 614.2 | 43 | 333.5 | 3272.9 | 79.7 | 15.2 | 55.5 | 1.5 | 128.8 | 18 | 0.055 | 43 |  | 8 | 0.047 | The test results are assessed as acceptable. Acetylene gas possibly from tapchanger. | Oil quality is assessed as acceptable.
33000 | 1973 | 38 | 572.2 | 42 | 395.3 | 3331.9 | 39.8 | 13 | 35 | 3.3 | 85.8 | 24 | 0.046 | 75 |  | 7 | 0.041 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1973 | 38 | 515.4 | 55 | 307.5 | 2872.7 | 51.1 | 12.7 | 36.2 | 2.2 | 105.7 | 26 | 0.063 | 45 |  | 8 | 0.033 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1973 | 38 | 516.5 | 38 | 246.4 | 2353.8 | 85.2 | 15.3 | 34.2 | 1.5 | 133.9 | 20 | 0.048 | 54 |  | 10 | 0.023 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1973 | 38 | 343.7 | 40 | 166.8 | 1904.9 | 45.6 | 9.4 | 25.4 | 1.1 | 95.4 | 22 | 0.048 | 46 |  | 10 | 0.025 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1973 | 38 | 277 | 54 | 157 | 1705 | 27 | 8 | 23 | 1 | 61 | 24 | 0.043 | 43 |  | 7 | 0.039 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1973 | 38 | 319.9 | 47 | 183.2 | 2256.1 | 36.1 | 9.9 | 20.7 | 0.4 | 69.6 | 25 | 0.053 | 48 |  | 10 | 0.024 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable. Corrosive IEC. Corrosive ASTM 4A.
33000 | 1973 | 38 | 190.6 | 56 | 126.2 | 1279.4 | 21.2 | 4.7 | 9 | 1.3 | 28.2 | 25 | 0.04 | 44 |  | 11 | 0.024 | Dissolved gas levels are reduced. DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1972 | 39 | 593 | 41.81 | 232 | 2350 | 75 | 20 | 37 | 2 | 227 | 28 | 0.133 | 44 |  | 7 | 0.032 | DGA suggests arcing or persistent sparking - possibly diffusion from tapchanger (tx's 1 - 4 similar).
33000 | 1972 | 39 | 759 | 41.81 | 274 | 2969 | 187 | 22 | 35 | 2 | 239 | 27 | 0.101 | 47 |  | 7.8 | 0.033 | DGA is assessed as acceptable | Oil quality is assessed as acceptable.
33000 | 1972 | 39 | 488 | 41.81 | 186 | 2330 | 61 | 14 | 27 | 1 | 199 | 31 | 0.113 | 41 |  | 7.4 | 0.035 | DGA is assessed as acceptable | Moisture content is high. Other oil quality results are assessed as acceptable.
33000 | 1972 | 39 | 43 | 41.81 | 38 | 377 | 2 | 1 | 1 | 0 | 1 | 14 | 0.01 | 29 |  | 224.4 | 0.006 | DGA is assessed as acceptable | Breakdown voltage is slightly low. Other oil quality results are assessed as acceptable.
33000 | 1972 | 39 | 351 | 50 | 327 | 2458 | 18 | 3 | 2 | 1 | 0 | 7 | 0.01 | 65 |  | 139.8 | 0.007 | DGA is assessed as acceptable | Oil quality is assessed as acceptable.
33000 | 1972 | 39 | 988.9 | 70 | 781 | 4890.8 | 71.5 | 51.6 | 22.4 | 62.2 | 0.2 | 30 | 0.038 | 33 |  | 5 | 0.066 | The test results are consistent with main tank sample and are assessed as acceptable.
33000 | 1972 | 39 | 1166.3 | 70 | 920.8 | 5131.9 | 97.9 | 57.7 | 24 | 65.9 | 0 | 29 | 0.037 | 27 |  | 7.6431 | 0.05115 | The test results are assessed as acceptable at present.
33000 | 1972 | 39 | 909.4 | 56 | 766.6 | 4687.3 | 53.7 | 28.7 | 17.6 | 42.6 | 0.2 | 19 | 0.041 | 51 |  | 7 | 0.045 | 2-furfural level is trending upwards. Other test results are assessed as acceptable. RECOMMEND RESAMPLE IN 1 YEAR TO MONITOR CONDITION.
33000 | 1972 | 39 | 928 | 50 | 776.2 | 7126.1 | 62.8 | 30.7 | 23.2 | 33.5 | 1.6 | 25 | 0.072 | 72 |  | 8 | 0.035 | Carbon oxides are high. | Oil quality is assessed as acceptable.
33000 | 1972 | 39 | 702.4 | 32 | 617.1 | 4950 | 39.8 | 17.4 | 12.9 | 14.9 | 0.3 | 29 | 0.093 | 75 |  | 5 | 0.049 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1972 | 39 | 1087.9 | 56 | 969.8 | 7265.6 | 68.8 | 27.3 | 11 | 11 | 0 | 23 | 0.142 | 47 |  | 4 | 0.064 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1972 | 39 | 613.7 | 40 | 543.1 | 5308 | 44.9 | 7.8 | 10.3 | 7.6 | 0 | 20 | 0.128 | 53 |  | 5 | 0.06 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1972 | 39 | 383.6 | 36 | 328.6 | 3465.3 | 42.5 | 4 | 4.6 | 3.4 | 0.5 | 18 | 0.147 | 61 |  | 4 | 0.061 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable. Corrosive IEC. Non-corrosive ASTM 3B.
33000 | 1972 | 39 | 266.3 | 45 | 234.6 | 2834.1 | 19.9 | 3.4 | 5 | 2.8 | 0.6 | 21 | 0.157 | 37 |  | 4 | 0.058 | DGA is assessed as acceptable. | Breakdown voltage is low. Other oil quality results are assessed as acceptable.
33000 | 1972 | 39 | 331 | 25 | 123 | 1205 | 53 | 8 | 30 | 1 | 116 | 15 | 0.057 | 52 |  | 15 | 0.0289 | Test results satisfactory at present. Check C2H2 level at time of next routine sample. | Oil quality is assessed as acceptable.
33000 | 1972 | 39 | 428 | 27 | 160 | 1244 | 83 | 11 | 29 | 1 | 144 | 9 | 0.066 | 71 |  | 60 | 0.0584 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1972 | 39 | 358 | 38 | 155 | 1196 | 52 | 7 | 31 | 1 | 112 | 18 | 0.085 | 59 |  | 8.4 | 0.033 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1972 | 39 | 286 | 41 | 155 | 1367 | 44 | 5 | 22 | 1 | 59 | 18 | 0.056 | 39 |  | 10.2 | 0.036 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1972 | 39 | 582 | 35 | 172 | 1261 | 105 | 22 | 41 | 1 | 241 | 16 | 0.058 | 61 |  | 6.6 | 0.047 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1972 | 39 | 557.9 | 46 | 281 | 2598.3 | 70 | 13.1 | 49.6 | 0.8 | 143.4 | 16 | 0.064 | 42 |  | 5 | 0.054 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1972 | 39 | 578.6 | 43 | 299.3 | 3061.6 | 68.9 | 12.4 | 44.4 | 3.5 | 150.1 | 16 | 0.075 | 40 |  | 5 | 0.045 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1972 | 39 | 428.2 | 46 | 225.3 | 2415.4 | 49.1 | 10 | 34 | 0 | 109.8 | 17 | 0.082 | 73 |  | 5 | 0.046 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1972 | 39 | 504.4 | 42 | 285.5 | 2647.6 | 52 | 16.3 | 32.6 | 1.2 | 116.8 | 18 | 0.078 | 75 |  | 6 | 0.045 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable. Corrosive IEC. Corrosive ASTM 4A.
33000 | 1972 | 39 | 599.2 | 54 | 449.4 | 3856.3 | 25.7 | 9.4 | 30.1 | 0 | 84.6 | 25 | 0.066 | 40 |  | 6 | 0.035 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable. Corrosive IEC. Corrosive ASTM 4A.
33000 | 1972 | 39 | 442.6 | 48 | 319 | 2982.4 | 36.9 | 6.4 | 16.9 | 1.6 | 61.8 | 19 | 0.08 | 84 |  | 6 | 0.038 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1972 | 39 | 394.5 | 52 | 245.1 | 2534.2 | 33.6 | 7.8 | 18.9 | 1.2 | 87.9 | 26 | 0.088 | 45 |  | 6 | 0.037 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1972 | 39 | 389.4 | 60 | 237.6 | 2390.1 | 45.6 | 7.5 | 16.5 | 0.6 | 81.6 | 21 | 0.078 | 65 |  | 7 | 0.032 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1972 | 39 | 850 | 41.81 | 580 | 2427 | 117 | 11 | 15 | 2 | 125 | 21 | 0.156 | 49 |  | 5.7 | 0.044 | High level of C2H2; possibly from tapchanger?
33000 | 1972 | 39 | 564 | 30 | 278 | 1649 | 110 | 10 | 29 | 2 | 135 | 19 | 0.146 | 61 |  | 5.8 | 0.042 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1972 | 39 | 1320 | 39 | 649 | 3908 | 129 | 43 | 86 | 8 | 405 | 23 | 0.176 | 57 |  | 4.6 | 0.054 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1972 | 39 | 730 | 41.81 | 350 | 2880 | 113 | 17 | 41 | 1 | 208 | 33 | 0.161 | 54 |  | 5.6 | 0.037 | Moisture content of oil slightly high. Other test results are assessed as acceptable. Acetylene gas possibly from tapchanger.
33000 | 1972 | 39 | 986.2 | 54 | 417.9 | 3073.4 | 123.9 | 25 | 78.3 | 0.8 | 340.3 | 23 | 0.189 | 41 |  | 4 | 0.056 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1972 | 39 | 929.2068 | 25 | 454 | 5033 | 100.2268 | 21 | 71.98 | 3.6 | 278.4 | 31 | 0.18 | 53 |  | 4 | 0.055 | DGA is assessed as acceptable. | Moisture content is slightly high. Oil quality is assessed as acceptable.
33000 | 1972 | 39 | 486 | 27 | 137 | 1136 | 65 | 10 | 31 | 2 | 241 | 13 | 0.1 | 66 |  | 7.5 | 0.0334 | DGA is assessed as acceptable. Acetylene gas possibly communicating from tapchanger. | Oil quality is assessed as acceptable.
33000 | 1972 | 39 | 624 | 32 | 146 | 1336 | 82 | 16 | 39 | 2 | 339 | 12 | 0.074 | 47 |  | 10 | 0.0268 | No major increase in gas levels. High C2H2 possibly oil mixing between main tank and tap changer? Tx tripped.
33000 | 1972 | 39 | 978 | 53 | 306 | 2048 | 108 | 27 | 66 | 4 | 467 | 15 | 0.079 | 75 |  | 9.3 | 0.031 | Test results satisfactory. Acetylene gas possibly from tapchanger.
33000 | 1972 | 39 | 1047 | 50 | 423 | 3383 | 116 | 21 | 60 | 1 | 426 | 15 | 0.087 | 61 |  | 7.4 | 0.035 | Test results are assessed as acceptable.
33000 | 1972 | 39 | 926 | 48 | 347 | 2943 | 65 | 18 | 61 | 22 | 413 | 21 | 0.103 | 51 |  | 5 | 0.046 | Test results are assessed as acceptable. Acetylene gas possibly from tapchanger.
33000 | 1972 | 39 | 836.7 | 29 | 216.5 | 2444.9 | 199.2 | 27.1 | 50 | 6.6 | 337.3 | 10 | 0.105 | 56 |  | 5 | 0.04 | The test results are assessed as acceptable. Acetylene gas possibly from tapchanger.
33000 | 1972 | 39 | 609.1 | 26 | 193.2 | 1911.2 | 62.2 | 17.3 | 49.4 | 2.9 | 284.1 | 14 | 0.095 | 50 |  | 5.7 | 0.045 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1972 | 39 | 503.4 | 41 | 191 | 1876.1 | 62 | 11.7 | 30.5 | 1.4 | 206.8 | 12 | 0.14 | 75 |  | 5 | 0.04 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1972 | 39 | 331.3 | 40 | 155.4 | 1530.4 | 55.2 | 6.8 | 15.3 | 1.1 | 97.5 | 13 | 0.104 | 74 |  | 6 | 0.041 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable. Corrosive IEC. Corrosive ASTM 4A.
33000 | 1972 | 39 | 376.1 | 65 | 230.2 | 2370.8 | 40.6 | 3.4 | 12.1 | 0.7 | 89.1 | 17 | 0.108 | 47 |  | 6 | 0.037 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1972 | 39 | 7673.3 | 23 | 267.2 | 2278.3 | 4028.5 | 198.2 | 299.2 | 11.2 | 2869 | 17 | 0.093 | 80 |  | 7 | 0.036 | DGA suggests sample was taken from OLTC. | Oil quality is assessed as acceptable.
33000 | 1972 | 39 | 153 | 31 | 136 | 1087 | 17 | 0 | 0 | 0 | 0 | 14 | 0.04 | 50 |  | 15 | 0.0183 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1972 | 39 | 398 | 42 | 365 | 2428 | 25 | 3 | 3 | 2 | 0 | 33 | 0.066 | 44 |  | 13.3 | 0.021 | Moisture content of oil high. Other test results satisfactory.
33000 | 1972 | 39 | 563 | 45 | 510 | 4136 | 41 | 4 | 4 | 4 | 0 | 14 | 0.072 | 74 |  | 6.4 | 0.037 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1972 | 39 | 299.3 | 36 | 251.3 | 2803.8 | 16.2 | 9.7 | 10.1 | 12 | 0 | 14 | 0.091 | 75 |  | 5 | 0.048 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1972 | 39 | 339.6 | 27 | 315.3 | 3414.1 | 12.9 | 7.6 | 2.4 | 1.4 | 0 | 17 | 0.101 | 75 |  | 4 | 0.048 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1972 | 39 | 219 | 39 | 206.8 | 2357.3 | 8.4 | 1.8 | 1.6 | 0.4 | 0 | 11 | 0.116 | 75 |  | 5 | 0.046 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1972 | 39 | 239.1 | 41 | 225.9 | 2270.2 | 9.8 | 1.7 | 1.2 | 0.5 | 0 | 11 | 0.111 | 52 |  | 5 | 0.058 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable. Non-corrosive IEC. Non-corrosive ASTM 3B.
33000 | 1972 | 39 | 135.5 | 22 | 128.2 | 1841.8 | 4.8 | 0.9 | 0.9 | 0.7 | 0 | 17 | 0.116 | 74 |  | 6 | 0.038 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1972 | 39 | 91.5 | 26 | 88.5 | 1375.5 | 0 | 1.1 | 1.5 | 0.4 | 0 | 16 | 0.117 | 72 |  | 6 | 0.034 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1972 | 39 | 89 | 28 | 85 | 1126 | 0 | 1 | 2 | 1 | 0 | 9 | 0.051 | 59 |  | 10 | 0.036 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1972 | 39 | 162 | 48 | 147 | 1130 | 10 | 2 | 2 | 1 | 0 | 12 | 0.051 | 57 |  | 17.3 | 0.017 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1972 | 39 | 260 | 41.81 | 237 | 2009 | 19 | 2 | 1 | 1 | 0 | 17 | 0.061 | 53 |  | 13.8 | 0.016 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1972 | 39 | 359 | 51 | 328.8 | 2551.3 | 22.5 | 2.9 | 2.6 | 2.2 | 0 | 15 | 0.08 | 75 |  | 8 | 0.028 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1972 | 39 | 747.8 | 55 | 690.2 | 6072.9 | 45.6 | 4.9 | 4.7 | 2.4 | 0 | 29 | 0.095 | 23 |  | 7.0728 | 0.036388 | The test results are consistent with main tank sample. | Breakdown voltage is low.
33000 | 1972 | 39 | 783.1 | 55 | 721.8 | 5981.6 | 49.6 | 4.4 | 4.8 | 2.5 | 0 | 27 | 0.096 | 28 |  | 7.4036 | 0.035123 | Carbon oxide levels are high suggesting insulation degradation. | Breakdown voltage of sample is slightly low. Possible sample contamination.
33000 | 1972 | 39 | 436.4 | 46 | 412.9 | 3795 | 16.5 | 2.9 | 2.6 | 1.5 | 0 | 18 | 0.083 | 75 |  | 6 | 0.038 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1972 | 39 | 298.5 | 45 | 273.4 | 3065.5 | 19.8 | 2.4 | 2 | 0.9 | 0 | 22 | 0.09 | 60 |  | 6 | 0.038 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1972 | 39 | 370.9 | 48 | 342.8 | 3206.4 | 16.6 | 2.4 | 5.6 | 3.5 | 0 | 27 | 0.096 | 48 |  | 5 | 0.045 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1972 | 39 | 328.3 | 61 | 309.7 | 3365.6 | 12.6 | 2.6 | 1.9 | 1.3 | 0.2 | 27 | 0.113 | 53 |  | 5 | 0.045 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1972 | 39 | 649.6 | 46 | 4.8 | 608.3 | 18.3 | 10.8 | 62.2 | 9 | 544.5 | 19 | 0.004 | 76 |  | 333 | 0.002 | DGA is assessed as acceptable. | Breakdown voltage is assessed as acceptable. Particle contamination load is high.
33000 | 1972 | 39 | 246.8 | 49 | 233 | 2716.4 | 10.7 | 2 | 1.1 | 0 | 0 | 24 | 0.12 | 58 |  | 6 | 0.036 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1972 | 39 | 671 | 34 | 431 | 2045 | 120 | 43 | 26 | 37 | 14 | 23 | 0.133 | 61 |  | 4 | 0.109 | Test results satisfactory. | Oil quality is assessed as acceptable.
33000 | 1972 | 39 | 688 | 29 | 423 | 1800 | 116 | 38 | 25 | 28 | 58 | 17 | 0.157 | 70 |  | 3 | 0.136 | Test results satisfactory. | Oil quality is assessed as acceptable.
33000 | 1972 | 39 | 1344 | 38 | 982 | 4106 | 152 | 74 | 55 | 24 | 57 | 33 | 0.188 | 30 |  | 3.3 | 0.091 | DGA is assessed as acceptable. Acetylene gas possibly from tapchanger. | Moisture content of oil slightly high. Other test results satisfactory.
33000 | 1972 | 39 | 1007 | 45 | 841 | 3649 | 87 | 12 | 22 | 4 | 41 | 31 | 0.193 | 58 |  | 4 | 0.075 | DGA is assessed as acceptable. | Moisture content of oil slightly high. Other test results satisfactory.
33000 | 1972 | 39 | 998 | 37 | 799 | 4834 | 123 | 25 | 21 | 16 | 14 | 31 | 0.21 | 48 |  | 4 | 0.0621 | Dissolved gas analysis appears to be normal after buchholz trip. | Other test results are assessed as acceptable.
33000 | 1972 | 39 | 1034 | 42 | 821 | 4326 | 144 | 20 | 17 | 15 | 17 | 28 | 0.212 | 59 |  | 4.1 | 0.053 | Test results are are assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1972 | 39 | 999.452 | 42 | 685.4296 | 4769.7204 | 137.085 | 31.8605 | 61.001 | 21.2322 | 62.8437 | 21 | 0.258 | 47 |  | 4 | 0.054 | The test results are assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1972 | 39 | 6.6 | 41.81 | 5.5 | 122.2 | 0 | 0.2 | 0.4 | 0.3 | 0.2 | 7 | 0.021 | 77 |  | 14 | 0.025 | The test results are assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1972 | 39 | 5.2 | 41.81 | 3.3 | 167.4 | 0 | 0.4 | 1.3 | 0.2 | 0 | 7 | 0.024 | 75 |  | 17 | 0.024 | The test results are assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1972 | 39 | 4.4 | 41.81 | 3.5 | 88.4 | 0 | 0.7 | 0.2 | 0 | 0 | 10 | 0.035 | 75 |  | 12 | 0.027 | The test results are assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1972 | 39 | 5.4 | 20 | 4.6 | 147.9 | 0 | 0.5 | 0.3 | 0 | 0 | 9 | 0.033 | 75 |  | 13 | 0.028 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1972 | 39 | 9.7 | 20 | 4.2 | 285.3 | 2 | 3.4 | 0.1 | 0 | 0 | 9 | 0.024 | 49 |  | 13 | 0.025 | The test results are assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1972 | 39 | 173.8 | 38 | 149.5 | 1796.1 | 19.2 | 2.5 | 1.4 | 1 | 0.2 | 10 | 0.061 | 75 |  | 7 | 0.044 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1972 | 39 | 145.3 | 45 | 123.6 | 1665.2 | 17 | 1.8 | 1.7 | 1 | 0.2 | 8 | 0.059 | 75 |  | 7 | 0.041 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1972 | 39 | 137.2 | 43 | 113.9 | 1636 | 18.3 | 2.1 | 1 | 1.2 | 0.7 | 12 | 0.062 | 64 |  | 7 | 0.042 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1972 | 39 | 97.5 | 46 | 87.8 | 1401.2 | 6.6 | 1.7 | 0.5 | 0.9 | 0 | 12 | 0.069 | 75 |  | 6 | 0.042 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1972 | 39 | 88.9 | 37 | 77.2 | 1224.6 | 6.8 | 1.6 | 0.8 | 1.5 | 1 | 11 | 0.065 | 75 |  | 7 | 0.038 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1972 | 39 | 87.2 | 33 | 62.2 | 1190.6 | 20.2 | 1.6 | 0.6 | 1.8 | 0.8 | 20 | 0.06 | 70 |  | 8 | 0.032 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable. Corrosive IEC. Corrosive ASTM 4A.
33000 | 1972 | 39 | 75.3 | 35 | 62.6 | 1074.8 | 7.5 | 1.6 | 0.8 | 0.8 | 2 | 17 | 0.075 | 69 |  | 7 | 0.034 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1972 | 39 | 668 | 28 | 214 | 1615 | 112 | 22 | 41 | 2 | 277 | 16 | 0.128 | 63 |  | 10 | 0.0305 | Acetylene level quite high. Other results satisfactory. | Oil quality is assessed as acceptable.
33000 | 1972 | 39 | 630 | 37 | 265 | 1725 | 73 | 15 | 33 | 2 | 242 | 15 | 0.118 | 60 |  | 7 | 0.0314 | Gas levels stable. Test results satisfactory. | Oil quality is assessed as acceptable.
33000 | 1972 | 39 | 1132 | 42 | 184 | 1499 | 108 | 45 | 169 | 13 | 613 | 12 | 0.114 | 46 |  | 5.8 | 0.044 | Test results satisfactory. Acetylene gas possibly from tapchanger. | Oil quality is assessed as acceptable.
33000 | 1972 | 39 | 52 | 44 | 14 | 321 | 3 | 2 | 6 | 1 | 26 | 12 | 0.014 | 65 |  | 59.4 | 0.007 | Test results are assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1972 | 39 | 609.4 | 46 | 189.6 | 2175.4 | 78.4 | 13.9 | 54.1 | 1.9 | 271.5 | 11 | 0.012 | 53 |  | 27 | 0.015 | The test results are assessed as acceptable. Acetylene gas possibly from tapchanger. | Oil quality is assessed as acceptable.
33000 | 1972 | 39 | 749.3 | 42 | 279 | 2806 | 109.8 | 22 | 59.1 | 6 | 273.4 | 16 | 0.011 | 53 |  | 38 | 0.01 | The test results are assessed as acceptable. Acetylene gas possibly communicating from tapchanger. | Oil quality is assessed as acceptable.
33000 | 1972 | 39 | 361.4 | 42 | 200.2 | 2357.6 | 19.9 | 7.2 | 31.2 | 3.4 | 99.5 | 13 | 0.015 | 54 |  | 36 | 0.011 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1972 | 39 | 239.1 | 38 | 181.5 | 2370.1 | 10.1 | 3 | 18.7 | 0 | 25.8 | 12 | 0.015 | 70 |  | 17 | 0.017 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1972 | 39 | 579 | 28 | 203 | 1583 | 114 | 17 | 42 | 1 | 202 | 18 | 0.066 | 67.5 |  | 15 | 0.02 | Acetylene level quite high. Otherwise test results satisfactory. | Oil quality is assessed as acceptable.
33000 | 1972 | 39 | 424 | 36 | 137 | 1640 | 51 | 11 | 38 | 2 | 185 | 16 | 0.06 | 61 |  | 7 | 0.046 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1972 | 39 | 1068 | 38 | 198 | 1370 | 143 | 34 | 78 | 3 | 612 | 13 | 0.076 | 47 |  | 9.2 | 0.03 | DGA is assessed as acceptable. Acetylene gas possibly communicating from tapchanger. | Oil quality is assessed as acceptable.
33000 | 1972 | 39 | 528 | 48 | 333 | 2474 | 52 | 3 | 30 | 0 | 110 | 17 | 0.079 | 75 |  | 7.6 | 0.028 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1972 | 39 | 767.6 | 50 | 402.8 | 2998.6 | 89.6 | 17.9 | 49.3 | 10.2 | 197.8 | 19 | 0.104 | 46 |  | 5 | 0.04 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1972 | 39 | 945.1 | 38 | 705.2 | 4961.5 | 92.5 | 10.4 | 31.7 | 7.6 | 97.7 | 27 | 0.112 | 52 |  | 5 | 0.04 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1972 | 39 | 637.9 | 41 | 509.3 | 4388.6 | 57.6 | 6.9 | 13.4 | 3.1 | 47.6 | 32 | 0.116 | 60 |  | 5 | 0.048 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1972 | 39 | 658.1 | 38 | 441.2 | 4551.3 | 58.3 | 12.3 | 23.6 | 0 | 122.7 | 21 | 0.152 | 30 |  | 4 | 0.048 | DGA is assessed as acceptable. | Breakdown voltage is slightly low. Other oil quality results are assessed as acceptable.
33000 | 1971 | 40 | 267 | 41.81 | 129 | 1397 | 24 | 3 | 13 | 1 | 97 | 9 | 0.028 | 46 |  | 50 | 0.0076 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1971 | 40 | 0 | 41.81 | 0 | 284 | 0 | 0 | 0 | 0 | 0 | 18 | 0.045 | 54 |  | 25 | 0.02 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1971 | 40 | 154 | 37 | 129 | 1138 | 0 | 1 | 23 | 0 | 1 | 19 | 0.041 | 54 |  | 16.3 | 0.02 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1971 | 40 | 206 | 42 | 155 | 2100 | 0 | 3 | 36 | 0 | 12 | 30 | 0.056 | 55 |  | 20.3 | 0.016 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1971 | 40 | 457 | 45 | 404 | 5358 | 0 | 3 | 49 | 1 | 0 | 26 | 0.054 | 74 |  | 18.8 | 0.019 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1971 | 40 | 509 | 40 | 351 | 5391 | 130 | 3 | 24 | 1 | 0 | 32 | 0.082 | 70 |  | 9.2 | 0.03 | 2-Furfural level is quite high. Moisture content of oil is above defect level. Other test results are assessed as acceptable.
33000 | 1971 | 40 | 428 | 50 | 357 | 4757 | 46 | 3 | 21 | 1 | 0 | 38 | 0.1 | 42 |  | 11 | 0.025 | Moisture content is high. 2-furfural level is high suggesting advanced rate of insulation degradation. RECOMMEND INVESTIGATE.
33000 | 1971 | 40 | 85.4 | 41.81 | 72.7 | 1528.9 | 3.4 | 1.1 | 8.2 | 0 | 0 | 26 | 0.093 | 46 |  | 10 | 0.03 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1971 | 40 | 648 | 50 | 156 | 1435 | 49 | 18 | 60 | 2 | 363 | 16 | 0.052 | 53 |  | 67.7 | 0.016 | Test results are assessed as acceptable. Acetylene gas possibly from tapchanger. | Oil quality is assessed as acceptable.
33000 | 1971 | 40 | 754 | 62 | 218 | 4940 | 33 | 9 | 97 | 5 | 392 | 38 | 0.057 | 24 |  | 10 | 0.027 | DGA is assessed as acceptable. Acetylene gas possibly communicating from tapchanger. | Moisture content of sample is high. Breakdown voltage of sample is low. Other test results are assessed as acceptable.
33000 | 1971 | 40 | 472.7 | 39 | 163.5 | 2951.8 | 19 | 7.5 | 49.4 | 4.7 | 228.6 | 13 | 0.052 | 75 |  | 10.2 | 0.027 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1971 | 40 | 485.2 | 48 | 209.8 | 3806.9 | 18.1 | 9.2 | 45.8 | 0.8 | 201.5 | 19 | 0.06 | 62 |  | 9 | 0.025 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1971 | 40 | 433.6 | 54 | 284.7 | 4153 | 12 | 8.3 | 33 | 1 | 94.6 | 20 | 0.06 | 58 |  | 10 | 0.027 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable. Corrosive IEC. Corrosive ASTM 4A.
33000 | 1971 | 40 | 127.7 | 41.81 | 83.1 | 1159.4 | 8.2 | 2.8 | 6.1 | 0.3 | 27.2 | 17 | 0.053 | 71 |  | 9 | 0.026 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1971 | 40 | 336.7 | 53 | 191.9 | 2840.8 | 11.6 | 6.5 | 28.9 | 1 | 96.8 | 23 | 0.057 | 71 |  | 9 | 0.028 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1971 | 40 | 247.9 | 53 | 116.2 | 2097.5 | 11.3 | 4.6 | 25.2 | 0.4 | 90.2 | 21 | 0.057 | 84 |  | 9 | 0.026 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1971 | 40 | 335.7 | 48 | 167.7 | 2582.4 | 16.2 | 6.2 | 32.7 | 0 | 112.9 | 24 | 0.057 | 62 |  | 9 | 0.026 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1971 | 40 | 827 | 29 | 356 | 1746 | 99 | 26 | 65 | 1 | 280 | 19 | 0.069 | 74 |  | 6 | 0.047 | DGA is assessed as acceptable. Acetylene gas possibly communicating from tapchanger. | Oil quality is assessed as acceptable.
33000 | 1971 | 40 | 987 | 40 | 752 | 4144 | 122 | 19 | 31 | 6 | 57 | 46 | 0.176 | 36 |  | 3.8 | 0.056 | DGA is assessed as acceptable. | Acidity and moisture high.
33000 | 1971 | 40 | 1059 | 41.81 | 799 | 4550 | 121 | 19 | 34 | 6 | 80 | 20 | 0.181 | 64 |  | 4.4 | 0.062 | DGA is assessed as acceptable. | Acidity high otherwise test results satisfactory. PCB content below 2mg/kg.
33000 | 1971 | 40 | 742 | 44 | 541 | 4111 | 69 | 9 | 24 | 2 | 97 | 29 | 0.215 | 60 |  | 4.1 | 0.05 | DGA is assessed as acceptable. | Acidity level is slightly high. Other test results are assessed as acceptable.
33000 | 1971 | 40 | 562 | 48 | 367.9 | 3586 | 38.2 | 8.8 | 27.5 | 1.7 | 117.9 | 26 | 0.282 | 36 |  | 4 | 0.054 | DGA is assessed as acceptable. | Acidity level of oil is high. Other test results are assessed as acceptable.
33000 | 1971 | 40 | 531.4 | 48 | 340 | 4654.4 | 31.6 | 10.4 | 26.2 | 6 | 117.2 | 29 | 0.289 | 45 |  | 3 | 0.064 | DGA is assessed as acceptable. | Acidity level of sample is high. Other test results are assessed as acceptable.
33000 | 1971 | 40 | 861.9 | 49 | 728.3 | 7421 | 42.2 | 11 | 20.6 | 4.5 | 55.3 | 39 | 0.252 | 42 |  | 3.9492 | 0.06303 | DGA is assessed as acceptable. | Moisture content of sample is high. Acidity level of sample is high but stable.
33000 | 1971 | 40 | 618.7 | 42 | 443 | 5362.2 | 35.5 | 9.6 | 20.7 | 4 | 105.9 | 34 | 0.309 | 36 |  | 4 | 0.062 | DGA is assessed as acceptable. | Oil quality is poor.
33000 | 1971 | 40 | 555.6 | 46 | 426.4 | 5966.2 | 31.5 | 7.1 | 14.9 | 2.2 | 73.5 | 29 | 0.303 | 53 |  | 4.9 | 0.049 | DGA is assessed as acceptable. | Acidity level is high. Other oil quality results are assessed as acceptable.
33000 | 1971 | 40 | 508 | 44 | 295.5 | 4614.2 | 26.5 | 8.4 | 18.7 | 1.4 | 157.5 | 35 | 0.374 | 60 |  | 4 | 0.068 | DGA is assessed as acceptable. | Moisture content is high. Acidity level is high. Other oil quality results are assessed as acceptable at present.
33000 | 1971 | 40 | 384.7 | 48 | 216.8 | 3477.4 | 19.9 | 5.8 | 19.3 | 1.3 | 121.6 | 33 | 0.322 | 63 |  | 4 | 0.065 | DGA is assessed as acceptable. | Acidity level is high. Other oil quality results are assessed as acceptable. Corrosive IEC. Corrosive astm 4A.
33000 | 1971 | 40 | 159.9 | 37 | 97.4 | 1977.7 | 6.7 | 3.2 | 8 | 1.1 | 43.5 | 24 | 0.324 | 59 |  | 4 | 0.056 | DGA is assessed as acceptable. | Acidity level is high but stable. Other oil quality results are assessed as acceptable. Corrosive IEC. Corrosive ASTM 4A.
33000 | 1971 | 40 | 148.4 | 36 | 86.1 | 1855.9 | 7.3 | 3.2 | 8 | 0.8 | 43 | 23 | 0.325 | 74 |  | 4 | 0.05 | DGA is assessed as acceptable. | Acidity level is high. Other oil quality results are assessed as acceptable.
33000 | 1971 | 40 | 638 | 29 | 298 | 1341 | 78 | 19 | 46 | 1 | 196 | 18 | 0.099 | 68 |  | 5.5 | 0.041 | DGA is assessed as acceptable. Acetylene gas possibly communicating from tapchanger. | Oil quality is assessed as acceptable.
33000 | 1971 | 40 | 854 | 42 | 646 | 3791 | 84 | 12 | 22 | 3 | 87 | 34 | 0.166 | 60 |  | 3.2 | 0.057 | DGA is assessed as acceptable. | Moisture content high. Otherwise test results satisfactory.
33000 | 1971 | 40 | 578 | 46 | 420 | 3136 | 52 | 7 | 16 | 1 | 82 | 25 | 0.189 | 61 |  | 3.4 | 0.067 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1971 | 40 | 438.9 | 51 | 233.6 | 2867.4 | 27.9 | 8.6 | 25.5 | 1.7 | 141.6 | 21 | 0.246 | 44 |  | 3 | 0.065 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1971 | 40 | 630.9 | 50 | 515 | 6029.7 | 28.8 | 7.6 | 16.1 | 4.7 | 58.7 | 35 | 0.248 | 34 |  | 3 | 0.076 | Carbon oxide levels are high. | Moisture content of sample is high. Acidity level is high but stable. Other test results are assessed as acceptable.
33000 | 1971 | 40 | 500.9 | 42 | 322 | 4269.5 | 31.8 | 8.6 | 19.2 | 3.7 | 115.6 | 25 | 0.228 | 45 |  | 3 | 0.083 | DGA is assessed as acceptable. | Acidity level is high but stable. Other oil quality results are assessed as acceptable.
33000 | 1971 | 40 | 407.6 | 46 | 284.8 | 4717.7 | 28 | 6.2 | 14.3 | 1.7 | 72.6 | 26 | 0.229 | 70 |  | 3.7 | 0.064 | DGA is assessed as acceptable. | Acidity level is high. Other oil quality results are assessed as acceptable.
33000 | 1971 | 40 | 463.5 | 46 | 228.2 | 3782 | 24.1 | 8.4 | 19.8 | 1.5 | 181.5 | 28 | 0.28 | 38 |  | 3 | 0.069 | DGA is assessed as acceptable. | Acidity level is high. Breakdown voltage is slightly low. Other oil quality results are assessed as acceptable.
33000 | 1971 | 40 | 315.3 | 30 | 173.1 | 2854.4 | 17.1 | 4.4 | 16.2 | 1.3 | 103.2 | 23 | 0.243 | 59 |  | 3 | 0.084 | DGA is assessed as acceptable. | Acidity level is high. Other oil quality results are assessed as acceptable. Corrosive IEC. Corrosive ASTM 4B.
33000 | 1971 | 40 | 173.8 | 39 | 86.8 | 1705.3 | 11.2 | 3.9 | 10.1 | 1 | 60.8 | 18 | 0.226 | 82 |  | 3 | 0.068 | DGA is assessed as acceptable. | Acidity level is high but stable. Other oil quality results are assessed as acceptable. Corrosive IEC. Corrosive ASTM 4A.
33000 | 1971 | 40 | 134.9 | 38 | 65.7 | 1703.5 | 0 | 2.9 | 9.4 | 0.8 | 56.1 | 22 | 0.232 | 43 |  | 3 | 0.06 | DGA is assessed as acceptable. | Acidity level is high. Other oil quality results are assessed as acceptable.
33000 | 1971 | 40 | 250 | 33 | 112 | 820 | 26 | 7 | 18 | 1 | 86 | 10 | 0.061 | 61 |  | 6.5 | 0.042 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1971 | 40 | 717 | 45 | 222 | 2020 | 52 | 15 | 52 | 4 | 372 | 8 | 0.08 | 75 |  | 4.6 | 0.045 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1971 | 40 | 444.5 | 36 | 171.3 | 2180.6 | 32.4 | 17.2 | 38.1 | 1.8 | 183.7 | 14 | 0.095 | 75 |  | 3 | 0.07 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1971 | 40 | 394.8 | 32 | 198.4 | 2319.7 | 29.3 | 6.3 | 29.4 | 4.2 | 127.2 | 9 | 0.15 | 75 |  | 2 | 0.078 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1971 | 40 | 304.7 | 39 | 190.4 | 2204.5 | 26.8 | 4.7 | 11.4 | 1.2 | 70.2 | 12 | 0.099 | 60 |  | 2 | 0.098 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable. Corrosive IEC. Corrosive ASTM 4A.
33000 | 1971 | 40 | 260.4 | 44 | 170.2 | 2409.7 | 20.8 | 3.7 | 8.9 | 0.9 | 55.9 | 20 | 0.1 | 71 |  | 3 | 0.076 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1971 | 40 | 230.3 | 39 | 144.1 | 1935.8 | 20 | 3.5 | 8.2 | 0.4 | 54.1 | 18 | 0.095 | 65 |  | 3 | 0.081 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1971 | 40 | 518 | 38 | 144 | 1312 | 63 | 17 | 48 | 2 | 244 | 16 | 0.078 | 59 |  | 8 | 0.038 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1971 | 40 | 464 | 36 | 210 | 1455 | 52 | 11 | 38 | 1 | 152 | 11 | 0.078 | 74 |  | 5 | 0.055 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1971 | 40 | 628 | 50 | 277 | 1955 | 46 | 10 | 48 | 1 | 246 | 16 | 0.074 | 57 |  | 5 | 0.053 | DGA is assessed as acceptable. Acetylene gas possibly communicating from tapchanger. | Oil quality is assessed as acceptable.
33000 | 1971 | 40 | 550 | 52 | 198 | 1922 | 29 | 12 | 44 | 1 | 266 | 22 | 0.085 | 58 |  | 4.7 | 0.044 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1971 | 40 | 551.5 | 47 | 261.9 | 1984 | 32.8 | 13.2 | 47.2 | 12.8 | 183.6 | 17 | 0.106 | 74 |  | 3 | 0.063 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1971 | 40 | 383.7 | 42 | 279.8 | 2629.5 | 18.5 | 5.7 | 21.9 | 3 | 54.8 | 24 | 0.106 | 39 |  | 3 | 0.073 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1971 | 40 | 528.5 | 51 | 330.8 | 3337.3 | 41.8 | 9.8 | 30.7 | 1.3 | 114.1 | 23 | 0.12 | 46 |  | 3 | 0.068 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1971 | 40 | 429.6 | 60 | 314.2 | 3173.8 | 16.5 | 5.7 | 20.7 | 1.2 | 71.3 | 34 | 0.119 | 25 |  | 3 | 0.065 | DGA is assessed as acceptable. | Breakdown voltage is low. Other oil quality results are assessed as acceptable.
33000 | 1971 | 40 | 384.6 | 49 | 266.3 | 3671.5 | 20.9 | 5.3 | 17 | 1.5 | 73.6 | 33 | 0.147 | 38 |  | 4 | 0.063 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable. Corrosive IEC. Corrosive ASTM 4A.
33000 | 1971 | 40 | 318 | 28 | 129 | 1007 | 26 | 7 | 23 | 2 | 131 | 9 | 0.038 | 61 |  | 8 | 0.026 | C2H2 Slightly high. Otherwise test results satisfactory. | Oil quality is assessed as acceptable.
33000 | 1971 | 40 | 475 | 45 | 207 | 1517 | 65 | 13 | 27 | 1 | 162 | 9 | 0.05 | 60 |  | 3.5 | 0.058 | Test results are assessed as acceptable. Acetylene gas possibly from tapchanger. | Oil quality is assessed as acceptable.
33000 | 1971 | 40 | 661.2 | 38 | 191.1 | 2343.8 | 68.6 | 27.4 | 54.5 | 2 | 317.6 | 14 | 0.09 | 75 |  | 3 | 0.068 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1971 | 40 | 625.8 | 32 | 206 | 2460.6 | 56.9 | 14.7 | 43.7 | 2.8 | 301.7 | 13 | 0.143 | 75 |  | 3 | 0.0685 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1971 | 40 | 421.4 | 40 | 236.3 | 2435.6 | 42.8 | 10.7 | 34 | 4.3 | 93.3 | 15 | 0.098 | 79 |  | 3 | 0.073 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable. Corrosive IEC. Corrosive ASTM 4A.
33000 | 1971 | 40 | 326.6 | 50 | 203 | 2755.7 | 34.8 | 6.1 | 14.7 | 1.1 | 66.9 | 21 | 0.098 | 76 |  | 3 | 0.068 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable. Corrosive IEC. Non-corrosive ASTM 3A.
33000 | 1971 | 40 | 284.5 | 40 | 141.2 | 2034 | 31.7 | 6 | 16 | 1 | 88.6 | 21 | 0.093 | 69 |  | 3 | 0.063 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1971 | 40 | 268 | 20 | 93 | 1240 | 0 | 10 | 40 | 1 | 124 | 33 | 0.05 | 45 |  | 17.3 | 0.018 | Test results satisfactory. Acetylene gas possibly from tapchanger. | Oil quality is assessed as acceptable.
33000 | 1971 | 40 | 850 | 62 | 224 | 2032 | 70 | 33 | 77 | 2 | 444 | 31 | 0.057 | 58 |  | 10.6 | 0.027 | Test results satisfactory. Acetylene gas possibly from tapchanger. | Oil quality is assessed as acceptable.
33000 | 1971 | 40 | 667 | 50 | 158 | 1387 | 59 | 21 | 60 | 2 | 367 | 18 | 0.05 | 59 |  | 12.3 | 0.021 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1971 | 40 | 931.9 | 48 | 210.8 | 4933.3 | 67.2 | 14 | 124.4 | 8.4 | 507.1 | 11 | 0.052 | 59 |  | 9 | 0.034 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1971 | 40 | 516 | 40 | 182 | 3121 | 33 | 9 | 52 | 5 | 235 | 16 | 0.052 | 73 |  | 10.8 | 0.026 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1971 | 40 | 492.9 | 46 | 186.5 | 3796.3 | 34 | 11.1 | 45.6 | 1.3 | 214.4 | 24 | 0.057 | 45 |  | 9 | 0.026 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1971 | 40 | 407.5 | 54 | 257.7 | 4347.9 | 19.1 | 8.7 | 29.7 | 1.1 | 91.2 | 27 | 0.053 | 62 |  | 11 | 0.025 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable. Corrosive IEC. Corrosive ASTM 4B.
33000 | 1971 | 40 | 149.9 | 41.81 | 83 | 1396.4 | 13.4 | 4.8 | 7.4 | 0.4 | 40.9 | 21 | 0.042 | 62 |  | 10 | 0.026 | Dissolved gas levels are reduced. DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1971 | 40 | 323.6 | 52 | 153.4 | 2770.9 | 21.5 | 8.1 | 26.8 | 0.9 | 112.9 | 23 | 0.042 | 74 |  | 11 | 0.021 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1971 | 40 | 348.7 | 51 | 95.2 | 2124.9 | 28.8 | 10.7 | 33.2 | 4.5 | 176.3 | 24 | 0.041 | 63 |  | 13 | 0.02 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1971 | 40 | 410.6 | 48 | 128.4 | 2652 | 30 | 12 | 42.3 | 0 | 197.9 | 26 | 0.039 | 79 |  | 12 | 0.019 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1971 | 40 | 48.5 | 20 | 44.9 | 1068.6 | 2.1 | 1.2 | 0.3 | 0 | 0 | 23 | 0.087 | 27 |  | 4 | 0.051 | DGA is assessed as acceptable. | Breakdown voltage is low. Other oil quality results are assessed as acceptable.
33000 | 1971 | 40 | 38.3 | 18 | 34.2 | 992.2 | 1.5 | 0.7 | 1.6 | 0.2 | 0.1 | 24 | 0.09 | 76 |  | 5 | 0.039 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1971 | 40 | 68.9 | 12 | 58.1 | 946.9 | 1.3 | 1.7 | 7.5 | 0.2 | 0.1 | 14 | 0.074 | 79 |  | 6 | 0.048 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1971 | 40 | 332 | 25 | 125 | 1139 | 42 | 9 | 34 | 1 | 121 | 14 | 0.072 | 50 |  | 9 | 0.0302 | Test results satisfactory at present. Check C2H2 level at next routine sample. | Oil quality is assessed as acceptable.
33000 | 1971 | 40 | 401 | 38 | 148 | 1032 | 69 | 12 | 29 | 1 | 142 | 11 | 0.064 | 60 |  | 60 | 0.0402 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1971 | 40 | 423 | 42 | 155 | 1152 | 56 | 9 | 33 | 1 | 169 | 14 | 0.073 | 64 |  | 8.2 | 0.037 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1971 | 40 | 360 | 46 | 150 | 1344 | 47 | 8 | 28 | 1 | 126 | 12 | 0.064 | 66 |  | 10.8 | 0.028 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1971 | 40 | 454 | 38 | 155 | 1251 | 49 | 12 | 37 | 1 | 200 | 15 | 0.061 | 45 |  | 6.8 | 0.035 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1971 | 40 | 669.3 | 49 | 236.1 | 2264.5 | 79.2 | 20.1 | 62.8 | 1.4 | 269.7 | 17 | 0.064 | 39 |  | 5 | 0.056 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1971 | 40 | 599.7 | 49 | 218.3 | 2236.2 | 74.6 | 17.5 | 47.7 | 5 | 236.6 | 18 | 0.064 | 65 |  | 6 | 0.043 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1971 | 40 | 432.2 | 50 | 167.9 | 1914 | 51.1 | 12.9 | 35.6 | 0 | 164.7 | 14 | 0.066 | 75 |  | 6 | 0.04 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1971 | 40 | 466.1 | 48 | 185 | 2116.8 | 55.6 | 13.1 | 37.9 | 1.5 | 173 | 14 | 0.059 | 58 |  | 5 | 0.053 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable. Corrosive IEC. Corrosive ASTM 4A.
33000 | 1971 | 40 | 560 | 44 | 198 | 2118 | 85 | 23 | 39 | 2 | 213 | 27 | 0.051 | 49 |  | 16 | 0.021 | DGA suggests arcing or persistent sparking - possibly diffusion from tapchanger (tx's 1 - 4 similar).
33000 | 1971 | 40 | 511 | 53 | 243 | 2660 | 68 | 14 | 26 | 1 | 159 | 28 | 0.043 | 54 |  | 26.9 | 0.01 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1971 | 40 | 519 | 44 | 108 | 2423 | 41 | 18 | 49 | 2 | 301 | 15 | 0.052 | 46 |  | 21.6 | 0.015 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1971 | 40 | 435.3 | 40 | 325.9 | 3214.9 | 62.9 | 13.6 | 24.5 | 7.8 | 0.6 | 6 | 0.01 | 60 |  | 76 | 0.008 | The test results are assessed as acceptable. Dissolved hydrocarbon gas levels are reduced. 2-furfural level is reduced.
33000 | 1971 | 40 | 732.6 | 60 | 545.2 | 3944.2 | 49.8 | 58.5 | 23 | 56.1 | 0 | 16 | 0.018 | 39 |  | 10.9435 | 0.039248 | The test results are consistent with main tank sample and are assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1971 | 40 | 863.4 | 60 | 648 | 4242.2 | 66.4 | 65.6 | 24.7 | 58.7 | 0 | 19 | 0.017 | 28 |  | 9.0185 | 0.04488 | DGA is assessed as acceptable | Breakdown voltage is slightly low. Possible sample contamination. Other test results are assessed as acceptable.
33000 | 1971 | 40 | 705.6 | 50 | 592.8 | 4878 | 60.3 | 16.9 | 14.2 | 21.4 | 0 | 16 | 0.04 | 75 |  | 4 | 0.062 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1971 | 40 | 922.4 | 50 | 837.7 | 7557.5 | 60.5 | 12.5 | 7.4 | 4.3 | 0 | 24 | 0.093 | 75 |  | 4 | 0.065 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1971 | 40 | 348.3 | 44 | 306.5 | 3808.1 | 31.1 | 2.8 | 4 | 2.9 | 1 | 18 | 0.086 | 47 |  | 3 | 0.078 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1971 | 40 | 335.2 | 38 | 278.6 | 3553 | 39 | 8.2 | 4.6 | 2.8 | 2 | 14 | 0.096 | 84 |  | 4 | 0.048 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1971 | 40 | 262.3 | 43 | 235 | 2994.2 | 19.4 | 2.6 | 2.6 | 1.7 | 1 | 18 | 0.105 | 78 |  | 3 | 0.067 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1971 | 40 | 548 | 41.81 | 271 | 2204 | 68 | 19 | 27 | 1 | 162 | 33 | 0.14 | 16 |  | 6 | 0.041 | DGA suggests arcing or persistent sparking - possibly diffusion from tapchanger (tx's 1 - 4 similar).
33000 | 1971 | 40 | 735 | 41.81 | 357 | 3843 | 86 | 18 | 32 | 2 | 240 | 27 | 0.176 | 64 |  | 5.8 | 0.04 | DGA is assessed as acceptable | Oil quality is assessed as acceptable.
33000 | 1971 | 40 | 600 | 41.81 | 173 | 3108 | 24 | 20 | 45 | 2 | 336 | 58 | 0.16 | 35 |  | 6.7 | 0.041 | DGA is assessed as acceptable | Moisture content of oil high; possibly sample contamination. Other test results satisfactory.
33000 | 1971 | 40 | 729 | 41.81 | 281 | 3550 | 83 | 27 | 38 | 2 | 298 | 29 | 0.141 | 56 |  | 5.9 | 0.041 | Sampled after buchholz trip. No significant increase in gas levels.
33000 | 1971 | 40 | 294 | 74 | 229 | 2450 | 15 | 3 | 46 | 1 | 0 | 8 | 0.01 | 54 |  | 56 | 0.013 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1971 | 40 | 192.4 | 42 | 115.2 | 3717.6 | 15.4 | 1.6 | 58.7 | 1.1 | 0.4 | 7 | 0.01 | 50 |  | 53 | 0.01 | The test results are assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1971 | 40 | 483.1 | 65 | 409.2 | 4288.5 | 9.9 | 3.5 | 59.1 | 1.4 | 0 | 13 | 0.011 | 35 |  | 42.7593 | 0.014839 | The test results are assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1971 | 40 | 454.2 | 65 | 384.8 | 4219.2 | 7.5 | 2.8 | 58 | 1.1 | 0 | 18 | 0.011 | 35 |  | 42 | 0.013 | The test results are consistent with main tank sample and is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1971 | 40 | 343.7 | 51 | 279.5 | 2969 | 12 | 2.1 | 49.4 | 0.7 | 0 | 15 | 0.014 | 47 |  | 24 | 0.023 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1971 | 40 | 287 | 30 | 223.6 | 2279.1 | 20.2 | 1.5 | 41.5 | 0.2 | 0 | 14 | 0.0166 | 68 |  | 22 | 0.025 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1971 | 40 | 335.2 | 31 | 260.7 | 2485.7 | 4.9 | 1.6 | 67.1 | 0.4 | 0.5 | 11 | 0.024 | 67 |  | 19 | 0.03 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1971 | 40 | 324.4 | 41 | 244.6 | 1931.4 | 13.2 | 1.8 | 63.9 | 0.3 | 0.6 | 11 | 0.028 | 75 |  | 13 | 0.038 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable. Corrosive IEC. Non-corrosive ASTM 3B.
33000 | 1971 | 40 | 284 | 40 | 209.6 | 1746.4 | 4.4 | 1.8 | 67.2 | 0.2 | 0.8 | 12 | 0.032 | 50 |  | 15 | 0.031 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1971 | 40 | 279.4 | 51 | 203.8 | 1769.2 | 4.7 | 1.3 | 68.2 | 0.5 | 0.9 | 12 | 0.029 | 59 |  | 17 | 0.028 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1971 | 40 | 88.9 | 35 | 47.2 | 720.8 | 23.2 | 5.3 | 13.2 | 0 | 0 | 14 | 0.037 | 29 |  | 12 | 0.032 | DGA is assessed as acceptable. | Breakdown voltage is low. Other oil quality results are assessed as acceptable.
33000 | 1971 | 40 | 51.5 | 35 | 30.3 | 509.8 | 9.3 | 0.5 | 11.4 | 0 | 0 | 11 | 0.051 | 32 |  | 12 | 0.033 | DGA is assessed as acceptable. | Breakdown voltage is low. Other oil quality results are assessed as acceptable.
33000 | 1971 | 40 | 332 | 41.81 | 311 | 2048 | 12 | 2 | 6 | 1 | 0 | 14 | 0.036 | 47 |  | 16.5 | 0.016 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1971 | 40 | 499.8 | 64 | 470.1 | 2668.7 | 19.2 | 3.9 | 4.6 | 1.8 | 0.2 | 13 | 0.045 | 75 |  | 6 | 0.041 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1971 | 40 | 1025.9 | 64 | 954.4 | 8010.9 | 53.3 | 9 | 6.7 | 2.5 | 0 | 22 | 0.058 | 50 |  | 5.6581 | 0.0495 | Carbon oxide levels are high and trending upwards. | Other test results are assessed as acceptable.
33000 | 1971 | 40 | 409.3 | 63 | 389.2 | 3675.2 | 12.2 | 3.4 | 3 | 1.5 | 0 | 19 | 0.047 | 60 |  | 6 | 0.04 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1971 | 40 | 14 | 40 | 13 | 251 | 0 | 0 | 1 | 0 | 0 | 12 | 0.024 | 49 |  | 30.3 | 0.01 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1971 | 40 | 109 | 60 | 103 | 1354 | 0 | 1 | 4 | 0 | 1 | 17 | 0.028 | 50 |  | 25.1 | 0.013 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1971 | 40 | 253 | 54 | 206 | 1604 | 31 | 10 | 5 | 1 | 0 | 22 | 0.029 | 55 |  | 17.2 | 0.021 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1971 | 40 | 226 | 41.81 | 213 | 2349 | 6 | 2 | 4 | 1 | 0 | 18 | 0.037 | 57 |  | 19 | 0.016 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1971 | 40 | 292.4 | 56 | 272.5 | 2032.6 | 13.3 | 2.6 | 2.5 | 0.9 | 0.6 | 14 | 0.045 | 75 |  | 10 | 0.026 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1971 | 40 | 320.5 | 35 | 299.7 | 3456.1 | 14.3 | 3 | 2.4 | 1.1 | 0 | 14 | 0.053 | 54 |  | 8 | 0.028 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1971 | 40 | 436.1 | 56 | 413.7 | 4299.2 | 16.7 | 3.5 | 2.2 | 0 | 0 | 21 | 0.06 | 51 |  | 8 | 0.032 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1971 | 40 | 167 | 41.81 | 135 | 1888 | 12 | 4 | 9 | 7 | 0 | 20 | 0.027 | 52 |  | 23.1 | 0.014 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1971 | 40 | 346.1 | 64 | 314.5 | 2587.8 | 16.9 | 5.1 | 5.4 | 4.2 | 0 | 18 | 0.028 | 62 |  | 10 | 0.027 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1971 | 40 | 830.6 | 63 | 757.8 | 7962.9 | 54.5 | 8.8 | 6.3 | 3.1 | 0.1 | 47 | 0.038 | 21 |  | 14.6393 | 0.020548 | Carbon oxide levels are high and trending upwards. | Moisture content of sample is high. Breakdown voltage of sample is low. Other test results are assessed as acceptable.
33000 | 1971 | 40 | 251.4 | 62 | 237.3 | 4000.2 | 7.9 | 2.6 | 2.4 | 1.2 | 0 | 41 | 0.027 | 19 |  | 15 | 0.017 | DGA is assessed as acceptable. | Moisture content is high. Breakdown voltage is low. Other oil quality results are assessed as acceptable.
33000 | 1971 | 40 | 60 | 33 | 56 | 920 | 0 | 1 | 1 | 2 | 0 | 16 | 0.029 | 54 |  | 70 | 0.0082 | Test results satisfactory. | Oil quality is assessed as acceptable.
33000 | 1971 | 40 | 15 | 29 | 13 | 945 | 0 | 1 | 1 | 0 | 0 | 9 | 0.011 | 63 |  | 60 | 0.016 | Test results satisfactory. | Oil quality is assessed as acceptable.
33000 | 1971 | 40 | 374 | 36 | 352 | 2777 | 10 | 4 | 7 | 1 | 0 | 15 | 0.021 | 38 |  | 30.1 | 0.022 | Test results satisfactory. | Oil quality is assessed as acceptable. PCB contaminated oil.
33000 | 1971 | 40 | 136 | 40 | 126 | 1622 | 0 | 2 | 8 | 0 | 0 | 17 | 0.013 | 61 |  | 63.9 | 0.006 | Test results satisfactory. | Oil quality is assessed as acceptable. PCB contaminated oil.
33000 | 1971 | 40 | 165 | 44 | 150 | 2501 | 5 | 2 | 7 | 1 | 0 | 18 | 0.018 | 58 |  | 41 | 0.008 | Test results are assessed as acceptable. | Oil quality is assessed as acceptable. PCB contaminated oil.
33000 | 1971 | 40 | 168.6557 | 40 | 147.8825 | 2222.1757 | 8.866 | 1.7606 | 9.391 | 0.7556 | 0 | 20 | 0.016 | 37 |  | 32 | 0.011 | The test results are assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1971 | 40 | 173.9 | 44 | 157 | 2662 | 9.4 | 1.8 | 5.5 | 0.1 | 0.1 | 42 | 0.024 | 23 |  | 27 | 0.012 | DGA is assessed as acceptable. | Moisture content is high. Breakdown voltage is low. Possible sample contamination. Other oil quality results are assessed as acceptable.
33000 | 1971 | 40 | 155.9 | 43 | 143.5 | 2842.5 | 7.5 | 1.6 | 3.3 | 0 | 0 | 36 | 0.02 | 24 |  | 23 | 0.013 | DGA is assessed as acceptable. | Moisture content is high. Breakdown voltage is low. Other oil quality results are assessed as acceptable.
33000 | 1971 | 40 | 145.2 | 44 | 133.4 | 2134.3 | 7.5 | 1.5 | 2.3 | 0.5 | 0 | 21 | 0.021 | 58 |  | 20 | 0.013 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1971 | 40 | 47 | 42 | 44 | 799 | 0 | 1 | 1 | 1 | 0 | 12 | 0.031 | 61 |  | 45 | 0.0097 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1971 | 40 | 26 | 28 | 15 | 816 | 6 | 2 | 1 | 2 | 0 | 7 | 0.033 | 63 |  | 30 | 0.014 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1971 | 40 | 176 | 35 | 172 | 1322 | 0 | 2 | 1 | 1 | 0 | 11 | 0.03 | 61 |  | 24.8 | 0.014 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1971 | 40 | 233 | 38 | 212 | 2158 | 14 | 4 | 2 | 1 | 0 | 13 | 0.036 | 53 |  | 17.6 | 0.014 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1971 | 40 | 291 | 56 | 277 | 2332 | 9 | 2 | 2 | 1 | 0 | 13 | 0.036 | 59 |  | 13.7 | 0.021 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1971 | 40 | 315 | 40 | 297 | 2544 | 14 | 2 | 1 | 1 | 0 | 14 | 0.038 | 74 |  | 17 | 0.018 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1971 | 40 | 690.6 | 55 | 627 | 4929.9 | 51 | 4.4 | 6 | 2.1 | 0.1 | 25 | 0.049 | 43 |  | 7.5625 | 0.039886 | 2-furfural and carbon oxide levels are trending upwards suggesting accelerated rate of insulation degradation. Other test results are assessed as acceptable. RECOMMEND RESAMPLE IN 1 YEAR TO MONITOR TREND.
33000 | 1971 | 40 | 508.9 | 38 | 480.3 | 3990.7 | 20.8 | 3.8 | 2.6 | 1.3 | 0.1 | 18 | 0.048 | 51 |  | 7 | 0.038 | The test results are relatively stable and are assessed as acceptable.
33000 | 1971 | 40 | 81 | 28 | 76 | 867 | 0 | 1 | 2 | 0 | 2 | 11 | 0.024 | 58 |  | 25 | 0.014 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1971 | 40 | 272 | 56 | 239 | 1770 | 20 | 3 | 9 | 1 | 0 | 20 | 0.033 | 59 |  | 16.3 | 0.025 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1971 | 40 | 224 | 60 | 208 | 2224 | 0 | 1 | 15 | 0 | 0 | 14 | 0.034 | 72 |  | 15 | 0.022 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1971 | 40 | 135.1 | 40 | 117.5 | 1342.1 | 3.8 | 0.7 | 12.4 | 0.4 | 0.3 | 8 | 0.028 | 73 |  | 12 | 0.022 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1971 | 40 | 189 | 26 | 162.2 | 1672.5 | 2.4 | 4.6 | 12.2 | 0 | 7.6 | 14 | 0.029 | 72 |  | 10.1 | 0.033 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1971 | 40 | 170.4 | 42 | 142.4 | 1515.5 | 11.2 | 1.8 | 10 | 0.2 | 4.8 | 10 | 0.03 | 75 |  | 12 | 0.022 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1971 | 40 | 120.1 | 38 | 107.6 | 1237.9 | 2.7 | 1.2 | 8.3 | 0.2 | 0.1 | 10 | 0.029 | 72 |  | 13 | 0.025 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable. Corrosive IEC. Corrosive ASTM 4A.
33000 | 1971 | 40 | 136.2 | 33 | 124.8 | 1714.1 | 1.2 | 0.4 | 9.8 | 0 | 0 | 22 | 0.035 | 32 |  | 10 | 0.028 | DGA is assessed as acceptable. | Breakdown voltage is low. Other oil quality results are assessed as acceptable.
33000 | 1971 | 40 | 152.5 | 50 | 133 | 1441.4 | 7.6 | 1.6 | 9.8 | 0.3 | 0.2 | 15 | 0.031 | 84 |  | 11 | 0.026 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1971 | 40 | 113.8 | 21 | 96.6 | 1342.8 | 7.3 | 1.1 | 8.6 | 0.2 | 0 | 10 | 0.036 | 56 |  | 9 | 0.027 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1971 | 40 | 51 | 44 | 50 | 912 | 0 | 1 | 0 | 0 | 0 | 9 | 0.022 | 60 |  | 70 | 0.0076 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1971 | 40 | 14 | 44 | 12 | 923 | 0 | 1 | 1 | 0 | 0 | 25 | 0.04 | 41 |  | 50 | 0.0074 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1971 | 40 | 191 | 52 | 157 | 1387 | 31 | 2 | 1 | 0 | 0 | 20 | 0.035 | 57 |  | 35.5 | 0.009 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1971 | 40 | 286 | 56 | 264 | 2349 | 18 | 2 | 1 | 1 | 0 | 17 | 0.03 | 54 |  | 11.8 | 0.009 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1971 | 40 | 174.4 | 34 | 160.6 | 2205.6 | 8.8 | 3.2 | 1.2 | 0.6 | 0 | 11 | 0.03 | 68 |  | 12 | 0.019 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1971 | 40 | 292.6 | 54 | 257 | 2084.3 | 31.1 | 2.4 | 1.2 | 0.9 | 0 | 21 | 0.032 | 53 |  | 9.7888 | 0.032901 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1971 | 40 | 200.7 | 42 | 192.7 | 1846.1 | 4.3 | 2 | 0.9 | 0.8 | 0 | 14 | 0.029 | 66 |  | 11 | 0.023 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1971 | 40 | 122.6 | 48 | 115 | 1541.2 | 5.6 | 1.5 | 0.5 | 0 | 0 | 13 | 0.032 | 75 |  | 9 | 0.029 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1971 | 40 | 181.7 | 37 | 168.6 | 1736.6 | 10.3 | 1.7 | 0.6 | 0.5 | 0 | 14 | 0.035 | 50 |  | 10 | 0.027 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1971 | 40 | 135.5 | 53 | 132 | 2078.1 | 1.9 | 0.4 | 0.8 | 0.4 | 0 | 17 | 0.039 | 69 |  | 11 | 0.022 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable. Corrosive IEC. Non-corrosive ASTM 3B.
33000 | 1971 | 40 | 171.3 | 54 | 156.8 | 1837.4 | 11.8 | 1.9 | 0.8 | 0 | 0 | 18 | 0.034 | 66 |  | 10 | 0.024 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1970 | 41 | 723.4 | 59 | 197.7 | 1492.7 | 38.1 | 40.3 | 241.5 | 33 | 172.8 | 14 | 0.022 | 61 |  | 14 | 0.025 | Dissolved gas analysis suggests high temperature oil overheating has occurred. Acetylene gas possibly from tapchanger. Other test results are assessed as acceptable. RECOMMEND RESAMPLE IN 1 YEAR TO MONITOR TREND.
33000 | 1970 | 41 | 370.6 | 72 | 160 | 2577 | 35.8 | 10 | 34.9 | 1.5 | 128.4 | 32 | 0.023 | 38 |  | 15 | 0.022 | DGA is assessed as acceptable. | Breakdown voltage is low. Other oil quality results are assessed as acceptable.
33000 | 1970 | 41 | 502 | 44 | 86 | 708 | 116 | 16 | 34 | 1 | 249 | 16 | 0.057 | 70 |  | 10 | 0.028 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1970 | 41 | 657 | 36 | 122 | 971 | 156 | 20 | 43 | 1 | 315 | 10 | 0.047 | 67 |  | 5 | 0.047 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1970 | 41 | 671 | 52 | 215 | 1375 | 90 | 19 | 49 | 1 | 297 | 23 | 0.071 | 56 |  | 6.9 | 0.038 | DGA is assessed as acceptable. Acetylene gas possibly communicating from tapchanger. | Oil quality is assessed as acceptable.
33000 | 1970 | 41 | 6 | 41.81 | 0 | 87 | 0 | 1 | 1 | 0 | 4 | 25 | 0.01 | 62 |  | 63.8 | 0.006 | DGA is assessed as acceptable. | Moisture content of oil slightly high after oil change. Possibly sample contamination.
33000 | 1970 | 41 | 349 | 37 | 67 | 991 | 88 | 15 | 16 | 1 | 162 | 17 | 0.01 | 62 |  | 24.3 | 0.01 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1970 | 41 | 609 | 48 | 91 | 1238 | 119 | 25 | 36 | 1 | 337 | 17 | 0.018 | 52 |  | 25.3 | 0.011 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1970 | 41 | 914 | 44 | 165.1 | 1578.8 | 189.2 | 42.1 | 84.1 | 0.9 | 432.6 | 12 | 0.01 | 75 |  | 20 | 0.014 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1970 | 41 | 490.2 | 35 | 217.4 | 1974.3 | 72.3 | 15.3 | 37.5 | 6 | 141.7 | 16 | 0.01 | 57 |  | 11 | 0.033 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1970 | 41 | 971.1 | 42 | 233.6 | 2429.9 | 264.9 | 38.3 | 67 | 1.1 | 366.2 | 15 | 0.011 | 51 |  | 16 | 0.017 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1970 | 41 | 653 | 52 | 253.2 | 2743.5 | 95.8 | 22.5 | 60.8 | 2.2 | 218.5 | 22 | 0.014 | 46 |  | 19 | 0.015 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1970 | 41 | 525.6 | 42 | 181.3 | 2227.4 | 90.9 | 20.5 | 42.5 | 1.8 | 188.6 | 17 | 0.01 | 55 |  | 20 | 0.013 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable. Corrosive IEC. Corrosive ASTM 4A.
33000 | 1970 | 41 | 340 | 32 | 115 | 1119 | 28 | 11 | 30 | 1 | 155 | 8 | 0.044 | 69 |  | 7 | 0.035 | DGA is assessed as acceptable | Oil quality is assessed as acceptable.
33000 | 1970 | 41 | 723 | 34 | 204 | 1346 | 169 | 24 | 46 | 2 | 278 | 16 | 0.057 | 46 |  | 7.6 | 0.031 | DGA is assessed as acceptable. Acetylene gas possibly communicating from tapchanger. | Oil quality is assessed as acceptable.
33000 | 1970 | 41 | 317 | 32 | 137 | 792 | 59 | 9 | 23 | 0 | 89 | 17 | 0.013 | 57 |  | 29.5 | 0.015 | DGA is assessed as acceptable | Oil quality is assessed as acceptable.
33000 | 1970 | 41 | 433 | 41.81 | 75 | 1155 | 65 | 7 | 25 | 2 | 259 | 37 | 0.02 | 25 |  | 36.6 | 0.009 | Test results are assessed as acceptable. Acetylene gas possibly from tapchanger. | Moisture content of oil is high; dielectric strength slightly low; possibly sample contamination.
33000 | 1970 | 41 | 685.4 | 48 | 344.3 | 2319.9 | 101.2 | 19.2 | 52.8 | 6 | 161.9 | 20 | 0.022 | 54 |  | 12 | 0.025 | DGA is assessed as acceptable. | Other test results are assessed as acceptable.
33000 | 1970 | 41 | 688.9 | 50 | 490.6 | 4263.1 | 57.8 | 12.2 | 43.7 | 4.9 | 79.7 | 23 | 0.026 | 54 |  | 19 | 0.015 | DGA is assessed as acceptable. | Other test results are assessed as acceptable.
33000 | 1970 | 41 | 640.2 | 50 | 447.2 | 4130.5 | 55.3 | 11.7 | 42.2 | 4.9 | 78.9 | 19 | 0.026 | 40 |  | 24 | 0.013 | The test results are consistent with the main tank sample and are assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1970 | 41 | 554.5 | 41.81 | 355.7 | 3879.5 | 48.2 | 12.5 | 36.5 | 3.2 | 98.4 | 28 | 0.026 | 36 |  | 12 | 0.028 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1970 | 41 | 246 | 38 | 71 | 716 | 22 | 9 | 23 | 1 | 120 | 7 | 0.03 | 69 |  | 10 | 0.036 | DGA is assessed as acceptable | Oil quality is assessed as acceptable.
33000 | 1970 | 41 | 702 | 36 | 142 | 959 | 189 | 27 | 44 | 1 | 299 | 9 | 0.038 | 54 |  | 12.4 | 0.022 | Test results satisfactory. Acetylene gas possibly from tapchanger. | Oil quality is assessed as acceptable.
33000 | 1970 | 41 | 316 | 28 | 141 | 764 | 62 | 8 | 21 | 0 | 84 | 14 | 0.016 | 52 |  | 29.4 | 0.017 | Test results satisfactory. | Oil quality is assessed as acceptable.
33000 | 1970 | 41 | 568 | 41.81 | 194 | 1439 | 122 | 18 | 40 | 1 | 193 | 20 | 0.014 | 47 |  | 41 | 0.01 | Test results are assessed as acceptable. Acetylene gas possibly from tapchanger. | Oil quality is assessed as acceptable.
33000 | 1970 | 41 | 542.8 | 67 | 231.6 | 1523.9 | 90.7 | 16.2 | 48.3 | 4.9 | 151.1 | 14 | 0.016 | 57 |  | 16 | 0.02 | The test results are assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1970 | 41 | 403.6 | 59 | 290.9 | 2977.9 | 19.6 | 7.2 | 30.3 | 2.2 | 53.4 | 20 | 0.018 | 54 |  | 17 | 0.021 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1970 | 41 | 766 | 40 | 106 | 1020 | 175 | 28 | 55 | 2 | 400 | 14 | 0.055 | 65 |  | 12 | 0.024 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1970 | 41 | 793 | 36 | 123 | 1346 | 222 | 23 | 51 | 2 | 372 | 10 | 0.058 | 67 |  | 7 | 0.035 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1970 | 41 | 1027 | 50 | 155 | 1065 | 266 | 29 | 59 | 1 | 517 | 20 | 0.047 | 50 |  | 8.3 | 0.029 | DGA is assessed as acceptable. Acetylene gas possibly communicating from tapchanger. | Oil quality is assessed as acceptable.
33000 | 1970 | 41 | 681 | 57 | 245 | 1732 | 91 | 17 | 48 | 1 | 279 | 29 | 0.068 | 58 |  | 4.7 | 0.069 | DGA is assessed as acceptable. Acetylene gas possibly communicating from tapchanger. | Oil quality is assessed as acceptable.
33000 | 1970 | 41 | 11 | 41.81 | 3 | 100 | 0 | 1 | 1 | 0 | 6 | 17 | 0.01 | 52 |  | 84 | 0.005 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1970 | 41 | 386 | 38 | 78 | 1055 | 93 | 15 | 17 | 1 | 182 | 16 | 0.01 | 59 |  | 23 | 0.011 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1970 | 41 | 803 | 48 | 134 | 1546 | 170 | 34 | 46 | 2 | 417 | 16 | 0.021 | 67 |  | 21.5 | 0.013 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1970 | 41 | 841.9 | 46 | 187.9 | 1628.9 | 170.5 | 35.3 | 73.2 | 0.6 | 374.4 | 16 | 0.01 | 75 |  | 16 | 0.016 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1970 | 41 | 423 | 37 | 191.1 | 1883.2 | 68 | 13.2 | 31.7 | 0.7 | 118.3 | 16 | 0.012 | 56 |  | 15 | 0.018 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1970 | 41 | 781.1 | 40 | 245.7 | 2436.1 | 200.5 | 25.7 | 48.3 | 0.6 | 260.3 | 17 | 0.013 | 52 |  | 17 | 0.015 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1970 | 41 | 659.1 | 52 | 249.1 | 2670.6 | 101.8 | 21.6 | 53.7 | 2 | 230.9 | 23 | 0.015 | 41 |  | 19 | 0.014 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1970 | 41 | 661.9 | 40 | 180.7 | 2415.5 | 131.3 | 27.4 | 51 | 2.1 | 269.4 | 24 | 0.01 | 54 |  | 17 | 0.018 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable. Corrosive IEC. Corrosive ASTM 4A.
33000 | 1970 | 41 | 2 | 41.81 | 0 | 647 | 0 | 1 | 0 | 1 | 0 | 17 | 0.011 | 83 |  | 140.2 | 0.004 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1970 | 41 | 32.3 | 30 | 26.5 | 818.8 | 4.4 | 1.1 | 0 | 0.3 | 0 | 19 | 0.008 | 62 |  | 69 | 0.005 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1970 | 41 | 21.2 | 23 | 17.5 | 737.8 | 1.8 | 1.7 | 0.2 | 0 | 0 | 13 | 0.009 | 90 |  | 105 | 0.004 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1970 | 41 | 24 | 25 | 20.8 | 743.6 | 1.8 | 0.9 | 0.2 | 0.3 | 0 | 17 | 0.007 | 52 |  | 104 | 0.004 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1970 | 41 | 19912 | 41.81 | 430 | 3338 | 18305 | 1073 | 4 | 100 | 0 | 11 | 0.01 | 65 |  | 92.6 | 0.006 | Dissolved gas analysis suggests partial discharge has occurred. Other test results are assessed as acceptable. RECOMMEND RESAMPLE IN 3 MONTHS TO MONITOR. RECOMMEND INVESTIGATE
33000 | 1970 | 41 | 20249 | 41.81 | 430 | 3030 | 18699 | 1024 | 3 | 93 | 0 | 4 | 0.006 | 53 |  | 93 | 0.007 | Dissolved gas analysis suggests partial discharge has occurred. Gas levels have remained stable. RECOMMEND DEGAS OIL; THEN RESAMPLE. RESAMPLE IN 3 MONTHS TO MONITOR.
33000 | 1970 | 41 | 18520 | 41.81 | 395 | 3049 | 17041 | 989 | 3 | 92 | 0 | 7 | 0.007 | 94 |  | 92.5 | 0.007 | Dissolved gas analysis suggests partial discharge has occurred. RECOMMEND INVESTIGATE.
33000 | 1970 | 41 | 219 | 41.81 | 29 | 860 | 154 | 31 | 1 | 4 | 0 | 9 | 0.004 | 62 |  | 380.1 | 0.002 | Dissolved gas analysis suggests partial discharge has occurred. RECOMMEND INVESTIGATE.
33000 | 1970 | 41 | 34.3 | 30 | 18.1 | 679.4 | 4.4 | 3.6 | 2.1 | 6.1 | 0 | 18 | 0.003 | 71 |  | 53 | 0.011 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1970 | 41 | 18.3 | 24 | 11.1 | 600.1 | 3 | 1.2 | 1.3 | 1.7 | 0 | 11 | 0.002 | 84 |  | 128 | 0.004 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1970 | 41 | 16.3 | 25 | 12.1 | 658.1 | 2.7 | 1 | 0.1 | 0.4 | 0 | 12 | 0.003 | 86 |  | 120 | 0.005 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1970 | 41 | 148 | 32 | 124 | 1261 | 20 | 1 | 3 | 0 | 0 | 8 | 0.072 | 54 |  | 9 | 0.037 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1970 | 41 | 290 | 52 | 249 | 1482 | 36 | 2 | 2 | 1 | 0 | 10 | 0.045 | 59 |  | 17.2 | 0.019 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1970 | 41 | 355 | 41.81 | 321 | 2176 | 19 | 6 | 4 | 4 | 1 | 15 | 0.054 | 56 |  | 6.9 | 0.036 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1970 | 41 | 602.6 | 55 | 568.6 | 3868 | 19.9 | 7.7 | 4.7 | 1.7 | 0 | 10 | 0.088 | 75 |  | 5 | 0.044 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1970 | 41 | 959.9 | 55 | 903.9 | 6309.2 | 41.8 | 5.5 | 6 | 2.7 | 0 | 24 | 0.106 | 28 |  | 4.5598 | 0.05797 | The test results are consistent with main tank sample. | Breakdown voltage is slightly low.
33000 | 1970 | 41 | 1010 | 55 | 945.8 | 6430.3 | 50.2 | 5.3 | 6.2 | 2.5 | 0 | 22 | 0.103 | 53 |  | 4.6713 | 0.05907 | Carbon oxide levels are high suggesting insulation degradation. | Oil quality is assessed as acceptable.
33000 | 1970 | 41 | 500.7 | 49 | 478.6 | 3948.8 | 13.6 | 3.3 | 3.3 | 1.9 | 0 | 19 | 0.09 | 44 |  | 4 | 0.057 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1970 | 41 | 417.2 | 47 | 383.8 | 3509.6 | 23.4 | 3.9 | 3.9 | 2.2 | 0 | 21 | 0.103 | 62 |  | 4 | 0.055 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1970 | 41 | 515.4 | 50 | 474.8 | 3838.8 | 21.1 | 3.7 | 9.6 | 6.2 | 0 | 25 | 0.105 | 48 |  | 4 | 0.056 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1970 | 41 | 387 | 63 | 367.8 | 3885.3 | 11.5 | 3.3 | 2.5 | 1.9 | 0 | 24 | 0.118 | 52 |  | 4 | 0.055 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1970 | 41 | 588.9 | 50 | 4.1 | 579.2 | 16.7 | 10.5 | 60.1 | 8.2 | 489.3 | 20 | 0.006 | 72 |  | 505 | 0.002 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable. Particle contamination load is high.
33000 | 1970 | 41 | 265 | 52 | 250.5 | 3070.1 | 9.2 | 2.4 | 2.9 | 0 | 0 | 20 | 0.121 | 62 |  | 6 | 0.041 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1970 | 41 | 323 | 30 | 283 | 2256 | 36 | 2 | 1 | 1 | 0 | 22 | 0.224 | 38 |  | 4.5 | 0.047 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1970 | 41 | 628 | 45 | 587 | 3987 | 31 | 4 | 5 | 1 | 0 | 23 | 0.269 | 73 |  | 3.9 | 0.058 | Test results satisfactory at present.
33000 | 1970 | 41 | 677 | 48 | 634 | 4713 | 33 | 4 | 5 | 1 | 0 | 23 | 0.276 | 60 |  | 4 | 0.058 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1970 | 41 | 532.7 | 40 | 489.8 | 4448.7 | 31.9 | 3.9 | 5.4 | 1.7 | 0 | 16 | 0.288 | 60 |  | 3 | 0.068 | Acidity is high but stable. Other test results are assessed as acceptable.
33000 | 1970 | 41 | 660.8 | 31 | 613.3 | 6114.5 | 35.6 | 7.7 | 3.7 | 0.5 | 0 | 21 | 0.311 | 75 |  | 3 | 0.064 | DGA is assessed as acceptable. | Acidity level is high. Other oil quality results are assessed as acceptable.
33000 | 1970 | 41 | 431.6 | 43 | 404.3 | 4459.3 | 20 | 3.1 | 3 | 1.2 | 0 | 17 | 0.357 | 71 |  | 3 | 0.065 | DGA is assessed as acceptable. | Acidity level is high. Other oil quality results are assessed as acceptable at present.
33000 | 1970 | 41 | 179.2 | 30 | 172.3 | 2669.4 | 4.1 | 0.5 | 1.6 | 0.7 | 0 | 18 | 0.36 | 50 |  | 3 | 0.068 | Dissolved gas levels are reduced. DGA is assessed as acceptable. | Acidity level is high. Other oil quality results are assessed as acceptable.
33000 | 1970 | 41 | 164.6 | 31 | 160.5 | 2117.6 | 0 | 1.5 | 2 | 0.6 | 0 | 19 | 0.361 | 84 |  | 3 | 0.068 | DGA is assessed as acceptable. | Acidity level is high. Other oil quality results are assessed as acceptable at present.
33000 | 1970 | 41 | 132 | 26 | 124 | 1089 | 0 | 1 | 7 | 0 | 0 | 15 | 0.053 | 62 |  | 15 | 0.029 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1970 | 41 | 137 | 42 | 127 | 1238 | 0 | 1 | 9 | 0 | 0 | 12 | 0.049 | 58 |  | 15 | 0.023 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1970 | 41 | 516 | 50 | 471 | 2403 | 39 | 2 | 3 | 1 | 0 | 24 | 0.061 | 47 |  | 10.4 | 0.031 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1970 | 41 | 800 | 50 | 722 | 4170 | 37 | 12 | 12 | 17 | 0 | 29 | 0.078 | 30 |  | 5 | 0.05 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1970 | 41 | 349.4 | 40 | 326.7 | 3900.6 | 11.7 | 2.4 | 4.9 | 3.7 | 0 | 12 | 0.1 | 73 |  | 5 | 0.056 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1970 | 41 | 586.8 | 57 | 537.4 | 4073.1 | 38.8 | 3.2 | 4.7 | 2.7 | 0 | 34 | 0.11 | 66 |  | 3.9224 | 0.07095 | DGA is assessed as acceptable. | Moisture content of sample is slightly high. Other test results are assessed as acceptable.
33000 | 1970 | 41 | 404.4 | 46 | 390.8 | 3528.5 | 3 | 3.4 | 4.2 | 3 | 0 | 23 | 0.096 | 70 |  | 5 | 0.047 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1970 | 41 | 241.7 | 49 | 229.2 | 2942.1 | 6.2 | 2.7 | 2.8 | 0.8 | 0 | 18 | 0.129 | 68 |  | 2 | 0.1477 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1970 | 41 | 299.2 | 46 | 286.2 | 2860.4 | 7.9 | 2.2 | 2 | 0.9 | 0 | 18 | 0.114 | 78 |  | 4 | 0.058 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1970 | 41 | 250.8 | 62 | 242.1 | 4129.7 | 2.2 | 2 | 4.3 | 0.2 | 0 | 23 | 0.134 | 32 |  | 5 | 0.044 | DGA is assessed as acceptable. | Breakdown voltage is slightly low. Other oil quality results are assessed as acceptable. Non-corrosive IEC. Non-corrosive ASTM 3A.
33000 | 1970 | 41 | 256.6 | 49 | 240.4 | 2877.4 | 13.4 | 1.8 | 1 | 0 | 0 | 18 | 0.117 | 54 |  | 4 | 0.058 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable. Non-corrosive IEC. Non-corrosive ASTM.
33000 | 1970 | 41 | 289.8 | 58 | 279 | 3012.9 | 7.8 | 1.9 | 1.1 | 0 | 0 | 22 | 0.113 | 55 |  | 4 | 0.055 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1970 | 41 | 520 | 41.81 | 183 | 1360 | 58 | 16 | 52 | 2 | 209 | 17 | 0.105 | 69 |  | 7 | 0.036 | DGA is assessed as acceptable. Acetylene gas possibly communicating from tapchanger. | Oil quality is assessed as acceptable.
33000 | 1970 | 41 | 570 | 50 | 262 | 1792 | 61 | 11 | 44 | 1 | 191 | 19 | 0.071 | 53 |  | 6.1 | 0.041 | DGA is assessed as acceptable. Acetylene gas possibly communicating from tapchanger. | Oil quality is assessed as acceptable.
33000 | 1970 | 41 | 798 | 40 | 182 | 1559 | 157 | 31 | 67 | 2 | 359 | 20 | 0.09 | 68 |  | 5 | 0.041 | DGA is assessed as acceptable. Acetylene gas possibly communicating from tapchanger. | Oil quality is assessed as acceptable.
33000 | 1970 | 41 | 958 | 40 | 230 | 2369 | 77 | 25 | 92 | 3 | 531 | 27 | 0.08 | 48 |  | 4.8 | 0.056 | Dissolved gas analysis suggests hot spot in oil. Acetylene gas possibly communicating from tapchanger. | Oil quality is assessed as acceptable.
33000 | 1970 | 41 | 788 | 49 | 179 | 2027 | 82 | 27 | 71 | 2 | 427 | 49 | 0.09 | 23 |  | 5.2 | 0.055 | Gas levels have remained stable. Acetylene gas possibly communicating from tapchanger. | Moisture content of oil is high. Dielectric strength is low possibly sample contamination.
33000 | 1970 | 41 | 505.1 | 50 | 186 | 2080.4 | 43.2 | 10.4 | 47.8 | 5 | 212.7 | 27 | 0.078 | 35 |  | 4.8 | 0.056 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1970 | 41 | 399.6 | 43 | 150.7 | 2086.6 | 28.9 | 13.5 | 38.5 | 0.3 | 167.7 | 43 | 0.071 | 17 |  | 4 | 0.053 | DGA is assessed as acceptable. | Moisture content is high. Breakdown voltage is low. Possible sample contamination. Other oil quality results are assessed as acceptable.
33000 | 1970 | 41 | 390.8 | 41.81 | 160.3 | 1866.7 | 45.8 | 11.7 | 36.1 | 1.4 | 135.5 | 29 | 0.075 | 24 |  | 4 | 0.06 | DGA is assessed as acceptable. | Breakdown voltage is low. Other oil quality results are assessed as acceptable.
33000 | 1970 | 41 | 348.5 | 45 | 176.7 | 2377.2 | 32.2 | 8.3 | 34.4 | 0.8 | 96.1 | 26 | 0.061 | 30 |  | 4 | 0.061 | DGA is assessed as acceptable. | Breakdown voltage is low. Other oil quality results are assessed as acceptable.
33000 | 1970 | 41 | 334.3 | 44 | 163.2 | 3244 | 47.8 | 7.2 | 31.4 | 0.5 | 84.2 | 56 | 0.072 | 13 |  | 4 | 0.076 | DGA is assessed as acceptable. | Breakdown voltage is low. Other oil quality results are assessed as acceptable.
33000 | 1970 | 41 | 358.7 | 42 | 173.6 | 2643 | 28.1 | 8.5 | 30.6 | 1.8 | 116.1 | 30 | 0.059 | 33 |  | 4 | 0.058 | DGA is assessed as acceptable. | Breakdown voltage is low. Other oil quality results are assessed as acceptable.
33000 | 1970 | 41 | 345.9 | 51 | 136.3 | 2343.9 | 39.5 | 9 | 31.6 | 1.8 | 127.7 | 32 | 0.056 | 28 |  | 5 | 0.049 | DGA is assessed as acceptable. | Breakdown voltage is low. Other oil quality results are assessed as acceptable.
33000 | 1970 | 41 | 297.9 | 54 | 137.6 | 2430.1 | 23.6 | 7.3 | 28.5 | 1.1 | 99.8 | 48 | 0.059 | 26 |  | 6 | 0.045 | DGA is assessed as acceptable. | Breakdown voltage is low. Other oil quality results are assessed as acceptable.
33000 | 1970 | 41 | 446 | 41.81 | 141 | 1264 | 71 | 13 | 32 | 1 | 188 | 44 | 0.086 | 29 |  | 6 | 0.042 | DGA is assessed as acceptable. | Moisture level slightly high considering low acidity.
33000 | 1970 | 41 | 232 | 41.81 | 59 | 1892 | 0 | 6 | 34 | 1 | 132 | 11 | 0.088 | 59 |  | 8.1 | 0.035 | Test results satisfactory. Transformer at Northgate for assessment. | Oil quality is assessed as acceptable.
33000 | 1970 | 41 | 729 | 41.81 | 134 | 1472 | 92 | 24 | 67 | 1 | 411 | 14 | 0.018 | 61 |  | 26.4 | 0.018 | Test results are assessed as acceptable. Acetylene gas is possibly from tapchanger. | Oil quality is assessed as acceptable.
33000 | 1970 | 41 | 472 | 63 | 227.5 | 2007.5 | 26.3 | 10.2 | 99.6 | 17.8 | 90.6 | 18 | 0.019 | 44 |  | 14 | 0.023 | Dissolved gas analysis suggests high temperature oil overheating has occurred. | Other test results are assessed as acceptable.
33000 | 1970 | 41 | 421.4 | 62 | 186.6 | 2033.9 | 41 | 10.4 | 51.3 | 9.6 | 122.5 | 26 | 0.023 | 75 |  | 13 | 0.025 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1970 | 41 | 475.4 | 54 | 229.8 | 2271.7 | 46.8 | 11.3 | 40.6 | 0.5 | 146.4 | 25 | 0.024 | 36 |  | 13 | 0.031 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1970 | 41 | 403.8 | 58 | 173 | 2083.3 | 41.7 | 10.5 | 37.7 | 1.4 | 139.5 | 21 | 0.027 | 55 |  | 16 | 0.021 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1970 | 41 | 299.5 | 71 | 138.8 | 1991.9 | 26.9 | 7.3 | 30 | 2.2 | 94.3 | 68 | 0.027 | 14 |  | 16 | 0.021 | DGA is assessed as acceptable. | Breakdown voltage is low. Other oil quality results are assessed as acceptable. Oil is cloudy in appearance.
33000 | 1970 | 41 | 374.7 | 70 | 164.2 | 2082.7 | 39.7 | 10.3 | 33.5 | 1.2 | 125.8 | 30 | 0.029 | 30 |  | 14 | 0.023 | DGA is assessed as acceptable. | Breakdown voltage is slightly low. Other oil quality results are assessed as acceptable.
33000 | 1970 | 41 | 245 | 28 | 114 | 1020 | 30 | 8 | 24 | 2 | 67 | 11 | 0.042 | 70 |  | 6 | 0.06 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1970 | 41 | 682 | 50 | 167 | 1106 | 101 | 27 | 50 | 2 | 335 | 17 | 0.058 | 67 |  | 9.8 | 0.02 | Acetylene gas level very high. Possibly from tapchanger? | Oil quality is assessed as acceptable.
33000 | 1970 | 41 | 665 | 41.81 | 152 | 2096 | 91 | 22 | 59 | 2 | 339 | 22 | 0.063 | 48 |  | 8.5 | 0.032 | Test results are assessed as acceptable. Acetylene gas possibly from tapchanger. | Oil quality is assessed as acceptable.
33000 | 1970 | 41 | 543.8 | 60 | 294.9 | 2772.4 | 29.7 | 11 | 47.4 | 1.1 | 159.7 | 26 | 0.064 | 31 |  | 9 | 0.026 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1970 | 41 | 556.2 | 60 | 322.3 | 3988 | 50.6 | 13.7 | 41.8 | 6.3 | 121.5 | 36 | 0.065 | 24 |  | 6 | 0.043 | DGA is assessed as acceptable. | Moisture content of sample is high. Breakdown voltage of sample is low. Other test results are assessed as acceptable.
33000 | 1970 | 41 | 643.5 | 56 | 356.2 | 4212.4 | 57.5 | 15 | 44.3 | 6.7 | 163.8 | 48 | 0.062 | 19 |  | 8 | 0.033 | DGA is assessed as acceptable. | Moisture content is high. Breakdown voltage is low. Other oil quality results are assessed as acceptable.
33000 | 1970 | 41 | 814.3 | 58 | 547 | 7194.4 | 49.2 | 12.2 | 48.1 | 1 | 156.8 | 56 | 0.068 | 16 |  | 6 | 0.035 | DGA is assessed as acceptable. | Moisture content is high. Breakdown voltage is low. Other oil quality results are assessed as acceptable.
33000 | 1970 | 41 | 554.4 | 49 | 259.1 | 3726.6 | 65.6 | 15 | 43.6 | 0.7 | 170.4 | 21 | 0.067 | 38 |  | 6 | 0.039 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1970 | 41 | 450.8 | 51 | 228.1 | 4276.2 | 55.8 | 11.4 | 32.1 | 1.6 | 121.8 | 21 | 0.071 | 52 |  | 6 | 0.041 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1970 | 41 | 376.4 | 44 | 192.7 | 3016.9 | 31 | 9.3 | 29 | 2.4 | 112 | 18 | 0.072 | 73 |  | 7 | 0.04 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable. Corrosive IEC. Corrosive ASTM 4A.
33000 | 1970 | 41 | 375.6 | 64 | 192.1 | 3317.9 | 45.6 | 22 | 20.3 | 3 | 92.6 | 46 | 0.071 | 15 |  | 7 | 0.038 | DGA is assessed as acceptable. | Breakdown voltage is low. Other oil quality results are assessed as acceptable. Oil is cloudy in appearance.
33000 | 1970 | 41 | 467.7 | 60 | 253.9 | 3421.3 | 58.5 | 11.1 | 23.5 | 1.4 | 119.3 | 32 | 0.076 | 29 |  | 6 | 0.042 | DGA is assessed as acceptable. | Breakdown voltage is low. Other oil quality results are assessed as acceptable.
33000 | 1970 | 41 | 388.3 | 65 | 169.8 | 2228.5 | 46 | 10.7 | 23.7 | 0.8 | 137.3 | 61 | 0.059 | 20 |  | 8 | 0.028 | DGA is assessed as acceptable. | Breakdown voltage is low. Other oil quality results are assessed as acceptable.
33000 | 1970 | 41 | 278.9 | 46 | 111.2 | 2895.6 | 27 | 7 | 20.8 | 2.2 | 110.7 | 58 | 0.06 | 18 |  | 10 | 0.025 | DGA is assessed as acceptable. | Breakdown voltage is low. Other oil quality results are assessed as acceptable.
33000 | 1969 | 42 | 14 | 41.81 | 13 | 730 | 0 | 1 | 0 | 0 | 0 | 19 | 0.028 | 55 |  | 16.5 | 0.022 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1969 | 42 | 552 | 32 | 440 | 3112 | 100 | 5 | 4 | 3 | 0 | 25 | 0.167 | 57 |  | 8 | 0.0274 | Test results satisfactory.
33000 | 1969 | 42 | 348 | 52 | 319 | 2854 | 22 | 2 | 4 | 1 | 0 | 22 | 0.194 | 62 |  | 6.1 | 0.037 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1969 | 42 | 479 | 42 | 445 | 3775 | 21 | 3 | 9 | 1 | 0 | 30 | 0.169 | 45 |  | 3.3 | 0.062 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1969 | 42 | 555 | 58 | 515 | 3875 | 31 | 3 | 5 | 1 | 0 | 37 | 0.154 | 54 |  | 5.5 | 0.041 | Moisture level slightly high. Possibly sample contamination.
33000 | 1969 | 42 | 464 | 60 | 426 | 3637 | 31 | 2 | 4 | 1 | 0 | 35 | 0.16 | 26 |  | 5 | 0.038 | Moisture content of oil is slightly high. Dielectric strength slightly low. Other test results are assessed as acceptable.
33000 | 1969 | 42 | 855.1 | 60 | 746.5 | 8370 | 80.5 | 12.3 | 12.1 | 3.7 | 0 | 36 | 0.195 | 21 |  | 4 | 0.06 | 2-furfural level is trending upwards suggesting accelerated rate of insulation degradation. Dissolved gas analysis is assessed as acceptable. Oil quality is poor. RECOMMEND RESAMPLE IN 1 YEAR TO MONITOR CONDITION.
33000 | 1969 | 42 | 1411.5 | 66 | 1185.4 | 11718.7 | 160.4 | 35.1 | 19 | 11.6 | 0 | 50 | 0.245 | 20 |  | 3.7613 | 0.0638 | 2-furfural and carbon oxide levels are high and trending upwards suggesting advanced state of insulation degradation. Moisture content of sample is high. Acidity level of sample is high. Breakdown voltage of sample is low. RECOMMEND OIL CHANGE / TREAT
33000 | 1969 | 42 | 480 | 34 | 328 | 2083 | 148 | 2 | 1 | 1 | 0 | 50 | 0.13 | 25 |  | 11 | 0.0225 | DGA is assessed as acceptable. | Breakdown strength low. Moisture content high.
33000 | 1969 | 42 | 323 | 54 | 292 | 2446 | 25 | 3 | 2 | 1 | 0 | 43 | 0.133 | 23 |  | 8.7 | 0.025 | DGA is assessed as acceptable. | Moisture level high; breakdown low other test results satisfactory.
33000 | 1969 | 42 | 569 | 52 | 510 | 5065 | 51 | 3 | 4 | 1 | 0 | 43 | 0.157 | 64 |  | 8.2 | 0.028 | DGA is assessed as acceptable. | Moisture content of oil is high. Other test results are assessed as acceptable.
33000 | 1969 | 42 | 677 | 44 | 611 | 5822 | 57 | 4 | 4 | 1 | 0 | 23 | 0.167 | 46 |  | 7 | 0.029 | Test results are assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1969 | 42 | 616.9 | 40 | 538.8 | 9609.5 | 60.6 | 4.3 | 11 | 2.2 | 0 | 51 | 0.171 | 26 |  | 3 | 0.062 | DGA is assessed as acceptable. | Moisture content of sample is high. Breakdown voltage of sample is low. Possible sample contamination.
33000 | 1969 | 42 | 1370.9 | 44 | 1131.3 | 11996.3 | 187.9 | 23.4 | 15.3 | 13 | 0 | 51 | 0.213 | 18 |  | 5 | 0.051 | Dissolved gas analysis is assessed as acceptable. | Moisture content of sample is high. Breakdown voltage of sample is low. Acidity level of sample is high.
33000 | 1969 | 42 | 864 | 48 | 744.4 | 7216.7 | 97.2 | 7.6 | 8.2 | 6.6 | 0 | 62 | 0.186 | 26 |  | 4 | 0.058 | DGA is assessed as acceptable. | Breakdown voltage is low. Moisture content is very high.
33000 | 1969 | 42 | 777.1 | 40 | 663.1 | 5457.1 | 96.9 | 6.4 | 7.2 | 3.5 | 0 | 28 | 0.223 | 35 |  | 5 | 0.043 | DGA is assessed as acceptable. | Acidity level is high. Other oil quality results are assessed as acceptable.
33000 | 1969 | 42 | 155 | 48 | 152 | 1849 | 0 | 0 | 2 | 1 | 0 | 21 | 0.166 | 46 |  | 7 | 0.0397 | Test results satisfactory. | Oil quality is assessed as acceptable.
33000 | 1969 | 42 | 271 | 50 | 266 | 2421 | 0 | 2 | 2 | 1 | 0 | 25 | 0.191 | 73 |  | 6.5 | 0.037 | Test results satisfactory. | Oil quality is assessed as acceptable. PCB contaminated oil.
33000 | 1969 | 42 | 78 | 50 | 76 | 1540 | 0 | 1 | 1 | 0 | 0 | 23 | 0.167 | 61 |  | 6.4 | 0.045 | Test results satisfactory. | Oil quality is assessed as acceptable.
33000 | 1969 | 42 | 196 | 41.81 | 186 | 2196 | 5 | 2 | 2 | 1 | 0 | 25 | 0.175 | 41 |  | 5.7 | 0.045 | Test results are assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1969 | 42 | 265.8 | 50 | 246.1 | 2986.9 | 12.5 | 2.2 | 3.5 | 1.5 | 0 | 30 | 0.204 | 28 |  | 4 | 0.055 | DGA is assessed as acceptable. | Oil quality is poor.
33000 | 1969 | 42 | 206.3 | 45 | 193 | 3174.9 | 7.2 | 4.8 | 1.3 | 0 | 0 | 20 | 0.238 | 46 |  | 4.7 | 0.054 | DGA is assessed as acceptable. | Acidity level is high. Other oil quality results are assessed as acceptable.
33000 | 1969 | 42 | 308.6 | 39 | 284.1 | 3999.3 | 18 | 2.5 | 3 | 1 | 0 | 22 | 0.255 | 75 |  | 4 | 0.05 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1969 | 42 | 139.8 | 43 | 129.9 | 2294 | 0 | 1.8 | 6.1 | 2 | 0 | 24 | 0.246 | 58 |  | 4 | 0.052 | DGA is assessed as acceptable. | Acidity is high but stable. Other oil quality results are assessed as acceptable.
33000 | 1969 | 42 | 192.2 | 48 | 183.2 | 3297.3 | 4.6 | 1.8 | 2.1 | 0.5 | 0 | 26 | 0.297 | 49 |  | 5 | 0.05 | DGA is assessed as acceptable. | Acidity level is high. Other oil quality results are assessed as acceptable.
33000 | 1969 | 42 | 171.1 | 43 | 161.7 | 2979.5 | 4.6 | 1.7 | 2.5 | 0.6 | 0 | 26 | 0.275 | 39 |  | 4 | 0.048 | DGA is assessed as acceptable. | Acidity level is high. Breakdown voltage is low. Other oil quality results are assessed as acceptable.
33000 | 1969 | 42 | 203 | 64 | 185 | 2595 | 11 | 2 | 4 | 1 | 0 | 55 | 0.218 | 28 |  | 7 | 0.049 | Moisture content of sample quite high. Dielectric strength of sample low.
33000 | 1969 | 42 | 330 | 50 | 320 | 2718 | 5 | 2 | 2 | 1 | 0 | 23 | 0.184 | 63 |  | 6 | 0.04 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1969 | 42 | 120 | 50 | 117 | 1915 | 0 | 2 | 1 | 0 | 0 | 21 | 0.173 | 62 |  | 6.2 | 0.045 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1969 | 42 | 176 | 28 | 157 | 2401 | 5 | 2 | 11 | 1 | 0 | 34 | 0.19 | 40 |  | 6.1 | 0.033 | Moisture content of oil slightly high. Other test results are assessed as acceptable.
33000 | 1969 | 42 | 169.3 | 48 | 156.5 | 2843.5 | 5.8 | 1.7 | 3.1 | 1.4 | 0.8 | 21 | 0.2 | 36 |  | 4 | 0.053 | DGA is assessed as acceptable. | Acidity level is high. Other oil quality results are assessed as acceptable.
33000 | 1969 | 42 | 205 | 34 | 197.6 | 3022.6 | 0 | 2.6 | 3.4 | 1.4 | 0 | 19 | 0.246 | 61 |  | 4 | 0.057 | DGA is assessed as acceptable. | Acidity level is high. Other oil quality results are assessed as acceptable.
33000 | 1969 | 42 | 336.4 | 34 | 313.8 | 3984.7 | 13.5 | 3.4 | 4.1 | 1.6 | 0 | 23 | 0.268 | 75 |  | 4 | 0.062 | DGA is assessed as acceptable. | Acidity level is high. Other oil quality results are assessed as acceptable.
33000 | 1969 | 42 | 120.7 | 42 | 109.9 | 2094.7 | 5.4 | 1.8 | 2.8 | 0.8 | 0 | 22 | 0.232 | 59 |  | 4 | 0.062 | DGA is assessed as acceptable. | Acidity level is high but stable. Other oil quality results are assessed as acceptable.
33000 | 1969 | 42 | 243.9 | 56 | 235.4 | 2829 | 5.8 | 0.2 | 2.4 | 0 | 0.1 | 33 | 0.274 | 65 |  | 4 | 0.054 | DGA is assessed as acceptable. | Acidity level is high. Other oil quality results are assessed as acceptable.
33000 | 1969 | 42 | 186.7 | 44 | 180.1 | 3011 | 2.9 | 1.9 | 1.3 | 0.5 | 0 | 22 | 0.276 | 67 |  | 4 | 0.052 | DGA is assessed as acceptable. | Acidity level is high. Other oil quality results are assessed as acceptable.
33000 | 1969 | 42 | 144.9 | 51 | 136.1 | 2759.7 | 4.3 | 1.8 | 1.9 | 0.7 | 0.1 | 21 | 0.245 | 59 |  | 4 | 0.046 | DGA is assessed as acceptable. | Acidity level is high. Other oil quality results are assessed as acceptable.
33000 | 1969 | 42 | 1062 | 41.81 | 637 | 559 | 92 | 113 | 53 | 156 | 11 | 16 | 0.106 | 50 |  | 1.3 | 0.343 | DGA is assessed as acceptable. | Dielectric Dissipation Factor (DDF) and Resistivity are outside acceptance limits.
33000 | 1969 | 42 | 559 | 35 | 488 | 5707 | 9 | 3 | 58 | 1 | 0 | 17 | 0.172 | 46 |  | 2 | 0.335 | DGA is assessed as acceptable. | Dielectric Dissipation Factor (DDF) is outside acceptance limits.
33000 | 1969 | 42 | 1136 | 38 | 801 | 3631 | 67 | 56 | 58 | 132 | 22 | 21 | 0.237 | 59 |  | 0.7 | 0.621 | DGA is assessed as acceptable. | Oil quality poor. Similar to HTN TR 2.
33000 | 1969 | 42 | 1867 | 40 | 1175 | 4417 | 126 | 153 | 108 | 207 | 98 | 33 | 0.273 | 56 |  | 0.587 | 0.709 | DGA is assessed as acceptable. | Oil quality is poor.
33000 | 1969 | 42 | 482 | 36 | 362 | 2115 | 32 | 9 | 43 | 11 | 25 | 15 | 0.08 | 60 |  | 13.1 | 0.063 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1969 | 42 | 512 | 34 | 375 | 2383 | 33 | 10 | 53 | 11 | 30 | 21 | 0.037 | 51 |  | 5.8 | 0.08 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1969 | 42 | 521 | 44 | 380 | 4349 | 35 | 7 | 67 | 7 | 25 | 25 | 0.043 | 75 |  | 8.7 | 0.077 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1969 | 42 | 663 | 57 | 529 | 6162 | 21 | 7 | 75 | 3 | 28 | 29 | 0.059 | 54 |  | 7.8 | 0.081 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1969 | 42 | 796 | 48 | 650 | 9093.1 | 15.4 | 5.2 | 87.4 | 4.7 | 33.3 | 23 | 0.07 | 53 |  | 6 | 0.066 | DGA is acceptable at present. | Oil quality is assessed as acceptable.
33000 | 1969 | 42 | 695.3 | 55 | 615.2 | 5847.6 | 19.3 | 5.2 | 44.4 | 1.9 | 9.3 | 32 | 0.071 | 25 |  | 7 | 0.043 | DGA is assessed as acceptable. | Moisture content is high. Breakdown voltage is low. Possible sample contamination.
33000 | 1969 | 42 | 690.7 | 58 | 603.7 | 6213.4 | 15.5 | 5.4 | 46.6 | 0.5 | 19 | 34 | 0.088 | 34 |  | 6 | 0.043 | DGA is assessed as acceptable. | Moisture content is high. Other oil quality results are assessed as acceptable.
33000 | 1969 | 42 | 525.1 | 56 | 444.9 | 4400.6 | 9.9 | 5 | 39.4 | 1 | 24.9 | 37 | 0.087 | 32 |  | 9 | 0.037 | DGA is assessed as acceptable. | Breakdown voltage is low. Other oil quality results are assessed as acceptable.
33000 | 1969 | 42 | 566.7 | 57 | 445.1 | 4742.8 | 15.5 | 6.7 | 49.2 | 2.1 | 48.1 | 60 | 0.097 | 22 |  | 10 | 0.03 | DGA is assessed as acceptable. | Breakdown voltage is low. Other oil quality results are assessed as acceptable.
33000 | 1969 | 42 | 510.4 | 40 | 396.1 | 4647.1 | 11.2 | 5.5 | 47.8 | 1.3 | 48.5 | 25 | 0.114 | 52 |  | 7 | 0.043 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1969 | 42 | 557.9 | 58 | 431.4 | 4549.2 | 14.8 | 6.6 | 48.8 | 1.7 | 54.6 | 35 | 0.108 | 27.5 |  | 7 | 0.039 | DGA is assessed as acceptable. | Breakdown voltage is low. Other oil quality results are assessed as acceptable.
33000 | 1969 | 42 | 578.6 | 52 | 477.3 | 4480.9 | 12.4 | 5.5 | 46.3 | 1.9 | 35.2 | 32 | 0.104 | 28 |  | 9 | 0.03 | DGA is assessed as acceptable. | Breakdown voltage is low. Other oil quality results are assessed as acceptable.
33000 | 1969 | 42 | 1255 | 33 | 878 | 3493 | 70 | 129 | 43 | 134 | 1 | 17 | 0.098 | 57 |  | 2 | 0.3 | D.G.A. Suggests slight overheating taking place. | Oil quality is assessed as acceptable.
33000 | 1969 | 42 | 1486 | 33 | 1091 | 3927 | 92 | 129 | 42 | 128 | 4 | 18 | 0.228 | 63 |  | 1.2 | 0.335 | Gas levels stable. | Acidity level is high. Dielectric Dissipation Factor (DDF) and Resistivity are outside acceptance limits.
33000 | 1969 | 42 | 1416 | 38 | 1032 | 3409 | 105 | 116 | 37 | 110 | 16 | 20 | 0.222 | 47 |  | 1.4 | 0.305 | Gas levels stable. | Oil quality is poor.
33000 | 1969 | 42 | 1013 | 45 | 694 | 3117 | 109 | 82 | 30 | 88 | 10 | 26 | 0.25 | 38 |  | 1.2 | 0.374 | Dissolved gas levels are relatively stable. | Oil quality is poor.
33000 | 1969 | 42 | 975 | 36 | 746 | 2547 | 109 | 21 | 23 | 63 | 13 | 23 | 0.268 | 40 |  | 1.1 | 0.387 | DGA is assessed as acceptable. | Oil quality is poor.
33000 | 1969 | 42 | 1793 | 43 | 1235 | 3967 | 202 | 123 | 53 | 103 | 77 | 29 | 0.289 | 64 |  | 1 | 0.389 | DGA is assessed as acceptable. | Oil quality is poor.
33000 | 1969 | 42 | 369 | 34 | 258 | 1554 | 34 | 8 | 30 | 5 | 34 | 15 | 0.07 | 71 |  | 14 | 0.054 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1969 | 42 | 469 | 34 | 322 | 1956 | 41 | 10 | 43 | 5 | 48 | 17 | 0.036 | 46 |  | 8.2 | 0.059 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1969 | 42 | 590 | 40 | 420 | 4445 | 50 | 8 | 69 | 4 | 39 | 22 | 0.046 | 65 |  | 11.4 | 0.053 | Minor increase in Ethylene. | Oil quality is assessed as acceptable.
33000 | 1969 | 42 | 632 | 52 | 498 | 5646 | 24 | 7 | 61 | 3 | 39 | 30 | 0.06 | 46 |  | 9.9 | 0.056 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1969 | 42 | 841 | 49 | 645.3 | 9730.4 | 17.7 | 4.8 | 103.2 | 2.6 | 67.4 | 19 | 0.07 | 46 |  | 5 | 0.061 | DGA is assessed as acceptable at present. | Oil quality is assessed as acceptable.
33000 | 1969 | 42 | 693.3 | 42 | 553.5 | 5353.8 | 31.6 | 7.4 | 69.5 | 2.9 | 28.4 | 36 | 0.078 | 30 |  | 6.4751 | 0.05115 | DGA is assessed as acceptable. | Moisture content is slightly high. Other oil quality results are assessed as acceptable.
33000 | 1969 | 42 | 668.4 | 52 | 589.3 | 5588.8 | 15.3 | 4.5 | 47 | 1.8 | 10.5 | 33 | 0.074 | 28 |  | 6 | 0.053 | DGA is assessed as acceptable. | Moisture content is high. Breakdown voltage is low. Possible sample contamination.
33000 | 1969 | 42 | 695.3 | 55 | 615.3 | 6099 | 12.7 | 4.7 | 47.5 | 1.4 | 13.7 | 31 | 0.091 | 36 |  | 5 | 0.055 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1969 | 42 | 509.8 | 52 | 442.6 | 4127.7 | 7.7 | 4 | 38.2 | 1 | 16.3 | 32 | 0.095 | 35 |  | 6 | 0.052 | DGA is assessed as acceptable. | Breakdown voltage is low. Other oil quality results are assessed as acceptable.
33000 | 1969 | 42 | 506.3 | 56 | 436 | 4278.9 | 8.3 | 3.8 | 44.6 | 0 | 13.6 | 28 | 0.101 | 33 |  | 6 | 0.052 | DGA is assessed as acceptable. | Breakdown voltage is low. Other oil quality results are assessed as acceptable.
33000 | 1969 | 42 | 487.5 | 60 | 411 | 3985.9 | 9.8 | 4.3 | 41.8 | 0 | 20.6 | 30 | 0.111 | 36 |  | 5 | 0.05 | DGA is assessed as acceptable. | Breakdown voltage is low. Other oil quality results are assessed as acceptable.
33000 | 1969 | 42 | 534.3 | 52 | 455.5 | 4204.3 | 8.9 | 4.7 | 43.4 | 0.2 | 21.6 | 26 | 0.106 | 38 |  | 5 | 0.053 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1969 | 42 | 262 | 41.81 | 240 | 2863 | 14 | 2 | 4 | 1 | 1 | 49 | 0.263 | 58 |  | 3 | 0.0739 | Moisture level high otherwise results satisfactory.Suggest recheck moisture after draining some oil through valve.
33000 | 1969 | 42 | 278 | 41.81 | 205 | 1055 | 23 | 3 | 11 | 1 | 35 | 19 | 0.25 | 63 |  | 3.5 | 0.07 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1969 | 42 | 888 | 41.81 | 315 | 3168 | 137 | 22 | 71 | 2 | 341 | 14 | 0.225 | 59 |  | 3.4 | 0.065 | Acetylene level quite high. Tapchanger ?
33000 | 1969 | 42 | 1256 | 41.81 | 296 | 2738 | 116 | 32 | 95 | 3 | 714 | 21 | 0.203 | 66 |  | 3.2 | 0.07 | Acetylene level quite high. Tapchanger?
33000 | 1969 | 42 | 998 | 41.81 | 297 | 3117 | 85 | 27 | 83 | 3 | 503 | 18 | 0.207 | 57 |  | 2.8 | 0.068 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1969 | 42 | 1140 | 41.81 | 320 | 3441 | 161 | 36 | 80 | 3 | 540 | 22 | 0.208 | 71 |  | 2.8 | 0.07 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1969 | 42 | 1469.1 | 52 | 707.7 | 7300.4 | 148.3 | 30.7 | 95.5 | 3.8 | 483.1 | 23 | 0.205 | 40 |  | 3 | 0.091 | DGA is assessed as acceptable. | Acidity level is high but stable. Other test results are assessed as acceptable.
33000 | 1969 | 42 | 1200 | 64 | 777 | 7317.6 | 89.5 | 18.8 | 60.1 | 5 | 249.6 | 32 | 0.23 | 35 |  | 3 | 0.087 | DGA is assessed as acceptable. | Moisture content of sample is slightly high. Other test results are assessed as acceptable.
33000 | 1969 | 42 | 1036.6 | 48 | 571.4 | 5771.7 | 106.1 | 21.2 | 51 | 6.1 | 280.8 | 27 | 0.212 | 36 |  | 3 | 0.083 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1969 | 42 | 802.9 | 32 | 557.2 | 5102 | 57.1 | 12.2 | 35.7 | 1.9 | 138.8 | 19 | 0.199 | 75 |  | 3 | 0.084 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1969 | 42 | 820.1 | 33 | 474.3 | 4809.1 | 83.5 | 16.8 | 40 | 3.4 | 202.1 | 19 | 0.273 | 72 |  | 3 | 0.083 | DGA is assessed as acceptable. | Acidity level is high. Other oil quality results are assessed as acceptable.
33000 | 1969 | 42 | 816 | 36 | 522 | 2901 | 98 | 17 | 41 | 2 | 136 | 32 | 0.292 | 55 |  | 1.7 | 0.119 | Oil fair condition. DLA suggests arcing; possible diffusion from tapchanger ?
33000 | 1969 | 42 | 822 | 48 | 332 | 2683 | 124 | 22 | 58 | 2 | 284 | 10 | 0.258 | 66 |  | 2.7 | 0.081 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1969 | 42 | 1127 | 60 | 390 | 2644 | 170 | 39 | 83 | 3 | 442 | 23 | 0.255 | 62 |  | 2.4 | 0.091 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1969 | 42 | 23 | 41.81 | 12 | 298 | 0 | 1 | 2 | 1 | 7 | 22 | 0.017 | 35 |  | 40.4 | 0.022 | Test results satisfactory. Sampled after oil change.
33000 | 1969 | 42 | 148 | 46 | 59 | 665 | 31 | 3 | 8 | 0 | 47 | 14 | 0.018 | 58 |  | 27.6 | 0.018 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1969 | 42 | 922 | 38 | 274 | 2713 | 154 | 38 | 66 | 2 | 388 | 27 | 0.041 | 50 |  | 14.6 | 0.018 | Test results are assessed as acceptable. Acetylene gas possibly from tapchanger. | Oil quality is assessed as acceptable.
33000 | 1969 | 42 | 1082.3 | 52 | 524.5 | 5892 | 131.7 | 32.1 | 86.7 | 2.5 | 304.8 | 25 | 0.048 | 36 |  | 10 | 0.029 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1969 | 42 | 983.9 | 65 | 636 | 7324.6 | 91.3 | 20.2 | 69.4 | 4 | 163 | 31 | 0.038 | 35 |  | 10 | 0.029 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1969 | 42 | 784.4 | 48 | 413.4 | 5101 | 90.6 | 19.9 | 59.8 | 4.7 | 196 | 29 | 0.052 | 41 |  | 9 | 0.028 | DGA is assessed as acceptable. | Other oil quality results are assessed as acceptable.
33000 | 1969 | 42 | 643.4 | 33 | 416 | 4868.3 | 51.7 | 12.6 | 52.9 | 2 | 108.2 | 19 | 0.044 | 75 |  | 9 | 0.034 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1969 | 42 | 661.3 | 33 | 347 | 4165.3 | 76.1 | 16.1 | 52.7 | 3.8 | 165.6 | 20 | 0.059 | 60 |  | 9 | 0.029 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1969 | 42 | 628 | 34 | 446 | 2949 | 40 | 69 | 42 | 1 | 30 | 31 | 0.247 | 46 |  | 4.5 | 0.0586 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1969 | 42 | 538 | 31 | 421 | 2512 | 52 | 6 | 27 | 1 | 31 | 17 | 0.241 | 69 |  | 4 | 0.0605 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1969 | 42 | 632 | 47 | 472 | 2992 | 56 | 7 | 38 | 1 | 58 | 29 | 0.205 | 46 |  | 3.3 | 0.074 | Test results satisfactory. Acetylene gas possibly from tapchanger. | Oil quality is assessed as acceptable.
33000 | 1969 | 42 | 438 | 76 | 269 | 2150 | 32 | 8 | 30 | 2 | 97 | 21 | 0.211 | 64 |  | 3.3 | 0.07 | Acetylene gas possibly from tapchanger. | Acidity level is slightly high. Other test results are assessed as acceptable.
33000 | 1969 | 42 | 480.4 | 45 | 278.1 | 3431.2 | 31 | 8.1 | 35.9 | 3.8 | 123.5 | 20 | 0.22 | 40 |  | 3 | 0.07 | The test results are assessed as acceptable. Acetylene gas possibly from tapchanger. | Oil quality is assessed as acceptable.
33000 | 1969 | 42 | 619.8 | 48 | 333.3 | 3263.3 | 77.7 | 16.7 | 34.7 | 4.1 | 153.3 | 31 | 0.207 | 25 |  | 3 | 0.071 | DGA is assessed as acceptable. | Acidity level is high but stable. Other oil quality results are assessed as acceptable.
33000 | 1969 | 42 | 595.1 | 46 | 305.5 | 3580.6 | 65.8 | 15.8 | 34 | 0 | 174 | 22 | 0.236 | 45 |  | 3 | 0.071 | DGA is assessed as acceptable. | Acidity level is high. Other oil quality results are assessed as acceptable.
33000 | 1969 | 42 | 494.8 | 57 | 303.9 | 3294.8 | 50.7 | 11.1 | 26.4 | 1.4 | 101.3 | 30 | 0.18 | 36 |  | 3 | 0.075 | DGA is assessed as acceptable. | Breakdown voltage is low. Other oil quality results are assessed as acceptable.
33000 | 1969 | 42 | 550.1 | 64 | 371.9 | 4161.9 | 53.4 | 9.8 | 25.8 | 1.3 | 87.9 | 53 | 0.205 | 19.5 |  | 3 | 0.073 | DGA is assessed as acceptable. | Acidity level is high. Breakdown voltage is low. DDF and Resistivity are assessed as acceptable. Corrosive IEC. Corrosive ASTM 4A.
33000 | 1969 | 42 | 516.4 | 54 | 364.9 | 4044.5 | 45.4 | 6.6 | 23.1 | 0.9 | 75.5 | 29 | 0.177 | 45 |  | 3 | 0.069 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable. Corrosive IEC. Corrosive ASTM 4A.
33000 | 1969 | 42 | 535.8 | 60 | 356.2 | 4081.8 | 48.2 | 9.6 | 21.4 | 1.1 | 99.3 | 34 | 0.2 | 25 |  | 4 | 0.055 | DGA is assessed as acceptable. | Acidity level is high. Breakdown voltage is low. DDF and Resistivity are assessed as acceptable.
33000 | 1969 | 42 | 284 | 58 | 248 | 2421 | 27 | 3 | 4 | 1 | 1 | 21 | 0.295 | 68 |  | 3.5 | 0.072 | Test results satisfactory. | Acidity getting high.
33000 | 1969 | 42 | 264 | 38 | 257 | 2072 | 0 | 2 | 3 | 1 | 1 | 11 | 0.299 | 48 |  | 2.5 | 0.069 | Test results satisfactory. | Oil quality is assessed as acceptable.
33000 | 1969 | 42 | 271 | 48 | 265 | 1983 | 0 | 3 | 2 | 1 | 0 | 20 | 0.318 | 45 |  | 2.3 | 0.106 | DGA is assessed as acceptable. | Acidity level of oil quite high. Oil change should be considered.
33000 | 1969 | 42 | 20 | 41.81 | 9 | 320 | 9 | 1 | 1 | 0 | 0 | 22 | 0.018 | 59 |  | 35.4 | 0.015 | Test results satisfactory after oil change.
33000 | 1969 | 42 | 225 | 41.81 | 198 | 2027 | 6 | 2 | 18 | 0 | 1 | 17 | 0.031 | 64 |  | 14.6 | 0.017 | Test results are assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1969 | 42 | 63 | 50 | 51 | 541 | 7 | 1 | 4 | 0 | 0 | 13 | 0.031 | 73 |  | 12.2 | 0.022 | Test results are assessed as acceptable. Sampled after filtration. | Oil quality is assessed as acceptable.
33000 | 1969 | 42 | 118 | 54 | 105 | 951 | 0 | 1 | 11 | 1 | 0 | 12 | 0.033 | 73 |  | 11.2 | 0.023 | Test results are assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1969 | 42 | 204.7 | 47 | 161.3 | 3149.9 | 5.6 | 2.1 | 34.2 | 1.5 | 0 | 12 | 0.041 | 48 |  | 12 | 0.023 | The test results are assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1969 | 42 | 279.6 | 44 | 246.5 | 3392.6 | 3.9 | 2.3 | 26.2 | 0.7 | 0 | 46 | 0.045 | 17 |  | 10 | 0.027 | DGA is assessed as acceptable. | Moisture content is high. Breakdown voltage is low. Possible sample contamination. Other oil quality results are assessed as acceptable.
33000 | 1969 | 42 | 254 | 32 | 217 | 2938.2 | 2.5 | 5.2 | 29.3 | 0 | 0 | 16 | 0.046 | 31 |  | 10.4 | 0.029 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1969 | 42 | 357.1 | 33 | 310.4 | 2954.2 | 11.1 | 2.5 | 32.2 | 0.9 | 0 | 14 | 0.04 | 53 |  | 8 | 0.034 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1969 | 42 | 277.8 | 36 | 236.6 | 3026 | 0 | 2.8 | 37.1 | 1.3 | 0 | 20 | 0.056 | 47 |  | 6 | 0.044 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1969 | 42 | 283.5 | 54 | 250.6 | 2249.2 | 5.7 | 0.4 | 26.3 | 0.5 | 0 | 15 | 0.045 | 50 |  | 9 | 0.028 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1969 | 42 | 206 | 50 | 177 | 2360.1 | 4.3 | 1.8 | 22.6 | 0.3 | 0 | 23 | 0.053 | 52 |  | 9 | 0.034 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1968 | 43 | 352 | 41.81 | 300 | 3395 | 18 | 2 | 30 | 1 | 1 | 25 | 0.065 | 38 |  | 13.1 | 0.022 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1968 | 43 | 378.7 | 35 | 312 | 2648.6 | 13.3 | 2.7 | 46.1 | 1.5 | 3.1 | 16 | 0.081 | 75 |  | 7 | 0.034 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1968 | 43 | 886.7 | 60 | 797.8 | 7169.6 | 25.9 | 6 | 54.4 | 1.4 | 1.2 | 35 | 0.098 | 22 |  | 8.3613 | 0.033539 | DGA is assessed as acceptable. | Moisture content of sample is high. Breakdown voltage of sample is low.
33000 | 1968 | 43 | 938 | 60 | 843.1 | 7134.1 | 25 | 6.8 | 59.5 | 2.7 | 0.9 | 36 | 0.094 | 19 |  | 7.7491 | 0.039886 | Carbon dioxide level is trending upwards. The test results are consistent with main tank sample. | Moisture content of sample is high. Breakdown voltage of sample is very low.
33000 | 1968 | 43 | 910.1 | 63 | 831.5 | 8354.6 | 24.3 | 5.3 | 47.4 | 1.2 | 0.4 | 36 | 0.089 | 37 |  | 8 | 0.035 | DGA is assessed as acceptable. | Moisture content is slightly high. Other oil quality results are assessed as acceptable.
33000 | 1968 | 43 | 659.9 | 60 | 589.6 | 6478.1 | 16.5 | 3.8 | 50 | 0 | 0 | 27 | 0.097 | 36 |  | 8 | 0.036 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1968 | 43 | 448.3 | 56 | 406 | 4221.3 | 9 | 2.5 | 30.8 | 0 | 0 | 21 | 0.09 | 75 |  | 7 | 0.043 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1968 | 43 | 362.5 | 41.81 | 325.7 | 3533.3 | 6.9 | 2.4 | 27.5 | 0 | 0 | 22 | 0.11 | 41 |  | 7 | 0.035 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1968 | 43 | 147 | 52 | 129.2 | 1322.6 | 3.7 | 1.2 | 11.6 | 0.3 | 1 | 13 | 0.096 | 75 |  | 7 | 0.032 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1968 | 43 | 122.3 | 19 | 108.7 | 1109 | 1.8 | 1 | 9.4 | 0.4 | 1 | 11 | 0.1 | 75 |  | 7 | 0.037 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable. Corrosive IEC. Non-corrosive ASTM 3B.
33000 | 1968 | 43 | 32.9 | 25 | 24.4 | 607.7 | 7.5 | 0.8 | 0.2 | 0 | 0 | 28 | 0.088 | 36 |  | 3 | 0.085 | DGA is assessed as acceptable. | Breakdown voltage is low. Other oil quality results are assessed as acceptable.
33000 | 1968 | 43 | 83 | 41.81 | 52 | 769 | 0 | 1 | 26 | 2 | 2 | 8 | 0.047 | 62 |  | 11.8 | 0.03 | DGA levels low as transformer in storage at Northgate.
33000 | 1968 | 43 | 257 | 41.81 | 223 | 1478 | 0 | 1 | 33 | 0 | 0 | 19 | 0.047 | 52 |  | 12.1 | 0.03 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1968 | 43 | 267 | 40 | 193 | 1372 | 40 | 1 | 31 | 0 | 2 | 38 | 0.045 | 16 |  | 16.9 | 0.015 | Dielectric strength of oil low. Moisture content high. Possible sample contamination.
33000 | 1968 | 43 | 367 | 48 | 292 | 1939 | 34 | 2 | 38 | 0 | 1 | 15 | 0.045 | 72 |  | 10.6 | 0.029 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1968 | 43 | 174 | 40 | 141 | 1222 | 9 | 1 | 23 | 0 | 0 | 15 | 0.047 | 74 |  | 13.5 | 0.022 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1968 | 43 | 377.1 | 45 | 270 | 1971.7 | 63.8 | 2.2 | 38.9 | 0.5 | 1.7 | 19 | 0.056 | 62 |  | 9 | 0.03 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1968 | 43 | 346.5 | 35 | 298.9 | 2213.6 | 11.3 | 2 | 33.1 | 0.4 | 0.8 | 15 | 0.056 | 56 |  | 9 | 0.037 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1968 | 43 | 102.3 | 41.81 | 72.1 | 1835.3 | 1 | 1.3 | 26.2 | 0.4 | 1.3 | 15 | 0.044 | 75 |  | 8 | 0.032 | Dissolved gas analysis is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1968 | 43 | 39.5 | 41.81 | 27 | 747 | 1 | 0.5 | 10 | 0.2 | 0.8 | 14 | 0.019 | 63 |  | 21 | 0.017 | Dissolved gas analysis is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1968 | 43 | 77.3 | 15 | 56.2 | 1296 | 0 | 1 | 18.1 | 0.3 | 1.7 | 10 | 0.042 | 64 |  | 9 | 0.034 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1968 | 43 | 860 | 30 | 680 | 4044 | 169 | 5 | 3 | 3 | 0 | 26 | 0.162 | 34 |  | 5.5 | 0.0388 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1968 | 43 | 524 | 52 | 464 | 3695 | 52 | 3 | 4 | 1 | 0 | 42 | 0.211 | 59 |  | 16.4 | 0.018 | DGA is assessed as acceptable. | Moisture content of oil slightly high. Other test results satisfactory.
33000 | 1968 | 43 | 1143 | 51 | 979 | 6603 | 151 | 6 | 5 | 2 | 0 | 30 | 0.218 | 45 |  | 3.4 | 0.066 | DGA is assessed as acceptable. | Acidity level of oil is slightly high. Other test results are assessed as acceptable.
33000 | 1968 | 43 | 1627 | 44 | 1380 | 9370 | 79 | 88 | 40 | 40 | 0 | 65 | 0.272 | 38 |  | 2 | 0.104 | Moisture content of sample is high. Acidity level of sample is high. 2-furfural level is high suggesting accelerated rate of insulation degradation. RECOMMEND RESAMPLE IN 1 YEAR TO MONITOR CONDITION.
33000 | 1968 | 43 | 1700.5 | 66 | 1396.8 | 11551 | 114.6 | 116.5 | 24.6 | 48 | 0 | 77 | 0.319 | 19 |  | 2 | 0.118 | 2-furfural and carbon oxide levels are high and trending upwards suggesting advanced state of insulation degradation. Moisture content of sample is high. Acidity level of sample is high. Breakdown voltage of sample is low. RECOMMEND OIL CHANGE / TREAT
33000 | 1968 | 43 | 398 | 24 | 306 | 2375 | 86 | 2 | 3 | 1 | 0 | 65 | 0.138 | 15 |  | 8 | 0.0278 | Breakdown strength; poor. Moisture content high.
33000 | 1968 | 43 | 674 | 53 | 563 | 3333 | 75 | 11 | 15 | 10 | 0 | 45 | 0.15 | 31 |  | 6.3 | 0.037 | DGA is assessed as acceptable. | Moisture content of oil high. Other test results satisfactory.
33000 | 1968 | 43 | 565 | 56 | 485 | 4185 | 50 | 5 | 14 | 11 | 0 | 72 | 0.192 | 38 |  | 4.2 | 0.049 | DGA is assessed as acceptable. | Moisture content of oil is very high. Other test results are assessed as acceptable.
33000 | 1968 | 43 | 631 | 40 | 579 | 4780 | 38 | 3 | 6 | 5 | 0 | 22 | 0.183 | 71 |  | 5.2 | 0.046 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1968 | 43 | 705.6 | 40 | 628.9 | 7248.4 | 47.6 | 8 | 16.3 | 4.8 | 0 | 39 | 0.225 | 14 |  | 3 | 0.083 | Dissolved gas analysis is assessed as acceptable. | Moisture content of sample is high. Acidity level of sample is high. Breakdown voltage of sample is low.
33000 | 1968 | 43 | 1374.7 | 42 | 1242.5 | 10824.2 | 92.6 | 18.3 | 14.1 | 7.2 | 0 | 41 | 0.265 | 16 |  | 2 | 0.094 | Carbon dioxide level is high. | Moisture content of sample is high. Breakdown voltage of sample is low. Acidity level of sample is high.
33000 | 1968 | 43 | 1026.4 | 46 | 947.3 | 7464.8 | 52.4 | 8.5 | 12.8 | 5.4 | 0 | 51 | 0.261 | 26 |  | 3 | 0.084 | DGA is assessed as acceptable. | Breakdown voltage is low. Moisture content is high.
33000 | 1968 | 43 | 888.8 | 41 | 829.3 | 5924.2 | 40.9 | 6.6 | 9.1 | 2.9 | 0 | 31 | 0.281 | 41 |  | 3 | 0.072 | DGA is assessed as acceptable. | Acidity level is high. Other oil quality results are assessed as acceptable.
33000 | 1968 | 43 | 185 | 41.81 | 63 | 806 | 7 | 5 | 24 | 0 | 86 | 21 | 0.098 | 44 |  | 50 | 0.094 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1968 | 43 | 359 | 41.81 | 127 | 1071 | 54 | 10 | 31 | 1 | 136 | 31 | 0.074 | 58 |  | 2.7 | 0.151 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1968 | 43 | 350 | 41.81 | 90 | 906 | 45 | 10 | 30 | 1 | 174 | 45 | 0.07 | 35 |  | 2.3 | 0.156 | DGA is assessed as acceptable. | Moisture content is high. Other oil quality results are assessed as acceptable.
33000 | 1968 | 43 | 400 | 41.81 | 119 | 1558 | 41 | 10 | 40 | 1 | 189 | 14 | 0.082 | 63 |  | 2.9 | 0.154 | DGA is assessed as acceptable. Acetylene gas possibly communicating from tapchanger. | Oil quality is assessed as acceptable.
33000 | 1968 | 43 | 428 | 41.81 | 102 | 1716 | 91 | 13 | 35 | 1 | 186 | 34 | 0.079 | 53 |  | 2.5 | 0.168 | DGA is assessed as acceptable. | Moisture content of oil high. Other oil quality results are assessed as acceptable.
33000 | 1968 | 43 | 409 | 41.81 | 75 | 1260 | 86 | 13 | 30 | 1 | 204 | 66 | 0.087 | 18 |  | 4.1 | 0.078 | Dissolved gas analysis is consistent with previous results. Moisture content of oil very high; possibly sample contamination.
33000 | 1968 | 43 | 342.7 | 45 | 182.9 | 6833.8 | 15.7 | 4.9 | 38.7 | 2.4 | 98.1 | 45 | 0.092 | 46 |  | 4 | 0.074 | Carbon dioxide gas level is high. Acetylene gas possibly from tapchanger. | Moisture content of sample is high. Other test results are assessed as acceptable.
33000 | 1968 | 43 | 291.1 | 36 | 162.1 | 2188.4 | 19.2 | 6.5 | 25.8 | 2.3 | 75.2 | 21 | 0.09 | 75 |  | 1.6 | 0.217 | DGA is assessed as acceptable. | DDF is high. Other oil quality results are assessed as acceptable.
33000 | 1968 | 43 | 377.4 | 32 | 291.4 | 2574.3 | 24.3 | 4.1 | 14.5 | 0.6 | 42.5 | 17 | 0.104 | 46 |  | 1 | 0.273 | DGA is assessed as acceptable. | DDF is high and Resistivity is low. Other oil quality results are assessed as acceptable.
33000 | 1968 | 43 | 309.1 | 44 | 242.6 | 2511.3 | 38.9 | 6 | 5.8 | 1 | 14.8 | 16 | 0.097 | 73 |  | 1 | 0.293 | DGA is assessed as acceptable. | DDF is high and Resistivity is low. Other oil quality results are assessed as acceptable. Corrosive IEC. Corrosive ASTM 4A.
33000 | 1968 | 43 | 343.4 | 35 | 245.5 | 2990.1 | 76.9 | 3.8 | 4.7 | 2 | 10.5 | 19 | 0.097 | 64 |  | 1 | 0.255 | Hydrogen level is increasing. Other dissolved gas levels are assessed as acceptable. | DDF is high and Resistivity is low. Other oil quality results are assessed as acceptable.
33000 | 1968 | 43 | 163 | 26 | 94.2 | 1809.9 | 38.5 | 3.2 | 5.6 | 1.8 | 19.7 | 15 | 0.089 | 76 |  | 2 | 0.205 | DGA is assessed as acceptable. | DDF is high. Other oil quality results are assessed as acceptable.
33000 | 1968 | 43 | 411 | 40 | 225 | 2184 | 55 | 8 | 20 | 1 | 102 | 16 | 0.132 | 55 |  | 7 | 0.041 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1968 | 43 | 169 | 25 | 84 | 1540 | 10 | 4 | 15 | 1 | 55 | 10 | 0.139 | 55 |  | 7 | 0.041 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1968 | 43 | 217 | 35 | 137 | 1531 | 35 | 3 | 15 | 1 | 26 | 12 | 0.127 | 73 |  | 5.4 | 0.052 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1968 | 43 | 185 | 64 | 147 | 1860 | 19 | 2 | 12 | 0 | 5 | 11 | 0.123 | 70 |  | 5 | 0.043 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1968 | 43 | 358.2 | 66 | 80 | 1946.2 | 97.7 | 13 | 35.7 | 5.6 | 126.2 | 11 | 0.132 | 73 |  | 4 | 0.052 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1968 | 43 | 297.9 | 89 | 143.8 | 2017.8 | 41.3 | 8.7 | 21.7 | 2.9 | 79.5 | 24 | 0.126 | 72 |  | 4 | 0.058 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1968 | 43 | 246.5 | 38 | 116.1 | 1712.7 | 10.9 | 7 | 23.6 | 1.1 | 87.8 | 21 | 0.155 | 75 |  | 4 | 0.054 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1968 | 43 | 302.8 | 36 | 167.4 | 3225.9 | 13.3 | 8.3 | 22.7 | 0.9 | 90.2 | 21 | 0.14 | 42 |  | 4 | 0.068 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable. Corrosive IEC. Corrosive ASTM 4A.
33000 | 1968 | 43 | 291.5 | 42 | 158.7 | 3206.3 | 58.5 | 6.6 | 12 | 1.3 | 54.4 | 24 | 0.123 | 76 |  | 4 | 0.064 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1968 | 43 | 210.2 | 40 | 124 | 1937.7 | 17.6 | 4.3 | 13.7 | 1.1 | 49.5 | 22 | 0.133 | 38 |  | 4 | 0.058 | DGA is assessed as acceptable. | Breakdown voltage is low. Other oil quality results are assessed as acceptable.
33000 | 1968 | 43 | 504 | 43 | 206 | 3268 | 47 | 8 | 40 | 3 | 200 | 17 | 0.158 | 70 |  | 6 | 0.049 | Test results satisfactory. Note C2H2 level. | Oil quality is assessed as acceptable.
33000 | 1968 | 43 | 288 | 30 | 115 | 2637 | 14 | 5 | 28 | 1 | 125 | 11 | 0.176 | 70 |  | 6 | 0.041 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1968 | 43 | 238 | 20 | 149 | 2014 | 5 | 6 | 25 | 4 | 49 | 12 | 0.16 | 60 |  | 5.2 | 0.051 | Test results satisfactory. Acetylene possibly from tapchanger. | Oil quality is assessed as acceptable.
33000 | 1968 | 43 | 351 | 50 | 131 | 1883 | 15 | 8 | 34 | 6 | 157 | 10 | 0.152 | 75 |  | 4.7 | 0.053 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1968 | 43 | 447.1 | 50 | 60.4 | 2172.9 | 107.5 | 12.8 | 42.7 | 3.6 | 220.1 | 10 | 0.151 | 75 |  | 4 | 0.053 | The test results are assessed as acceptable. Acetylene gas possibly from tapchanger. | Oil quality is assessed as acceptable.
33000 | 1968 | 43 | 432.3 | 73 | 136.9 | 1856.5 | 109.5 | 15.9 | 27 | 3.7 | 139.3 | 22 | 0.145 | 75 |  | 4 | 0.065 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1968 | 43 | 254.9 | 38 | 97.2 | 1833.8 | 12 | 20.9 | 51.7 | 1.3 | 71.8 | 20 | 0.168 | 75 |  | 4 | 0.061 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1968 | 43 | 350.3 | 43 | 127.2 | 2217.7 | 31.3 | 11.5 | 34.9 | 2.2 | 143.2 | 18 | 0.153 | 75 |  | 4 | 0.069 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable. Corrosive IEC. Corrosive ASTM 4A.
33000 | 1968 | 43 | 249.9 | 57 | 123.3 | 2108.3 | 34.7 | 7.5 | 12.9 | 1.3 | 70.2 | 28 | 0.13 | 64 |  | 3 | 0.077 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1968 | 43 | 160.8 | 41.81 | 88 | 1649 | 16 | 3 | 13 | 0.8 | 40 | 23 | 0.13 | 38 |  | 3 | 0.066 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1968 | 43 | 232.6 | 42 | 103.5 | 1889.5 | 24.4 | 6.9 | 17.7 | 2.3 | 77.8 | 21 | 0.141 | 54 |  | 3 | 0.07 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1968 | 43 | 100 | 40 | 84 | 1246 | 0 | 0 | 16 | 0 | 0 | 11 | 0.017 | 47 |  | 60 | 0.014 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1968 | 43 | 305 | 48 | 261 | 2345 | 0 | 3 | 38 | 3 | 0 | 13 | 0.034 | 58 |  | 29 | 0.016 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1968 | 43 | 391 | 33 | 347 | 3364 | 0 | 2 | 41 | 1 | 0 | 14 | 0.033 | 41 |  | 14.7 | 0.021 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1968 | 43 | 406.9 | 40 | 340.4 | 4027.6 | 7.2 | 2.7 | 54.6 | 1.6 | 0.4 | 32 | 0.045 | 15 |  | 12 | 0.027 | DGA is assessed as acceptable. | Moisture content of sample is high. Breakdown voltage of sample is low. Other test results are assessed as acceptable.
33000 | 1968 | 43 | 626.4 | 64 | 562 | 5278 | 14.5 | 3.4 | 45.6 | 0.9 | 0 | 38 | 0.057 | 22 |  | 9 | 0.035 | DGA is assessed as acceptable. | Moisture content is slightly high but acceptable for operating temperature. Breakdown voltage is low. Possible sample contamination. Other oil quality results are assessed as acceptable.
33000 | 1968 | 43 | 649.5 | 52 | 593.5 | 5406.9 | 6 | 3.7 | 45.2 | 1 | 0.1 | 32 | 0.041 | 40 |  | 7 | 0.042 | DGA is assessed as acceptable. | Moisture content is slightly high but acceptable for operating temperature. Other oil quality results are assessed as acceptable.
33000 | 1968 | 43 | 761.2 | 62 | 692.2 | 6378.4 | 9.7 | 4.2 | 54.5 | 0.6 | 0 | 53 | 0.054 | 18 |  | 10 | 0.033 | DGA is assessed as acceptable. | Moisture content is high. Breakdown voltage is low. Other oil quality results are assessed as acceptable.
33000 | 1968 | 43 | 686.1 | 64 | 623.2 | 6722.5 | 8.3 | 3.8 | 48.8 | 2 | 0 | 32 | 0.072 | 41 |  | 8 | 0.036 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1967 | 44 | 75 | 21 | 64.9 | 1170.6 | 1.9 | 1.7 | 6.4 | 0.1 | 0 | 28 | 0.14 | 45 |  | 7 | 0.029 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1967 | 44 | 117 | 50 | 99 | 621 | 0 | 1 | 11 | 0 | 6 | 13 | 0.017 | 54 |  | 60 | 0.013 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1967 | 44 | 124 | 26 | 86 | 760 | 0 | 2 | 11 | 0 | 25 | 15 | 0.035 | 58 |  | 18.6 | 0.018 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1967 | 44 | 143 | 41.81 | 107 | 1803 | 13 | 1 | 18 | 1 | 3 | 30 | 0.029 | 42 |  | 24.3 | 0.013 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1967 | 44 | 336 | 37 | 116 | 1849 | 9 | 6 | 50 | 0 | 155 | 11 | 0.029 | 62 |  | 25.9 | 0.013 | Test results are assessed as acceptable. Acetylene gas probably from tapchanger. | Oil quality is assessed as acceptable.
33000 | 1967 | 44 | 143.1 | 47 | 108.5 | 1349.1 | 7.9 | 1.3 | 15.8 | 0.9 | 8.7 | 26 | 0.025 | 32 |  | 15 | 0.022 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1967 | 44 | 189.2 | 37 | 111.4 | 1329.9 | 6.1 | 3.6 | 56.6 | 11.5 | 0 | 21 | 0.024 | 31 |  | 21 | 0.015 | DGA is assessed as acceptable | Oil quality is assessed as acceptable.
33000 | 1967 | 44 | 118.7 | 40 | 100 | 1257.9 | 2.4 | 0.9 | 13.1 | 0 | 2.3 | 24 | 0.027 | 52 |  | 18 | 0.018 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1967 | 44 | 127.7 | 28 | 86 | 1380.3 | 8.3 | 1.6 | 15.1 | 0.5 | 16.2 | 26 | 0.03 | 32 |  | 14 | 0.02 | DGA is assessed as acceptable. | Breakdown voltage is low. Other oil quality results are assessed as acceptable. Corrosive IEC. Non-corrosive ASTM 3B.
33000 | 1967 | 44 | 141.7 | 30 | 93.5 | 1288.9 | 9.6 | 2.5 | 14.8 | 0.2 | 21.1 | 25 | 0.031 | 31 |  | 18 | 0.016 | DGA is assessed as acceptable. | Breakdown voltage is low. Other oil quality results are assessed as acceptable. Corrosive IEC. Corrosive ASTM 4A.
33000 | 1967 | 44 | 121.3 | 36 | 82.7 | 1221.3 | 7.3 | 1.9 | 12.5 | 0.3 | 16.6 | 20 | 0.028 | 49 |  | 14 | 0.022 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1967 | 44 | 258 | 30 | 163 | 1216 | 18 | 3 | 32 | 0 | 42 | 11 | 0.04 | 67.6 |  | 10 | 0.0415 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1967 | 44 | 363 | 35 | 193 | 1307 | 44 | 4 | 31 | 1 | 90 | 15 | 0.049 | 74 |  | 16.9 | 0.028 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1967 | 44 | 408 | 45 | 241 | 1511 | 32 | 5 | 33 | 1 | 96 | 21 | 0.054 | 53 |  | 18.9 | 0.019 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1967 | 44 | 425.8 | 42 | 289.8 | 2895.8 | 20.9 | 4.8 | 41.8 | 0.8 | 67.7 | 14 | 0.057 | 64 |  | 8 | 0.037 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1967 | 44 | 376.1 | 40 | 264.2 | 2506.2 | 18 | 3.6 | 32.8 | 2.6 | 54.9 | 17 | 0.056 | 71 |  | 10 | 0.028 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1967 | 44 | 258 | 33 | 196.9 | 1948.7 | 19 | 1.9 | 21.3 | 0 | 18.9 | 6 | 0.052 | 70 |  | 8 | 0.037 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1967 | 44 | 226.5 | 30 | 171.1 | 2075 | 10.5 | 1.8 | 20.8 | 0.6 | 21.7 | 14 | 0.084 | 63 |  | 8 | 0.032 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1967 | 44 | 255.4 | 48 | 209.3 | 2377.4 | 6.1 | 6.9 | 21 | 0.5 | 11.6 | 16 | 0.064 | 35 |  | 8 | 0.041 | DGA is assessed as acceptable. | Breakdown voltage is slightly low. Other oil quality results are assessed as acceptable. Corrosive IEC. Corrosive ASTM 4A.
33000 | 1967 | 44 | 170.2 | 40 | 148.3 | 1684.4 | 0 | 1 | 15.2 | 0.6 | 5.1 | 15 | 0.074 | 73 |  | 8 | 0.032 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1967 | 44 | 195.8 | 42 | 140.1 | 1659.4 | 11.9 | 9.9 | 15.1 | 0.1 | 18.7 | 19 | 0.055 | 65 |  | 10 | 0.027 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1967 | 44 | 234 | 45 | 171 | 3021 | 16 | 4 | 6 | 2 | 35 | 25 | 0.162 | 69 |  | 5 | 0.051 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1967 | 44 | 153 | 42 | 113 | 3476 | 0 | 3 | 12 | 7 | 18 | 98 | 0.181 | 22 |  | 2.2 | 0.128 | Moisture content of oil sample very high Failed electric breakdown test. DGA satisfactory.
33000 | 1967 | 44 | 158 | 41 | 128 | 2480 | 0 | 2 | 5 | 1 | 22 | 33 | 0.147 | 32 |  | 4.4 | 0.051 | DGA is assessed as acceptable.
33000 | 1967 | 44 | 196 | 41.81 | 152 | 2095 | 0 | 2 | 5 | 1 | 36 | 21 | 0.15 | 52 |  | 3.3 | 0.068 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1967 | 44 | 244 | 49 | 127 | 2197 | 34 | 3 | 10 | 1 | 69 | 31 | 0.146 | 56 |  | 4.1 | 0.058 | Test results satisfactory. | Oil quality is assessed as acceptable.
33000 | 1967 | 44 | 192 | 41.81 | 132 | 1891 | 21 | 3 | 8 | 2 | 26 | 39 | 0.144 | 40 |  | 4 | 0.052 | Test results are assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1967 | 44 | 296.6 | 48 | 222.9 | 2455.2 | 14.9 | 4.7 | 11.9 | 3.1 | 39.1 | 33 | 0.157 | 17 |  | 3 | 0.069 | DGA is assessed as acceptable. | Breakdown voltage of sample is low. Moisture content of sample is high. Other test results are assessed as acceptable.
33000 | 1967 | 44 | 246.5 | 22 | 180.9 | 3335.8 | 11.2 | 5 | 11 | 2.6 | 35.8 | 21 | 0.164 | 48 |  | 3 | 0.074 | DGA is assessed as acceptable. | Other test results are assessed as acceptable.
33000 | 1967 | 44 | 297.5 | 41 | 240.8 | 3640.8 | 14.2 | 3.5 | 7.7 | 2 | 29.3 | 29 | 0.165 | 61 |  | 3.2 | 0.078 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1967 | 44 | 285.4 | 41.81 | 212.8 | 3042.3 | 23.9 | 3.7 | 6.8 | 0.8 | 37.4 | 22 | 0.183 | 75 |  | 3 | 0.077 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1967 | 44 | 178.3 | 45.5 | 91.8 | 2061.8 | 20.4 | 4.7 | 9.2 | 0.6 | 51.6 | 19 | 0.146 | 73 |  | 3 | 0.079 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1967 | 44 | 227.6 | 48 | 168.5 | 2431.3 | 10.6 | 3.7 | 5.8 | 0.9 | 38.1 | 23 | 0.146 | 58 |  | 3 | 0.078 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable. Corrosive IEC. Corrosive ASTM 4A.
33000 | 1967 | 44 | 175.1 | 44 | 138.7 | 2692.9 | 7.2 | 3.7 | 4.9 | 1.3 | 19.3 | 23 | 0.141 | 50 |  | 3 | 0.068 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1967 | 44 | 160 | 32 | 112 | 1484 | 15 | 3 | 5 | 2 | 23 | 21 | 0.15 | 67 |  | 5 | 0.067 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1967 | 44 | 233 | 41.81 | 172 | 1758 | 15 | 5 | 6 | 3 | 32 | 19 | 0.15 | 63 |  | 2.7 | 0.113 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1967 | 44 | 401 | 41.81 | 311 | 2383 | 30 | 4 | 6 | 1 | 49 | 17 | 0.139 | 62 |  | 4.3 | 0.058 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1967 | 44 | 186.5 | 27 | 137.7 | 1833.4 | 0 | 2.9 | 8.4 | 1.9 | 35.6 | 20 | 0.173 | 67 |  | 3 | 0.065 | 2-furfural level is trending upwards. Other test results are assessed as acceptable. RECOMMEND RESAMPLE IN 1 YEAR TO MONITOR TREND.
33000 | 1967 | 44 | 16.8 | 25 | 16 | 93 | 0 | 0.4 | 0.4 | 0 | 0 | 8 | 0.146 | 75 |  | 4 | 0.058 | The test results are assessed as acceptable. EX STRATHPINE.
33000 | 1967 | 44 | 14.2 | 22 | 13.6 | 259 | 0 | 0.5 | 0.1 | 0 | 0 | 9 | 0.144 | 75 |  | 4 | 0.056 | The test results are assessed as acceptable.
33000 | 1967 | 44 | 604.8 | 47 | 526.6 | 2924.7 | 37.8 | 5.1 | 6.7 | 1.7 | 26.9 | 14 | 0.156 | 60 |  | 3 | 0.081 | The test results are assessed as acceptable. Acetylene gas possibly communicating from tapchanger.
33000 | 1967 | 44 | 984.6 | 59 | 863.6 | 4763.1 | 73.7 | 6.5 | 9.3 | 2.5 | 29 | 24 | 0.162 | 36 |  | 3 | 0.08 | The test results are assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1967 | 44 | 515.7 | 46 | 445.1 | 3596.4 | 26.9 | 4.4 | 7.8 | 2.3 | 29.2 | 15 | 0.151 | 75 |  | 3 | 0.083 | The test results are assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1967 | 44 | 678.1 | 47 | 582.6 | 4654 | 35.9 | 5.7 | 10.3 | 2.8 | 40.8 | 18 | 0.18 | 63 |  | 3 | 0.086 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1967 | 44 | 726.4 | 56 | 622.2 | 5651 | 33.2 | 6.3 | 12.2 | 0.9 | 51.6 | 22 | 0.197 | 50 |  | 3 | 0.087 | DGA is assessed as acceptable. | Acidity level is high. Other oil quality results are assessed as acceptable.
33000 | 1967 | 44 | 864 | 34 | 358 | 2576 | 153 | 18 | 33 | 3 | 299 | 50 | 0.162 | 33 |  | 8 | 0.034 | C2H2 high tapchanger ? Moisture content of sample fairly high.
33000 | 1967 | 44 | 489 | 34 | 202 | 1934 | 70 | 10 | 19 | 2 | 186 | 95 | 0.186 | 13 |  | 5.1 | 0.049 | Moisture content of sample extremely high with subsequently poor oil breakdown strength. Recommend resample for moisture using glass syringes.
33000 | 1967 | 44 | 503 | 50 | 182 | 1492 | 72 | 9 | 32 | 2 | 206 | 20 | 0.15 | 29 |  | 4.1 | 0.053 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1967 | 44 | 399 | 41.81 | 140 | 2367 | 44 | 5 | 24 | 2 | 184 | 38 | 0.149 | 29 |  | 4.4 | 0.061 | Moisture content of oil high. Other test results satisfactory. Acetylene gas possibly from tapchanger.
33000 | 1967 | 44 | 327 | 41.81 | 126 | 1928 | 29 | 5 | 19 | 1 | 147 | 58 | 0.157 | 28 |  | 5 | 0.05 | Moisture content of oil high; dielectric strength low. Other test results satisfactory. Acetylene gas possibly from tapchanger.
33000 | 1967 | 44 | 393 | 41.81 | 139 | 1863 | 43 | 7 | 22 | 2 | 180 | 18 | 0.136 | 70 |  | 4.5 | 0.049 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1967 | 44 | 480.8 | 37 | 147.1 | 3069.4 | 50.4 | 8.4 | 34.9 | 2.5 | 237.5 | 29 | 0.142 | 31 |  | 4 | 0.052 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1967 | 44 | 501.3 | 54 | 279 | 5753.6 | 25.1 | 5.8 | 26.4 | 2.4 | 162.6 | 56 | 0.148 | 21 |  | 4 | 0.052 | DGA is assessed as acceptable. | Moisture content is high. Breakdown voltage is low. Possible sample contamination. Other oil quality results are assessed as acceptable.
33000 | 1967 | 44 | 430.7 | 41.81 | 212.6 | 4713.9 | 28.4 | 5.1 | 21.2 | 1.6 | 161.8 | 31 | 0.142 | 17 |  | 4.2 | 0.063 | DGA is assessed as acceptable. | Breakdown voltage is low. Moisture content is high. Other oil quality results are assessed as acceptable.
33000 | 1967 | 44 | 343.8 | 35 | 162.9 | 2836 | 38.6 | 5.9 | 16.3 | 0.4 | 119.7 | 52 | 0.156 | 16 |  | 3 | 0.067 | DGA is assessed as acceptable. | Moisture content is high. Breakdown voltage is low. Other oil quality results are assessed as acceptable.
33000 | 1967 | 44 | 322.4 | 52 | 150.6 | 2833.9 | 24.1 | 5.1 | 15.4 | 1.9 | 125.3 | 29 | 0.137 | 23 |  | 4 | 0.065 | DGA is assessed as acceptable. | Breakdown voltage is low. Other oil quality results are assessed as acceptable. Corrosive IEC. Corrosive ASTM 4A.
33000 | 1967 | 44 | 173.4 | 41.81 | 136 | 3399.3 | 6.3 | 1.7 | 6.5 | 1 | 21.9 | 61 | 0.119 | 14 |  | 5 | 0.047 | DGA is assessed as acceptable. | Breakdown voltage is low. Other oil quality results are assessed as acceptable.
33000 | 1967 | 44 | 163.7 | 41.81 | 110.6 | 2798.6 | 15 | 2.3 | 5.3 | 1 | 29.5 | 64 | 0.155 | 12 |  | 4 | 0.05 | DGA is assessed as acceptable. | Breakdown voltage is low. Other oil quality results are assessed as acceptable.
33000 | 1967 | 44 | 173.4 | 41.81 | 110 | 3120.6 | 19.9 | 3.4 | 5.6 | 1 | 33.5 | 43 | 0.136 | 34 |  | 4 | 0.051 | DGA is assessed as acceptable. | Breakdown voltage is low. Other oil quality results are assessed as acceptable.
33000 | 1967 | 44 | 234.2 | 41.81 | 156.4 | 4370.4 | 23.2 | 3.6 | 9.7 | 1.1 | 40.2 | 64 | 0.12 | 15 |  | 3 | 0.072 | DGA is assessed as acceptable. | Breakdown voltage is low. Other oil quality results are assessed as acceptable at present.
33000 | 1967 | 44 | 181.4 | 48 | 118.8 | 2722.8 | 17.6 | 4.1 | 1.5 | 0.9 | 38.5 | 64 | 0.139 | 15 |  | 4 | 0.053 | DGA is assessed as acceptable. | Breakdown voltage is low. Other oil quality results are assessed as acceptable.
33000 | 1967 | 44 | 74.4 | 41.81 | 42.7 | 693.5 | 7.2 | 1.2 | 3.2 | 0.5 | 19.6 | 12 | 0.137 | 49 |  | 5 | 0.051 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1967 | 44 | 127.2 | 30 | 87.6 | 2386.1 | 13.8 | 1.9 | 4.3 | 0.4 | 19.2 | 61 | 0.113 | 14 |  | 4 | 0.05 | DGA is assessed as acceptable. | Breakdown voltage is low. Oil is cloudy in appearance. Other oil quality results are assessed as acceptable at present.
33000 | 1967 | 44 | 250 | 32 | 166 | 1653 | 17 | 2 | 35 | 0 | 30 | 19 | 0.072 | 72 |  | 15 | 0.031 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1967 | 44 | 243 | 41.81 | 160 | 1427 | 19 | 2 | 24 | 1 | 37 | 17 | 0.075 | 31 |  | 11.8 | 0.027 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1967 | 44 | 346 | 41.81 | 249 | 1701 | 23 | 3 | 27 | 1 | 43 | 22 | 0.057 | 60 |  | 12.4 | 0.024 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1967 | 44 | 435.7 | 52 | 195.2 | 2909.8 | 29.6 | 6.2 | 66.7 | 2 | 136 | 22 | 0.088 | 58 |  | 6 | 0.042 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1967 | 44 | 481.3 | 44 | 255.1 | 4019.1 | 25.1 | 4.6 | 62.3 | 3.9 | 130.3 | 23 | 0.082 | 41 |  | 6 | 0.039 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1967 | 44 | 477.7 | 41.81 | 235.7 | 4200.1 | 27.8 | 5.1 | 63.9 | 1.9 | 143.3 | 20 | 0.0923 | 59 |  | 7 | 0.03638 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1967 | 44 | 460.3 | 37 | 225.5 | 3545.2 | 30 | 5.5 | 51.2 | 0 | 148.1 | 17 | 0.095 | 44 |  | 7 | 0.035 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1967 | 44 | 428.4 | 34 | 145.1 | 1727.4 | 42.5 | 6 | 42.9 | 1.7 | 190.2 | 13 | 0.106 | 68 |  | 7 | 0.039 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable. Corrosive IEC. Corrosive ASTM 4B.
33000 | 1967 | 44 | 373.7 | 30 | 143.7 | 1722.1 | 27 | 5.1 | 39.4 | 1.5 | 157 | 13 | 0.097 | 73 |  | 6 | 0.038 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1967 | 44 | 256.8 | 30 | 114.2 | 1455.8 | 11.7 | 3.9 | 28.5 | 1.7 | 96.8 | 15 | 0.094 | 55 |  | 6 | 0.038 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1967 | 44 | 259.4 | 46 | 117.7 | 1475.6 | 11 | 3.3 | 28.4 | 2.3 | 96.7 | 16 | 0.096 | 66 |  | 7 | 0.035 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1967 | 44 | 237.1 | 37 | 124.8 | 1605.2 | 10.3 | 3 | 27.9 | 0.6 | 70.5 | 19 | 0.094 | 56 |  | 6 | 0.04 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1967 | 44 | 98 | 20 | 75 | 1854 | 0 | 2 | 17 | 0 | 4 | 8 | 0.026 | 49 |  | 47.5 | 0.0128 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1967 | 44 | 148 | 40 | 82 | 988 | 28 | 2 | 13 | 0 | 23 | 23 | 0.026 | 50 |  | 46.5 | 0.009 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1967 | 44 | 229 | 40 | 140 | 1270 | 31 | 3 | 18 | 1 | 36 | 21 | 0.026 | 54 |  | 33 | 0.011 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1967 | 44 | 229 | 25 | 174 | 1543 | 0 | 4 | 28 | 1 | 22 | 23 | 0.025 | 58 |  | 52.6 | 0.01 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1967 | 44 | 229 | 46 | 165 | 1545 | 15 | 3 | 24 | 1 | 21 | 29 | 0.04 | 40 |  | 29 | 0.016 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1967 | 44 | 242 | 31 | 148 | 1492 | 37 | 4 | 22 | 1 | 30 | 22 | 0.024 | 46 |  | 36.2 | 0.012 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1967 | 44 | 295.3 | 41.81 | 187 | 2753.2 | 23.5 | 4.8 | 32 | 2.7 | 45.3 | 23 | 0.03 | 43 |  | 16 | 0.019 | The test results are assessed as acceptable. Acetylene gas possibly from tapchanger. | Oil quality is assessed as acceptable.
33000 | 1967 | 44 | 325 | 41 | 230.8 | 3240.2 | 19.6 | 4.1 | 30.2 | 2 | 38.3 | 27 | 0.037 | 31 |  | 22 | 0.018 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1967 | 44 | 228.9 | 47 | 155.7 | 2595.4 | 16.7 | 3.5 | 22.7 | 0.6 | 29.7 | 24 | 0.01 | 46 |  | 21 | 0.017 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1967 | 44 | 353.2 | 46 | 254.5 | 3360.6 | 20.5 | 4.4 | 29 | 0.3 | 44.5 | 34 | 0.04 | 16 |  | 20 | 0.014 | DGA is assessed as acceptable. | Moisture content is high. Breakdown voltage is low. Other oil quality results are assessed as acceptable.
33000 | 1967 | 44 | 238 | 70 | 170.7 | 2560.3 | 9.6 | 3.2 | 22.2 | 0.8 | 31.5 | 33 | 0.034 | 17 |  | 20 | 0.018 | DGA is assessed as acceptable. | Breakdown voltage is low. Other oil quality results are assessed as acceptable.
33000 | 1967 | 44 | 194.4 | 63 | 129.1 | 2095.9 | 1.4 | 2.5 | 22.5 | 1.3 | 37.6 | 28 | 0.032 | 23 |  | 22 | 0.015 | DGA is assessed as acceptable. | Breakdown voltage is low. Other oil quality results are assessed as acceptable. Corrosive IEC. Corrosive ASTM 4B.
33000 | 1967 | 44 | 237.6 | 72 | 181.4 | 2511.8 | 9.7 | 2.9 | 22.1 | 0.8 | 20.7 | 29 | 0.04 | 25 |  | 19 | 0.018 | DGA is assessed as acceptable. | Breakdown voltage is low. Other oil quality results are assessed as acceptable.
33000 | 1967 | 44 | 223 | 50 | 127.1 | 1655.8 | 9.5 | 11.3 | 43.9 | 10.2 | 21 | 23 | 0.037 | 37 |  | 19 | 0.017 | DGA is assessed as acceptable. | Breakdown voltage is slightly low. Other oil quality results are assessed as acceptable.
33000 | 1967 | 44 | 206 | 44 | 135 | 1034 | 11 | 3 | 25 | 8 | 24 | 21 | 0.031 | 54 |  | 12 | 0.032 | Test results satisfactory.
33000 | 1967 | 44 | 226 | 35 | 147 | 1126 | 9 | 5 | 39 | 1 | 25 | 34 | 0.036 | 31 |  | 18.8 | 0.018 | Moisture content of oil slightly high. Other test results satisfactory. Acetylene gas possibly from tapchanger.
33000 | 1967 | 44 | 233 | 41.81 | 108 | 1037 | 31 | 3 | 25 | 1 | 65 | 25 | 0.036 | 27 |  | 14.7 | 0.022 | Test results are assessed as acceptable. Acetylene gas possibly from tapchanger.
33000 | 1967 | 44 | 273.1 | 32 | 131.6 | 1559.7 | 17 | 4.7 | 41.1 | 4.4 | 74.3 | 21 | 0.033 | 36 |  | 13 | 0.019 | The test results are assessed as acceptable. Acetylene gas possibly from tapchanger.
33000 | 1967 | 44 | 244 | 36 | 134.7 | 1683.7 | 18.9 | 6.5 | 28.3 | 0 | 55.6 | 16 | 0.034 | 75 |  | 11 | 0.024 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1967 | 44 | 239.2 | 30 | 151 | 1958.9 | 13.1 | 3 | 28.2 | 0.2 | 43.7 | 40 | 0.046 | 12 |  | 13 | 0.018 | DGA is assessed as acceptable. | Moisture content is high. Breakdown voltage is low. Other oil quality results are assessed as acceptable.
33000 | 1967 | 44 | 270.4 | 41.81 | 187.9 | 1625.7 | 7.4 | 7.1 | 23.7 | 0.7 | 43.6 | 12 | 0.044 | 75 |  | 11 | 0.026 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable. Corrosive IEC. Corrosive ASTM 4A.
33000 | 1967 | 44 | 164.8 | 28 | 111.5 | 1517.7 | 0 | 1.7 | 23.5 | 0 | 28.1 | 24 | 0.043 | 40 |  | 8 | 0.03 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1967 | 44 | 173.8 | 36 | 84.6 | 1223.9 | 26.6 | 3.1 | 17.4 | 0.5 | 41.6 | 14 | 0.037 | 74 |  | 10 | 0.026 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable. Particle contamination load is marginal.
33000 | 1967 | 44 | 142.3 | 35 | 108.6 | 1344.7 | 3.5 | 2.6 | 15.8 | 0.5 | 11.3 | 18 | 0.044 | 54 |  | 11 | 0.022 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1967 | 44 | 194 | 21 | 141 | 1363 | 19 | 2 | 19 | 0 | 13 | 16 | 0.07 | 64 |  | 15 | 0.021 | Test results satisfactory.
33000 | 1967 | 44 | 548 | 38 | 208 | 1534 | 31 | 30 | 160 | 85 | 34 | 22 | 0.09 | 54 |  | 8 | 0.035 | Ethylene level quite high. Possible hot spot. RECOMMEND RESAMPLE IN 6 MONTHS
33000 | 1967 | 44 | 469 | 45 | 256 | 1953 | 70 | 7 | 34 | 1 | 101 | 25 | 0.105 | 59 |  | 7.7 | 0.039 | Test results satisfactory. | Oil quality is assessed as acceptable.
33000 | 1967 | 44 | 573 | 47 | 270 | 2274 | 64 | 10 | 49 | 2 | 178 | 24 | 0.118 | 51 |  | 5.8 | 0.047 | High acetylene gas level possibly from tapchanger via conservator. | Other test results satisfactory.
33000 | 1967 | 44 | 636 | 38 | 223 | 4589 | 84 | 10 | 66 | 3 | 250 | 32 | 0.108 | 30 |  | 8.3 | 0.031 | Test results are assessed as acceptable. Acetylene gas possibly from tapchanger. | Oil quality is assessed as acceptable.
33000 | 1967 | 44 | 373.2 | 54 | 152.2 | 2423.7 | 20.9 | 4.8 | 56.8 | 1.8 | 136.7 | 29 | 0.098 | 27 |  | 4 | 0.058 | The test results are assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1967 | 44 | 363.5 | 44 | 179.1 | 3575.9 | 25.1 | 4.3 | 36.4 | 3.4 | 115.2 | 59 | 0.08 | 16 |  | 7 | 0.035 | DGA is assessed as acceptable. | Moisture content is high. Breakdown voltage is low. Possible sample contamination. Other oil quality results are assessed as acceptable.
33000 | 1967 | 44 | 356.7 | 43 | 170.9 | 3372.1 | 25 | 4.7 | 37.1 | 1.5 | 117.5 | 58 | 0.0944 | 19 |  | 8 | 0.031 | DGA is assessed as acceptable. | Moisture content is high. Breakdown voltage is low. Other oil quality results are assessed as acceptable.
33000 | 1967 | 44 | 370.4 | 38 | 183.7 | 3220.9 | 27.6 | 4.8 | 34.2 | 0 | 120.1 | 36 | 0.099 | 18 |  | 6 | 0.037 | DGA is assessed as acceptable. | Moisture content is high. Breakdown voltage is low. Other oil quality results are assessed as acceptable.
33000 | 1967 | 44 | 328.3 | 38 | 99 | 1672.2 | 39.7 | 5.2 | 27.6 | 1.5 | 155.3 | 34 | 0.093 | 27 |  | 7 | 0.042 | DGA is assessed as acceptable. | Breakdown voltage is low. Other oil quality results are assessed as acceptable. Corrosive IEC. Corrosive ASTM 4A.
33000 | 1967 | 44 | 249.6 | 30 | 98.1 | 1728.2 | 19.9 | 3.9 | 21.8 | 2.3 | 103.6 | 60 | 0.086 | 23 |  | 8 | 0.028 | DGA is assessed as acceptable. | Breakdown voltage is low. Other oil quality results are assessed as acceptable.
33000 | 1967 | 44 | 221 | 28 | 80.4 | 1661 | 19.7 | 3.6 | 20.7 | 1.6 | 95 | 59 | 0.085 | 18 |  | 4 | 0.058 | DGA is assessed as acceptable. | Breakdown voltage is low. Other oil quality results are assessed as acceptable at present.
33000 | 1967 | 44 | 221.5 | 41.81 | 90.6 | 1446 | 15.8 | 3.9 | 17.7 | 1.1 | 92.4 | 27 | 0.093 | 20 |  | 6 | 0.044 | DGA is assessed as acceptable. | Breakdown voltage is low. Other oil quality results are assessed as acceptable.
33000 | 1967 | 44 | 200 | 47 | 87.6 | 1556.7 | 14.1 | 3.1 | 16.2 | 1.2 | 77.8 | 66 | 0.081 | 18 |  | 8 | 0.03 | DGA is assessed as acceptable. | Breakdown voltage is low. Other oil quality results are assessed as acceptable.
33000 | 1967 | 44 | 193.8 | 42 | 99.2 | 1686.8 | 14.9 | 2.9 | 15.7 | 0 | 61.1 | 61 | 0.08 | 16 |  | 8 | 0.03 | DGA is assessed as acceptable. | Breakdown voltage is low. Other oil quality results are assessed as acceptable.
33000 | 1967 | 44 | 196.7 | 33 | 90.6 | 1450.2 | 21.5 | 2.8 | 15.2 | 0.7 | 65.9 | 31 | 0.077 | 29 |  | 7 | 0.032 | DGA is assessed as acceptable. | Breakdown voltage is low. Other oil quality results are assessed as acceptable.
33000 | 1967 | 44 | 317 | 31 | 247 | 1720 | 13 | 2 | 32 | 0 | 23 | 21 | 0.198 | 72 |  | 4 | 0.072 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1967 | 44 | 370 | 41.81 | 291 | 2038 | 13 | 4 | 26 | 0 | 36 | 27 | 0.183 | 66 |  | 3 | 0.073 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1967 | 44 | 557 | 41.81 | 455 | 2586 | 26 | 5 | 30 | 1 | 40 | 33 | 0.165 | 66 |  | 3.1 | 0.071 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1967 | 44 | 413 | 41.81 | 337 | 2364 | 7 | 3 | 27 | 1 | 38 | 29 | 0.202 | 58 |  | 3.1 | 0.08 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1967 | 44 | 56.2 | 41.81 | 39.1 | 1037.3 | 0 | 1 | 11 | 0.9 | 4.2 | 14 | 0.225 | 75 |  | 3 | 0.075 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1967 | 44 | 6.1 | 41.81 | 6 | 130 | 0 | 0.1 | 0 | 0 | 0 | 7 | 0.01 | 75 |  | 46 | 0.013 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1967 | 44 | 13.3 | 24 | 4.5 | 193.6 | 0 | 8.7 | 0.1 | 0 | 0 | 4 | 0.01 | 62 |  | 33 | 0.016 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1967 | 44 | 133.6 | 45 | 55.4 | 1320.7 | 21.6 | 3.3 | 4.9 | 4.5 | 43.9 | 10 | 0.01 | 55 |  | 10 | 0.035 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1967 | 44 | 224.3 | 40 | 79.7 | 1994.8 | 27 | 5.2 | 9.2 | 2.7 | 100.5 | 10 | 0.024 | 75 |  | 10 | 0.031 | DGA is assessed as acceptable. Acetylene gas possibly communicating from tapchanger. | Oil quality is assessed as acceptable.
33000 | 1967 | 44 | 175.3 | 38 | 44.9 | 1412.5 | 31 | 3.9 | 9.1 | 0.3 | 86.1 | 10 | 0.01 | 73 |  | 10 | 0.027 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1967 | 44 | 228 | 44 | 73.1 | 1820 | 20 | 4.8 | 14.4 | 0.3 | 115.4 | 15 | 0.012 | 73 |  | 8 | 0.036 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1967 | 44 | 339.8 | 40 | 185.5 | 3990.1 | 42 | 14.2 | 15.8 | 9.3 | 73 | 17 | 0.021 | 75 |  | 9 | 0.032 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable. Corrosive IEC. Corrosive ASTM 4A.
33000 | 1967 | 44 | 214.6 | 41 | 114.3 | 2518.8 | 32 | 4.6 | 11.2 | 5.3 | 47.2 | 17 | 0.029 | 68 |  | 8 | 0.031 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1967 | 44 | 357 | 45 | 268 | 1993 | 14 | 3 | 40 | 1 | 31 | 23 | 0.139 | 67.6 |  | 4 | 0.0645 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1967 | 44 | 680 | 32 | 548 | 4071 | 31 | 5 | 50 | 1 | 45 | 25 | 0.179 | 69 |  | 3.5 | 0.07 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1967 | 44 | 393 | 46 | 253 | 2428 | 30 | 4 | 34 | 1 | 71 | 35 | 0.188 | 66 |  | 3.6 | 0.06 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1967 | 44 | 642.6 | 42 | 504.7 | 8037.9 | 19.8 | 6.1 | 65 | 3.1 | 43.9 | 29 | 0.2 | 46 |  | 3 | 0.087 | DGA is assessed as acceptable.
33000 | 1967 | 44 | 586.2 | 32 | 491.3 | 5730.1 | 18.8 | 4.9 | 36.8 | 2.3 | 32.1 | 44 | 0.181 | 18 |  | 2 | 0.092 | DGA is assessed as acceptable. | Moisture content is high. Possible sample contamination.
33000 | 1967 | 44 | 618.4 | 40 | 485.2 | 5684.4 | 32.3 | 6.4 | 42.2 | 3 | 49.3 | 39 | 0.201 | 21 |  | 2.5 | 0.0905 | DGA is assessed as acceptable. | Moisture content is high. Breakdown voltage is low.
33000 | 1967 | 44 | 448.6 | 33 | 388.5 | 5369.4 | 13.4 | 3.9 | 27.2 | 0.7 | 14.9 | 50 | 0.2 | 19 |  | 2 | 0.1049 | DGA is assessed as acceptable. | Breakdown voltage is low. Moisture content is high. Acidity level is high. Other oil quality results are assessed as acceptable.
33000 | 1967 | 44 | 474.2 | 35 | 394.1 | 5539.7 | 19.3 | 3.9 | 31.2 | 1.4 | 24.3 | 48 | 0.345 | 10 |  | 2 | 0.0874 | DGA is assessed as acceptable. | Oil quality is poor.
33000 | 1967 | 44 | 353.6 | 48 | 293.1 | 4417.9 | 6.9 | 2.9 | 24.8 | 1.2 | 24.7 | 32 | 0.224 | 35 |  | 3 | 0.086 | DGA is assessed as acceptable. | Acidity level is high. Breakdown voltage is low. DDF and Resistivity are assessed as acceptable. Corrosive IEC. Corrosive ASTM 4A.
33000 | 1967 | 44 | 210.7 | 43 | 175 | 2467.5 | 4.6 | 2 | 15.1 | 1.2 | 12.8 | 27 | 0.216 | 19 |  | 3 | 0.075 | DGA is assessed as acceptable. | Acidity level is high. Breakdown voltage is low. DDF and Resistivity assessed as acceptable.
33000 | 1967 | 44 | 202.9 | 40 | 178.5 | 2901.8 | 3.8 | 1.4 | 12.2 | 0.7 | 6.3 | 62 | 0.231 | 15 |  | 4 | 0.056 | DGA is assessed as acceptable. | Acidity level is high. Other oil quality results are assessed as acceptable.
33000 | 1967 | 44 | 235 | 62 | 176.9 | 2919.3 | 12.6 | 9.7 | 13.5 | 0.3 | 22 | 87 | 0.214 | 12 |  | 3 | 0.071 | DGA is assessed as acceptable. | Oil quality is poor. Oil is cloudy in appearance.
33000 | 1967 | 44 | 663 | 41.81 | 534 | 5675 | 40 | 8 | 37 | 2 | 42 | 14 | 0.088 | 68 |  | 9 | 0.035 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1967 | 44 | 396 | 41.81 | 292 | 1909 | 29 | 4 | 27 | 1 | 43 | 35 | 0.102 | 63 |  | 4.4 | 0.046 | Moisture content of oil slightly high. Otherwise test results satisfactory. Acetylene gas possibly from tapchanger.
33000 | 1967 | 44 | 294 | 41.81 | 237 | 2439 | 18 | 3 | 7 | 1 | 28 | 36 | 0.167 | 32 |  | 4.5 | 0.052 | DGA satisfactory. | Moisture content is high.
33000 | 1967 | 44 | 368 | 41.81 | 286 | 2501 | 17 | 5 | 6 | 1 | 53 | 18 | 0.164 | 45 |  | 5.2 | 0.052 | Test results satisfactory. | Oil quality is assessed as acceptable.
33000 | 1967 | 44 | 676 | 41.81 | 507 | 4246 | 49 | 8 | 12 | 4 | 96 | 37 | 0.189 | 62 |  | 5 | 0.049 | DGA is assessed as acceptable. | Moisture content of oil is high. Other test results are assessed as acceptable.
33000 | 1967 | 44 | 657 | 41.81 | 506 | 5232 | 43 | 3 | 12 | 1 | 92 | 40 | 0.181 | 29 |  | 5.4 | 0.042 | DGA is assessed as acceptable. | Moisture content of oil is high. Other test results are assessed as acceptable.
33000 | 1967 | 44 | 219.7 | 48 | 132.3 | 1687.9 | 12.9 | 3.6 | 9.1 | 4.7 | 57.1 | 36 | 0.175 | 30 |  | 4 | 0.058 | DGA is assessed as acceptable. | Moisture content of sample is high. Other test results are assessed as acceptable.
33000 | 1967 | 44 | 220.7 | 50 | 140.5 | 2080 | 14.2 | 3.7 | 7.3 | 3 | 52 | 46 | 0.165 | 25 |  | 4 | 0.061 | Dissolved gas analysis is assessed as acceptable. Acetylene gas possibly from tapchanger. | Breakdown voltage of sample is low. Moisture content of sample is high.
33000 | 1967 | 44 | 160 | 40 | 110.8 | 1786.2 | 15.9 | 2.6 | 5.4 | 1.5 | 23.8 | 57 | 0.149 | 17 |  | 4 | 0.064 | DGA is assessed as acceptable. | Moisture content is high. Breakdown voltage is low. Possible sample contamination. Other oil quality results are assessed as acceptable.
33000 | 1967 | 44 | 189.3 | 38 | 128.4 | 1392.3 | 17.2 | 3.2 | 7.2 | 0.8 | 32.5 | 57 | 0.138 | 20 |  | 4 | 0.064 | DGA is assessed as acceptable. | Moisture content is high. Breakdown voltage is low. Oil is cloudy in appearance. Other oil quality results are assessed as acceptable at present.
33000 | 1967 | 44 | 146.1 | 43 | 89.1 | 1814.2 | 12.3 | 2.7 | 8.5 | 0.6 | 32.9 | 37 | 0.135 | 16 |  | 4 | 0.049 | DGA is assessed as acceptable. | Moisture content is high. Breakdown voltage is low. Other oil quality results are assessed as acceptable.
33000 | 1967 | 44 | 340 | 41.81 | 299 | 2564 | 0 | 4 | 7 | 2 | 28 | 27 | 0.211 | 56 |  | 70 | 0.0335 | Test results satisfactory. | Oil quality is assessed as acceptable.
33000 | 1967 | 44 | 326 | 41.81 | 218 | 2341 | 41 | 4 | 10 | 1 | 52 | 21 | 0.136 | 48 |  | 4.8 | 0.059 | Test results satisfactory. | Oil quality is assessed as acceptable.
33000 | 1967 | 44 | 738 | 41.81 | 560 | 4252 | 51 | 8 | 15 | 2 | 102 | 35 | 0.16 | 32 |  | 4.5 | 0.047 | DGA is assessed as acceptable. | Moisture content of oil is slightly high. Other test results are assessed as acceptable.
33000 | 1967 | 44 | 270.8 | 40 | 185.4 | 2252.8 | 17.1 | 4.2 | 10 | 3.5 | 50.6 | 56 | 0.179 | 28 |  | 3 | 0.078 | DGA is assessed as acceptable. | Moisture content of oil is high. Breakdown voltage of sample is low. Other test results are assessed as acceptable.
33000 | 1967 | 44 | 259.8 | 50 | 184.2 | 2390 | 20.1 | 3.9 | 7.9 | 0.8 | 42.9 | 49 | 0.147 | 21 |  | 3 | 0.07 | DGA is assessed as acceptable. | Moisture content of sample is high. Breakdown voltage of sample is low.
33000 | 1967 | 44 | 188.6 | 41 | 138 | 2073 | 17 | 2.8 | 3.6 | 1.4 | 25.8 | 51 | 0.121 | 22 |  | 4 | 0.064 | DGA is assessed as acceptable. | Moisture content is high. Breakdown voltage is low. Possible sample contamination. Other oil quality results are assessed as acceptable.
33000 | 1967 | 44 | 203.4 | 38 | 142.7 | 1428 | 18.1 | 3 | 4.5 | 0.5 | 34.6 | 62 | 0.139 | 24 |  | 4 | 0.056 | DGA is assessed as acceptable. | Moisture content is high. Breakdown voltage is low. Oil is cloudy in appearance. Other oil quality results are assessed as acceptable.
33000 | 1967 | 44 | 144.9 | 43 | 85.6 | 1436.5 | 13.5 | 2.8 | 5.7 | 0.5 | 36.8 | 37 | 0.102 | 24 |  | 4 | 0.058 | DGA is assessed as acceptable. | Moisture content is high. Breakdown voltage is low. Other oil quality results are assessed as acceptable.
33000 | 1967 | 44 | 91 | 45 | 86 | 1528 | 0 | 1 | 3 | 1 | 0 | 14 | 0.18 | 59 |  | 6 | 0.044 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1967 | 44 | 139 | 52 | 112 | 1417 | 0 | 10 | 1 | 16 | 0 | 35 | 0.186 | 54 |  | 3.3 | 0.087 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1967 | 44 | 80 | 41.81 | 74 | 1431 | 0 | 2 | 3 | 1 | 0 | 39 | 0.162 | 29 |  | 4.5 | 0.048 | DGA is assessed as acceptable. | Moisture content is high. Breakdown voltage is low. Possible sample contamination.
33000 | 1967 | 44 | 292.4 | 54 | 260.2 | 2389.2 | 9.9 | 4.5 | 12.2 | 4.9 | 0.7 | 58 | 0.222 | 14 |  | 4 | 0.062 | DGA is assessed as acceptable. | Breakdown voltage of oil is low. Moisture and acidity levels of oil are high.
33000 | 1967 | 44 | 315.9 | 33 | 191.8 | 2339.3 | 112.7 | 2.9 | 6.2 | 2 | 0.3 | 32 | 0.222 | 25 |  | 3 | 0.067 | DGA is assessed as acceptable. | Breakdown voltage of sample is low. Moisture content of sample is high. Acidity level of sample is high but stable. Other test results are assessed as acceptable.
33000 | 1967 | 44 | 235 | 39 | 212.9 | 2747.6 | 11 | 2.6 | 6.5 | 2 | 0 | 70 | 0.235 | 15 |  | 3 | 0.083 | DGA is assessed as acceptable. | Acidity level of sample is high but stable. Breakdown voltage of sample is low. Moisture content of sample is very high. Possible sample contamination.
33000 | 1967 | 44 | 467.2 | 48 | 434.7 | 4057.7 | 22.2 | 3.3 | 6.2 | 0.8 | 0 | 41 | 0.237 | 37 |  | 3 | 0.072 | DGA is assessed as acceptable. | Moisture content is high. Acidity level is high but stable.
33000 | 1967 | 44 | 279.9 | 50 | 259.7 | 3111.3 | 14.5 | 1.7 | 4 | 0 | 0 | 36 | 0.235 | 75 |  | 3 | 0.084 | DGA is assessed as acceptable. | Acidity level is high but stable. Moisture content is high. Other oil quality results are assessed as acceptable.
33000 | 1967 | 44 | 252.6 | 48 | 237.2 | 2703 | 9.3 | 2.1 | 3.2 | 0.8 | 0 | 34 | 0.245 | 34 |  | 3 | 0.081 | DGA is assessed as acceptable. | Moisture content is consistently high. Acidity level is high but stable. Other oil quality results are assessed as acceptable.
33000 | 1967 | 44 | 226.3 | 55 | 202.8 | 2941.3 | 13.2 | 2 | 6.6 | 1.7 | 0 | 36 | 0.298 | 35 |  | 3 | 0.08 | DGA is assessed as acceptable. | Breakdown voltage is low. Acidity level is high. DDF and Resistivity are assessed as acceptable.
33000 | 1967 | 44 | 247.8 | 57 | 212.6 | 2523.6 | 11.2 | 2 | 17.4 | 4.6 | 0 | 36 | 0.271 | 29 |  | 4 | 0.059 | DGA is assessed as acceptable. | Oil quality is poor.
33000 | 1967 | 44 | 197.6 | 46 | 180.4 | 2569.2 | 10.5 | 2.1 | 3.8 | 0.8 | 0 | 39 | 0.276 | 25 |  | 3 | 0.073 | DGA is assessed as acceptable. | Oil quality is poor.
33000 | 1967 | 44 | 319 | 50 | 279 | 2942 | 30 | 3 | 4 | 1 | 2 | 52 | 0.162 | 36 |  | 9 | 0.035 | DGA is assessed as acceptable.
33000 | 1967 | 44 | 223 | 42 | 215 | 1966 | 0 | 2 | 3 | 1 | 2 | 23 | 0.158 | 52 |  | 7 | 0.04 | DGA is assessed as acceptable.
33000 | 1967 | 44 | 200 | 50 | 195 | 2128 | 0 | 2 | 2 | 1 | 0 | 48 | 0.179 | 29 |  | 5.9 | 0.051 | DGA is assessed as acceptable.
33000 | 1967 | 44 | 249 | 35 | 236 | 4046 | 7 | 2 | 3 | 1 | 0 | 45 | 0.181 | 16 |  | 5.4 | 0.048 | DGA is assessed as acceptable.
33000 | 1967 | 44 | 0 | 50 | 0 | 130 | 0 | 0 | 0 | 0 | 0 | 14 | 0.011 | 75 |  | 21.2 | 0.029 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1967 | 44 | 24 | 50 | 19 | 444 | 0 | 1 | 1 | 3 | 0 | 13 | 0.011 | 70 |  | 22.9 | 0.029 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1967 | 44 | 125.3 | 40 | 87.1 | 2949.3 | 7.7 | 1.3 | 28.2 | 1 | 0 | 21 | 0.017 | 16 |  | 40 | 0.01 | DGA is assessed as acceptable. | Breakdown voltage of sample is low. Other test results are assessed as acceptable.
33000 | 1967 | 44 | 141.9 | 39 | 121.4 | 1714.5 | 2.6 | 1.3 | 16.2 | 0.4 | 0 | 15 | 0.022 | 34 |  | 16 | 0.026 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1967 | 44 | 133.9 | 44 | 115 | 1826.9 | 5.9 | 1.3 | 11.7 | 0 | 0 | 38 | 0.015 | 24 |  | 27 | 0.012 | DGA is assessed as acceptable. | Moisture content is high. Breakdown voltage is low. Other oil quality results are assessed as acceptable.Possible sample contamination.
33000 | 1967 | 44 | 133.2 | 40 | 116.7 | 1780.5 | 3.2 | 1.4 | 11.8 | 0.1 | 0 | 18 | 0.021 | 37 |  | 20 | 0.018 | DGA is assessed as acceptable. | Breakdown voltage is low. Other oil quality results are assessed as acceptable. Corrosive IEC. Non-corrosive ASTM 3A.
33000 | 1967 | 44 | 142.8 | 54 | 121 | 1874.5 | 5.5 | 2.1 | 14.2 | 0 | 0 | 20 | 0.021 | 80 |  | 15 | 0.024 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1967 | 44 | 137.1 | 74 | 112.9 | 2573.9 | 9.4 | 1.6 | 12.9 | 0.3 | 0 | 28 | 0.019 | 43 |  | 17 | 0.024 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1967 | 44 | 221 | 48 | 165 | 1878 | 50 | 2 | 2 | 2 | 0 | 30 | 0.141 | 53 |  | 10 | 0.024 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1967 | 44 | 172 | 42 | 146 | 1991 | 18 | 2 | 4 | 1 | 1 | 44 | 0.161 | 47 |  | 9 | 0.026 | Test results satisfactory. Though moisture content of sample slightly high.
33000 | 1967 | 44 | 197 | 30 | 183 | 1671 | 0 | 2 | 6 | 6 | 0 | 47 | 0.193 | 26 |  | 4.7 | 0.045 | Moisture content of oil high. Other test results satisfactory.
33000 | 1967 | 44 | 206 | 34 | 163 | 2028 | 7 | 2 | 14 | 20 | 0 | 46 | 0.227 | 64 |  | 6.5 | 0.037 | Acidity and moisture levels are high. Other results are assessed as acceptable.
33000 | 1967 | 44 | 165 | 38 | 152 | 1835 | 7 | 1 | 4 | 1 | 0 | 28 | 0.211 | 24 |  | 3.9 | 0.065 | Acidity level of oil is high. Other results are assessed as acceptable.
33000 | 1967 | 44 | 461.6 | 45 | 385 | 3830.7 | 42 | 4.3 | 19.6 | 10.7 | 0 | 66 | 0.268 | 20 |  | 2.9871 | 0.08283 | Moisture content of sample is high. Breakdown voltage of sample is low. Acidity level of sample is high. Other test results are assessed as acceptable. RECOMMEND OIL CHANGE/TREATMENT. RECOMMEND RESAMPLE IN 1 YEAR TO MONITOR TREND.
33000 | 1967 | 44 | 303.3 | 32 | 272.3 | 3161.5 | 18.6 | 2.5 | 5.2 | 2.3 | 2.4 | 52 | 0.257 | 21 |  | 4 | 0.062 | Moisture content of sample is very high. Breakdown voltage of sample is low. Acidity level is trending upwards. Dissolved gas analysis is assessed as acceptable. RECOMMEND OIL CHANGE / TREATMENT.
33000 | 1967 | 44 | 607.8 | 41.81 | 19.3 | 1639.3 | 35.1 | 2.9 | 73.6 | 7.5 | 469.4 | 19 | 0.042 | 57 |  | 16 | 0.016 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1967 | 44 | 55 | 41.81 | 48.9 | 2015.7 | 2.8 | 1.2 | 1.8 | 0.3 | 0 | 24 | 0.268 | 44 |  | 4 | 0.052 | DGA is assessed as acceptable. | Acidity level is high. Other oil quality results are assessed as acceptable.
33000 | 1967 | 44 | 15.3 | 41.81 | 13 | 197 | 2 | 0.3 | 0 | 0 | 0 | 8 | 0.034 | 71 |  | 9 | 0.034 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1967 | 44 | 25.7 | 28 | 23 | 337 | 0 | 0.7 | 2 | 0 | 0 | 18 | 0.04 | 75 |  | 7 | 0.04 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1967 | 44 | 16.8 | 28 | 14 | 573 | 0 | 0.8 | 0 | 0 | 2 | 24 | 0.016 | 34 |  | 16 | 0.025 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1967 | 44 | 30.8 | 36 | 22.7 | 585.7 | 3.6 | 1.1 | 0.5 | 2.9 | 0 | 6 | 0.04 | 75 |  | 5 | 0.051 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1967 | 44 | 96.6 | 25 | 80.3 | 752 | 5.9 | 7.1 | 0.8 | 2.5 | 0 | 3 | 0.029 | 75 |  | 5 | 0.063 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable. Corrosive IEC. Corrosive ASTM 4A.
33000 | 1967 | 44 | 49.6 | 42 | 47.6 | 874.5 | 0 | 0.5 | 1 | 0.3 | 0.2 | 8 | 0.032 | 75 |  | 4 | 0.069 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable. Corrosive IEC. Corrosive ASTM 4A.
33000 | 1967 | 44 | 49.4 | 38 | 35.5 | 900.1 | 11.4 | 1.1 | 0.9 | 0.5 | 0 | 11 | 0.032 | 52 |  | 4 | 0.068 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1967 | 44 | 1594 | 56 | 1503 | 2802 | 84 | 3 | 3 | 1 | 0 | 52 | 0.164 | 31 |  | 7 | 0.035 | Level of CO and Moisture quite high. | Moisture content is high.
33000 | 1967 | 44 | 484 | 53 | 414 | 3723 | 60 | 5 | 4 | 1 | 0 | 127 | 0.181 | 32 |  | 5.3 | 0.045 | DGA satisfactory. | Moisture in sample extremely high. Possible sample contamination ?
33000 | 1967 | 44 | 609 | 52 | 469 | 3040 | 99 | 6 | 4 | 1 | 30 | 56 | 0.194 | 27 |  | 6.1 | 0.042 | Acetylene gas possibly from tapchanger. DGA is assessed as acceptable. | Moisture content of oil high. Breakdown low. Other test results satisfactory.
33000 | 1967 | 44 | 590 | 41.81 | 499 | 4118 | 81 | 3 | 5 | 1 | 1 | 70 | 0.228 | 25 |  | 4.8 | 0.043 | DGA is assessed as acceptable. | Moisture content of oil is very high; dielectric strength low. Other test results are assessed as acceptable.
33000 | 1967 | 44 | 52 | 56 | 46 | 531 | 5 | 1 | 0 | 0 | 0 | 40 | 0.254 | 71 |  | 5.5 | 0.041 | DGA is assessed as acceptable. | Moisture content of oil high. Other test results are assessed as acceptable.
33000 | 1967 | 44 | 727 | 43 | 457.6 | 3513.5 | 250.8 | 10.8 | 6 | 1.8 | 0 | 26 | 0.258 | 28 |  | 3 | 0.078 | DGA is assessed as acceptable. | Breakdown voltage of oil is low. Acidity level of oil is high. Other test results are assessed as acceptable.
33000 | 1967 | 44 | 877.5 | 38 | 511.1 | 6105.1 | 346.2 | 11.6 | 7 | 1.6 | 0 | 45 | 0.292 | 24 |  | 1 | 0.194 | Dissolved gas analysis is assessed as acceptable. | Moisture content of sample is high. Oil appearred cloudy. Breakdown voltage of sample is low. Acidity level of sample is high. Dielectric Dissipation Factor (DDF) and Resistivity are on acceptance limits.
33000 | 1967 | 44 | 989.4 | 46 | 737 | 6833.9 | 232.6 | 12.1 | 6.1 | 1.6 | 0 | 70 | 0.274 | 20 |  | 3 | 0.068 | DGA is assessed as acceptable. | Moisture content is high. Sample appears cloudy. Breakdown voltage is low. Acidity level is high.
33000 | 1967 | 44 | 1078.5 | 44 | 746 | 6839.3 | 301.9 | 19.8 | 8.8 | 1.9 | 0.1 | 88 | 0.284 | 36 |  | 2 | 0.113 | DGA is assessed as acceptable. | Oil quality is poor.
33000 | 1967 | 44 | 691.6 | 42 | 570.8 | 6941.5 | 106.4 | 7.4 | 5.7 | 1.3 | 0 | 64 | 0.302 | 19 |  | 3 | 0.068 | DGA is assessed as acceptable. | Oil quality is poor.
33000 | 1967 | 44 | 755.8 | 22 | 582.1 | 6066.9 | 157.8 | 8.9 | 5.8 | 1.2 | 0 | 46 | 0.301 | 29 |  | 3 | 0.092 | DGA is assessed as acceptable. | Acidity level is high. Moisture content is high. Breakdown voltage is low. Other oil quality results are assessed as acceptable.
33000 | 1967 | 44 | 689.8 | 37 | 614.5 | 6370.6 | 62.8 | 6 | 5.5 | 1 | 0 | 36 | 0.348 | 24 |  | 3 | 0.066 | DGA is assessed as acceptable. | Acidity level is high. Breakdown voltage is low. Moisture content is high.
33000 | 1967 | 44 | 1284.4 | 38 | 972.5 | 11722.2 | 283.6 | 14.1 | 11.9 | 2.3 | 0 | 46 | 0.359 | 30 |  | 2 | 0.143 | Carbon dioxide level is high. | Oil quality is poor.
33000 | 1967 | 44 | 2394.9 | 42 | 581.1 | 11581.1 | 1721.1 | 64 | 23.3 | 5.4 | 0 | 52 | 0.365 | 24 |  | 2 | 0.124 | Carbon dioxide and hydrogen levels are high. DGA suggests partial discharge has occurred. | Oil quality is poor. Oil is cloudy in appearance.
33000 | 1967 | 44 | 582 | 40 | 500 | 3556 | 73 | 3 | 4 | 2 | 0 | 49 | 0.129 | 30 |  | 10 | 0.036 | DGA is assessed as acceptable. | Moisture level quite high. Possible contaminated sample? Other results satisfactory.
33000 | 1967 | 44 | 418 | 73 | 361 | 2339 | 49 | 3 | 4 | 1 | 0 | 8 | 0.143 | 24 |  | 5.9 | 0.042 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1967 | 44 | 575 | 72 | 511 | 2868 | 56 | 3 | 4 | 1 | 0 | 21 | 0.153 | 39 |  | 5.8 | 0.042 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable. PCB contaminated oil.
33000 | 1967 | 44 | 329 | 41.81 | 295 | 2398 | 28 | 2 | 3 | 1 | 0 | 63 | 0.173 | 16 |  | 6 | 0.039 | DGA is assessed as acceptable. | Moisture content of oil very high. Dielectric strength low; possibly sample contamination. Other test results are assessed as acceptable. PCB contaminated oil.
33000 | 1967 | 44 | 465.7 | 43 | 410.5 | 3334.4 | 47.2 | 3.2 | 3.3 | 1.5 | 0 | 37 | 0.194 | 20 |  | 4 | 0.062 | Dissolved gas analysis is assessed as acceptable. | Oil quality is poor.
33000 | 1967 | 44 | 1294.3 | 48 | 553.3 | 5857.4 | 713.5 | 16.7 | 7.5 | 3.3 | 0 | 53 | 0.2 | 12 |  | 2 | 0.103 | Hydrogen level is high. Other dissolved gas levels are assessed as acceptable. | Moisture content is high. Sample appears cloudy. Breakdown voltage is low. Acidity level is high.
33000 | 1967 | 44 | 778.9 | 44 | 575.3 | 5367.8 | 189.7 | 7.1 | 5 | 1.8 | 0 | 46 | 0.204 | 33 |  | 3 | 0.073 | DGA is assessed as acceptable. | Oil quality is poor.
33000 | 1967 | 44 | 821.4 | 54 | 556.7 | 5266 | 248.2 | 7.5 | 7.4 | 1.6 | 0 | 42 | 0.252 | 29 |  | 2 | 0.106 | DGA is assessed as acceptable | Oil quality is poor.
33000 | 1967 | 44 | 799.2 | 48 | 625.7 | 5143.6 | 161.1 | 5.9 | 5 | 1.5 | 0 | 41 | 0.269 | 33 |  | 3 | 0.066 | DGA is assessed as acceptable. | Acidity level is high. Breakdown voltage is low. Other oil quality results are assessed as acceptable.
33000 | 1967 | 44 | 703 | 50 | 565.4 | 5356.4 | 126.3 | 5.8 | 4.5 | 1 | 0 | 30 | 0.266 | 64 |  | 4 | 0.061 | DGA is assessed as acceptable. | Acidity level is high. Other oil quality results are assessed as acceptable. Corrosive IEC. Corrosive ASTM 4A.
33000 | 1967 | 44 | 696.9 | 65 | 502 | 4120.9 | 179 | 8.7 | 6.4 | 0.8 | 0 | 76 | 0.245 | 24 |  | 2 | 0.092 | DGA is assessed as acceptable. | Breakdown voltage is low. Other oil quality results are assessed as acceptable.
33000 | 1967 | 44 | 763.9 | 46 | 588.5 | 5469.3 | 160.6 | 6.3 | 6.3 | 2.2 | 0 | 99 | 0.271 | 20 |  | 3 | 0.081 | DGA is assessed as acceptable. | Acidity level is high. Breakdown voltage is low. Oil is cloudy in appearance. DDF and Resistivity are assessed as acceptable.
33000 | 1967 | 44 | 737.7 | 61 | 621.1 | 6221.4 | 105.1 | 5.2 | 5 | 1.3 | 0 | 36 | 0.275 | 62 |  | 3 | 0.065 | DGA is assessed as acceptable. | Acidity level is high. Other oil quality results are assessed as acceptable.
33000 | 1967 | 44 | 744.4 | 48 | 529.6 | 4694.3 | 202.3 | 6.8 | 4.5 | 1.2 | 0 | 36 | 0.279 | 37 |  | 3 | 0.077 | DGA is assessed as acceptable. | Acidity level is high. Breakdown voltage is low. DDF and Resistivity are assessed as acceptable.
33000 | 1967 | 44 | 816.3 | 48 | 510.7 | 4507.7 | 292 | 7.8 | 4.9 | 0.9 | 0 | 45 | 0.278 | 30 |  | 3 | 0.077 | DGA is assessed as acceptable. | Oil quality is poor.
33000 | 1966 | 45 | 795 | 41.81 | 362 | 4189 | 152 | 52 | 69 | 5 | 155 | 56 | 0.2 | 40 |  | 6.5 | 0.0347 | Gases indicate arcing taking place. No indication of major insulation damage.
33000 | 1966 | 45 | 1239 | 41.81 | 740 | 6015 | 193 | 47 | 90 | 26 | 143 | 80 | 0.22 | 17 |  | 6 | 0.0435 | Gases indicate arcing taking place. No indication of major insulation damage.
33000 | 1966 | 45 | 92 | 41.81 | 65 | 926 | 0 | 1 | 24 | 1 | 1 | 12 | 0.021 | 55 |  | 35.1 | 0.015 | Test results satisfactory.
33000 | 1966 | 45 | 127 | 41.81 | 105 | 1039 | 0 | 1 | 21 | 0 | 0 | 12 | 0.028 | 69 |  | 20.9 | 0.022 | Test results are assessed as acceptable.
33000 | 1966 | 45 | 185.9 | 43 | 151.2 | 1374 | 0 | 1.4 | 32.7 | 0.6 | 0 | 9 | 0.024 | 75 |  | 11 | 0.029 | The test results are assessed as acceptable.
33000 | 1966 | 45 | 181.6 | 40 | 153.2 | 1557.9 | 0 | 4.2 | 24.2 | 0 | 0 | 10 | 0.0245 | 75 |  | 12 | 0.025 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1966 | 45 | 210.8 | 41.81 | 160.2 | 1335 | 26.9 | 1.3 | 21.8 | 0.4 | 0.2 | 10 | 0.036 | 75 |  | 13 | 0.023 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1966 | 45 | 173.4 | 35 | 135.9 | 1247.2 | 4.7 | 5.4 | 26.8 | 0.6 | 0 | 9 | 0.034 | 47 |  | 11 | 0.03 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable. Corrosive IEC. Non-corrosive ASTM 3A.
33000 | 1966 | 45 | 187.9 | 45 | 163.9 | 1315.9 | 2.3 | 1.1 | 20.6 | 0 | 0 | 10 | 0.034 | 75 |  | 12 | 0.027 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable. Corrosive IEC. Non-corrosive ASTM 3B.
33000 | 1966 | 45 | 156.1 | 23 | 137.3 | 1257.9 | 0 | 1 | 17.8 | 0 | 0 | 10 | 0.038 | 70 |  | 10 | 0.028 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1966 | 45 | 152.4 | 42 | 130.6 | 1198.3 | 1.8 | 2.1 | 17.3 | 0.6 | 0 | 11 | 0.039 | 70 |  | 11 | 0.024 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1966 | 45 | 14 | 41.81 | 7 | 697 | 0 | 1 | 6 | 0 | 0 | 10 | 0.033 | 64 |  | 19.8 | 0.019 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1966 | 45 | 243 | 58 | 221 | 2515 | 1 | 2 | 19 | 0 | 0 | 20 | 0.032 | 59 |  | 16.1 | 0.023 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1966 | 45 | 289.9 | 52 | 246.8 | 2452.4 | 3.9 | 2.3 | 35.8 | 1 | 0.1 | 20 | 0.035 | 68 |  | 6 | 0.056 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1966 | 45 | 267.9 | 25 | 221 | 2830.3 | 11 | 2.4 | 32.4 | 0.7 | 0.4 | 8 | 0.035 | 75 |  | 11 | 0.03 | The test results are assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1966 | 45 | 84.4 | 41.81 | 79.8 | 1007.3 | 2 | 1.2 | 0.6 | 0.4 | 0.4 | 11 | 0.01 | 75 |  | 18 | 0.023 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1966 | 45 | 1.3 | 20 | 1.2 | 88.7 | 0 | 0.1 | 0 | 0 | 0 | 6 | 0.01 | 67 |  | 12 | 0.024 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1966 | 45 | 7.1 | 20 | 3 | 241 | 0 | 0.6 | 0.2 | 0.3 | 3 | 13 | 0.01 | 75 |  | 250 | 0.005 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1966 | 45 | 1.4 | 22 | 1.2 | 115.6 | 0 | 0.2 | 0 | 0 | 0 | 10 | 0 | 71 |  | 21 | 0.019 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1966 | 45 | 9.4 | 22 | 2.7 | 257.5 | 0 | 0.8 | 0.8 | 0.6 | 4.5 | 14 | 0 | 58 |  | 227 | 0.004 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1966 | 45 | 67 | 50 | 62.3 | 1136.9 | 2.8 | 1.3 | 0.6 | 0 | 0 | 15 | 0.01 | 71 |  | 12 | 0.034 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1966 | 45 | 95 | 43 | 88.3 | 1399 | 4 | 1.4 | 0.7 | 0.6 | 0 | 13 | 0.01 | 72 |  | 13 | 0.027 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1966 | 45 | 49.1 | 56 | 44 | 1225 | 2 | 1.4 | 1 | 0.7 | 0 | 15 | 0.001 | 69 |  | 14 | 0.023 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable. Corrosive IEC. Corrosive ASTM 4A.
33000 | 1966 | 45 | 29.9 | 40 | 25.4 | 818.2 | 0 | 2.6 | 1.1 | 0.8 | 0 | 9 | 0.004 | 67 |  | 10 | 0.028 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable. Corrosive IEC. Corrosive ASTM 4A.
33000 | 1966 | 45 | 48 | 20 | 45 | 584 | 0 | 0 | 2 | 0 | 1 | 8 | 0.013 | 65 |  | 30 | 0.0267 | Test results satisfactory.
33000 | 1966 | 45 | 135 | 43 | 116 | 1417 | 0 | 1 | 18 | 0 | 0 | 34 | 0.028 | 33 |  | 24.7 | 0.021 | Test results satisfactory.
33000 | 1966 | 45 | 102 | 38 | 84 | 1395 | 0 | 1 | 17 | 0 | 0 | 20 | 0.038 | 63 |  | 15.3 | 0.027 | Test results satisfactory.
33000 | 1966 | 45 | 164 | 41.81 | 143 | 2229 | 0 | 1 | 19 | 0 | 1 | 19 | 0.032 | 58 |  | 12.8 | 0.021 | Test results satisfactory.
33000 | 1966 | 45 | 226 | 46 | 205 | 2378 | 0 | 2 | 18 | 1 | 0 | 26 | 0.034 | 53 |  | 11.3 | 0.029 | Test results are assessed as acceptable.
33000 | 1966 | 45 | 576.2 | 52 | 521 | 7360 | 8 | 4 | 42 | 1 | 0.2 | 24 | 0.063 | 27 |  | 8 | 0.032 | Breakdown voltage of sample is low. Carbon dioxide level is high. 2-furfural level is very high suggesting accelerated rate of insulation degradation. Other test results are assessed as acceptable. RECOMMEND RESAMPLE IN 1 YEAR TO MONITOR CONDITION.
33000 | 1966 | 45 | 191 | 50 | 147 | 1371 | 0 | 0 | 43 | 0 | 1 | 11 | 0.068 | 49 |  | 13 | 0.0235 | Test results satisfactory.
33000 | 1966 | 45 | 553 | 41.81 | 370 | 2923 | 8 | 4 | 56 | 1 | 114 | 21 | 0.061 | 40 |  | 7.8 | 0.031 | Test results satisfactory. Acetylene gas possibly from tapchanger.
33000 | 1966 | 45 | 163 | 41.81 | 30 | 1026 | 0 | 2 | 30 | 1 | 100 | 11 | 0.081 | 48 |  | 7.2 | 0.036 | Test results satisfactory. Acetylene gas possibly from tapchanger.
33000 | 1966 | 45 | 131 | 41.81 | 44 | 906 | 0 | 1 | 23 | 1 | 62 | 13 | 0.081 | 37 |  | 7.1 | 0.034 | Test results satisfactory.
33000 | 1966 | 45 | 46 | 40 | 39 | 1478 | 0 | 1 | 4 | 1 | 1 | 9 | 0.014 | 75 |  | 86.9 | 0.006 | Test results are assessed as acceptable. Has transformer oil been changed/treated?
33000 | 1966 | 45 | 762.2 | 58 | 94.9 | 2206.3 | 19.6 | 100 | 455.8 | 85.9 | 6 | 20 | 0.01 | 48 |  | 59 | 0.006 | Dissolved gas analysis suggests high temperature oil overheating has occurred. Other test results are assessed as acceptable. RECOMMEND RESAMPLE IN 1 MONTH TO MONITOR TREND.
33000 | 1966 | 45 | 683.6 | 33 | 83.2 | 2393.9 | 19.8 | 74.5 | 422.8 | 79.1 | 4.2 | 10 | 0.01 | 75 |  | 42 | 0.009 | Dissolved gas analysis is consistent with sample taken 26.11.02. Dissolved gas analysis suggests high temperature oil overheating has occurred. Other test results are assessed as acceptable. RECOMMEND RESAMPLE IN 3 MONTHS TO MONITOR TREND.
33000 | 1966 | 45 | 584.7 | 48 | 162.8 | 3089.4 | 16.9 | 47.5 | 295 | 59.3 | 3.2 | 14 | 0.01 | 68 |  | 54 | 0.006 | Dissolved hydrocarbon gas levels are reduced. Other test results are assessed as acceptable. RECOMMEND RESAMPLE IN 1 YEAR TO MONITOR TREND.
33000 | 1966 | 45 | 495.9 | 40 | 121 | 2562.3 | 13.6 | 51.4 | 256.9 | 49.2 | 3.8 | 11 | 0.01 | 68 |  | 49.9 | 0.008 | Dissolved gas levels are relatively stable. | Oil quality is assessed as acceptable.
33000 | 1966 | 45 | 524.3 | 46 | 100.1 | 2272 | 42.4 | 55.8 | 274.8 | 46.6 | 4.6 | 11 | 0.01 | 71 |  | 42 | 0.007 | Dissolved gas levels are relatively stable. | Oil quality is assessed as acceptable.
33000 | 1966 | 45 | 141.6 | 35 | 32.4 | 782.8 | 3 | 17.2 | 74 | 13.9 | 1.1 | 9 | 0.01 | 43 |  | 44 | 0.008 | Dissolved gas levels are reduced. DGA is assessed as acceptable at present. | Oil quality is assessed as acceptable. Corrosive IEC. Corrosive ASTM 4A.
33000 | 1966 | 45 | 187.8 | 23 | 39.6 | 1021.6 | 0 | 11.1 | 113.1 | 23.3 | 0.7 | 10 | 0.005 | 76 |  | 39 | 0.01 | DGA suggests high temperature oil overheating (300-700°C) has occurred. | Oil quality is assessed as acceptable.
33000 | 1966 | 45 | 83.3 | 44 | 32.4 | 881 | 1.2 | 2.1 | 36.8 | 10.4 | 0.4 | 9 | 0.007 | 81 |  | 60 | 0.006 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1966 | 45 | 88 | 32 | 34.3 | 923.3 | 2.6 | 2 | 36.7 | 11.8 | 0.6 | 9 | 0.007 | 82 |  | 44 | 0.007 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1966 | 45 | 86 | 36 | 45.5 | 1046.8 | 1.9 | 5.3 | 25.6 | 7.7 | 0 | 8 | 0.005 | 85 |  | 35 | 0.008 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1966 | 45 | 845 | 41.81 | 769 | 6104 | 37 | 20 | 12 | 6 | 1 | 24 | 0.27 | 62.8 |  | 6 | 0.047 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1966 | 45 | 124 | 41.81 | 107 | 2046 | 0 | 2 | 12 | 2 | 1 | 33 | 0.198 | 51 |  | 5.5 | 0.0407 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1966 | 45 | 158 | 41.81 | 142 | 1697 | 0 | 2 | 13 | 1 | 0 | 32 | 0.165 | 39 |  | 4.6 | 0.047 | DGA is assessed as acceptable. | Moisture content of oil is slightly high.
33000 | 1966 | 45 | 245.3 | 43 | 220.5 | 2604.3 | 4.5 | 1.9 | 17.9 | 0.3 | 0.2 | 73 | 0.17 | 16 |  | 3 | 0.074 | Other test results are assessed as stable. | Moisture content of sample is high. Breakdown voltage of sample is low. Other test results are assessed as stable.
33000 | 1966 | 45 | 151.3 | 37 | 139.4 | 2017.8 | 0 | 1.4 | 10.1 | 0.4 | 0 | 72 | 0.156 | 23 |  | 3 | 0.074 | DGA is assessed as acceptable. | Moisture content is high. Breakdown voltage is low. Other oil quality results are assessed as acceptable. Sample is cloudy in appearance.
33000 | 1966 | 45 | 193.8 | 45 | 166.5 | 2734.7 | 10.9 | 1.6 | 14.2 | 0.5 | 0.1 | 62 | 0.172 | 26 |  | 3 | 0.072 | DGA is assessed as acceptable. | Moisture content is high. Breakdown voltage is low. Oil is cloudy in appearance. Other oil quality results are assessed as acceptable.
33000 | 1966 | 45 | 142.7 | 41.81 | 126.5 | 2489.4 | 1.2 | 1.5 | 13.2 | 0.3 | 0 | 59 | 0.171 | 13 |  | 3 | 0.068 | DGA is assessed as acceptable. | Moisture content is high. Breakdown voltage is low. Other oil quality results are assessed as acceptable.
33000 | 1966 | 45 | 187.7 | 20 | 163.8 | 2609.1 | 9.8 | 1.6 | 12.2 | 0.3 | 0 | 57 | 0.196 | 14 |  | 2 | 0.098 | DGA is assessed as acceptable. | Breakdown voltage is low. Other oil quality results are assessed as acceptable at present. Non-corrosive IEC. Non-corrosive ASTM 3B.
33000 | 1966 | 45 | 244 | 41.81 | 199 | 3170 | 21 | 6 | 12 | 6 | 0 | 46 | 0.181 | 35 |  | 5.4 | 0.052 | DGA is assessed as acceptable. | Moisture content of oil is high. Other test results are assessed as acceptable.
33000 | 1966 | 45 | 254 | 40 | 230 | 4200 | 10 | 2 | 10 | 2 | 0 | 52 | 0.189 | 20 |  | 4 | 0.058 | DGA is assessed as acceptable. | Moisture content of oil is high. Breakdown voltage of oil is low. Other test results are assessed as acceptable.
33000 | 1966 | 45 | 540.3 | 40 | 498.6 | 7410.5 | 18.3 | 5.4 | 15.3 | 2.7 | 0 | 49 | 0.184 | 19 |  | 4 | 0.064 | Dissolved gas analysis is assessed as acceptable. | Breakdown voltage of sample is low. Moisture content of sample is high. Acidity level of sample is high.
33000 | 1966 | 45 | 190.5 | 41.81 | 178.4 | 2693.1 | 5.9 | 1.6 | 3.9 | 0.7 | 0 | 54 | 0.167 | 17 |  | 4 | 0.056 | DGA is assessed as acceptable. | Moisture content is high. Breakdown voltage is low. Other oil quality results are assessed as acceptable. Sample is cloudy in appearance.
33000 | 1966 | 45 | 234 | 38 | 211.1 | 3579 | 16 | 1.8 | 4.2 | 0.9 | 0 | 24 | 0.193 | 75 |  | 4 | 0.105 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1966 | 45 | 148.8 | 32 | 133.8 | 2621.2 | 4.6 | 1.9 | 7 | 1.5 | 0 | 62 | 0.177 | 15 |  | 5 | 0.043 | DGA is assessed as acceptable. | Moisture content is high. Breakdown voltage is low. Other oil quality results are assessed as acceptable.
33000 | 1966 | 45 | 168.9 | 38 | 157 | 2673.6 | 7 | 1.3 | 2.6 | 1 | 0 | 62 | 0.186 | 13 |  | 5 | 0.049 | DGA is assessed as acceptable. | Breakdown voltage is low. Other oil quality results are assessed as acceptable. Corrosive IEC. Corrosive ASTM 4A.
33000 | 1966 | 45 | 200.2 | 60 | 182.6 | 2814.9 | 8.9 | 2.2 | 6.1 | 0.4 | 0 | 60 | 0.199 | 16 |  | 4 | 0.056 | DGA is assessed as acceptable. | Oil quality is poor.
33000 | 1966 | 45 | 576 | 26 | 322 | 2816 | 56 | 9 | 51 | 1 | 137 | 17 | 0.209 | 69 |  | 4 | 0.069 | DGA is assessed as acceptable. | Acidity is high.
33000 | 1966 | 45 | 932 | 48 | 360 | 2507 | 93 | 19 | 68 | 1 | 391 | 32 | 0.234 | 64 |  | 3.2 | 0.072 | Test results satisfactory. Acetylene gas possibly from tapchanger. | Acidity level is high.
33000 | 1966 | 45 | 594 | 41.81 | 229 | 2312 | 87 | 16 | 43 | 1 | 218 | 27 | 0.193 | 65 |  | 3.2 | 0.062 | Test results are assessed as acceptable. Acetylene gas possibly from tapchanger. | Oil quality is assessed as acceptable.
33000 | 1966 | 45 | 726.4 | 56 | 515.3 | 3727.7 | 44.1 | 10.5 | 46.7 | 5.2 | 104.6 | 32 | 0.229 | 34 |  | 3 | 0.066 | The test results are relatively stable and are assessed as acceptable. | Acidity level is high but stable.
33000 | 1966 | 45 | 1091.7 | 66 | 823.4 | 6530.7 | 86 | 19 | 34.9 | 6 | 122.4 | 56 | 0.25 | 24 |  | 3 | 0.067 | DGA is assessed as acceptable. | Moisture content is high. Breakdown voltage is low. Acidity level is high and increasing.
33000 | 1966 | 45 | 1617.7 | 66 | 1204 | 9191.7 | 170.2 | 41.7 | 42.6 | 4.7 | 154.5 | 69 | 0.275 | 12 |  | 3 | 0.077 | DGA is assessed as acceptable. | Oil quality is poor.
33000 | 1966 | 45 | 1176.4 | 44 | 822 | 6404.4 | 157.8 | 27.2 | 35.6 | 1.7 | 132.1 | 36 | 0.278 | 38 |  | 3 | 0.074 | DGA is assessed as acceptable. | Moisture content is high. Acidity level is high. Other oil quality results are assessed as acceptable.
33000 | 1966 | 45 | 597 | 54 | 268 | 2910.8 | 96.8 | 17.1 | 31 | 2.5 | 181.6 | 33 | 0.239 | 42 |  | 4 | 0.059 | DGA is assessed as acceptable. | Acidity level is high. Other oil quality results are assessed as acceptable.
33000 | 1966 | 45 | 529 | 57 | 289.7 | 3867.9 | 78 | 19.1 | 27.6 | 6 | 108.6 | 54 | 0.261 | 17 |  | 3 | 0.08 | DGA is assessed as acceptable. | Breakdown voltage is low. Acidity level is high. DDF and Resistivity are assessed as acceptable. Oil is cloudy in appearance.
33000 | 1966 | 45 | 707.9 | 59 | 368.5 | 3923.2 | 131.1 | 17.6 | 28 | 2.1 | 160.6 | 52 | 0.243 | 19 |  | 4 | 0.055 | DGA is assessed as acceptable. | Acidity level is high. Breakdown voltage is low. DDF and Resistivity are assessed as acceptable.
33000 | 1966 | 45 | 657 | 45 | 262.9 | 3350.2 | 125.6 | 23.4 | 37.8 | 4.7 | 202.6 | 43 | 0.252 | 26 |  | 4 | 0.058 | DGA is assessed as acceptable. | Acidity level is high. Breakdown voltage is low. DDF and Resistivity are acceptable.
33000 | 1966 | 45 | 596.5 | 45 | 205.4 | 2721.8 | 103.3 | 19.2 | 35.6 | 2.3 | 230.7 | 38 | 0.254 | 36 |  | 4 | 0.051 | DGA is assessed as acceptable. | Acidity level is high. Breakdown voltage is low. DDF and Resistivity are acceptable.
33000 | 1966 | 45 | 410.8 | 53 | 189.5 | 2927.2 | 49.6 | 15.2 | 26.2 | 3.3 | 127 | 48 | 0.215 | 30 |  | 5 | 0.047 | DGA is assessed as acceptable. | Oil quality is poor.
33000 | 1966 | 45 | 489.3 | 43 | 220.7 | 2913.6 | 68.2 | 16.1 | 26.3 | 3.4 | 154.6 | 41 | 0.224 | 29 |  | 5 | 0.046 | DGA is assessed as acceptable. | Breakdown voltage is low. Acidity level is high. Other oil quality results are assessed as acceptable.
33000 | 1966 | 45 | 112 | 40 | 86 | 1258 | 0 | 3 | 12 | 11 | 0 | 23 | 0.161 | 52 |  | 3.8 | 0.07 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1966 | 45 | 95 | 51 | 91 | 1266 | 0 | 1 | 3 | 0 | 0 | 20 | 0.182 | 62 |  | 5.1 | 0.05 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1966 | 45 | 104 | 41.81 | 101 | 1570 | 0 | 1 | 2 | 0 | 0 | 19 | 0.163 | 48 |  | 4.7 | 0.054 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1966 | 45 | 241.6 | 53 | 224.4 | 2206.5 | 10.7 | 2.1 | 3.2 | 1.2 | 0 | 23 | 0.205 | 40 |  | 4 | 0.057 | Acidity level of oil is high. Other test results are assessed as acceptable. RECOMMEND RESAMPLE IN 1 YEAR TO MONITOR TREND.
33000 | 1966 | 45 | 229.2 | 33 | 199.5 | 2627.6 | 22.4 | 3.1 | 3.3 | 0.9 | 0 | 26 | 0.207 | 36 |  | 3 | 0.067 | Acidity level of sample is high but stable. Other test results are assessed as acceptable. RECOMMEND RESAMPLE IN 2 YEARS TO MONITOR TREND.
33000 | 1966 | 45 | 243.6 | 56 | 226.8 | 2912.1 | 12.3 | 1.8 | 2.7 | 0 | 0 | 32 | 0.223 | 51 |  | 4 | 0.062 | DGA is assessed as acceptable. | Acidity level is high but relatively stable. Other oil quality results are assessed as acceptable.
33000 | 1966 | 45 | 253.2 | 48 | 235.5 | 2742.3 | 11.1 | 2.3 | 3.3 | 1 | 0 | 29 | 0.224 | 48 |  | 4 | 0.071 | DGA is assessed as acceptable. | Acidity level is high but relatively stable. Other oil quality results are assessed as acceptable.
33000 | 1966 | 45 | 235.9 | 55 | 206.3 | 3512 | 11.6 | 3.7 | 9.9 | 4.4 | 0 | 32 | 0.27 | 29 |  | 2 | 0.154 | DGA is assessed as acceptable. | Breakdown voltage is low. Acidity level is high. DDF and Resistivity are assessed as acceptable.
33000 | 1966 | 45 | 207.1 | 59 | 190 | 2631.1 | 6.5 | 2.1 | 7.9 | 0.6 | 0 | 39 | 0.246 | 25 |  | 4 | 0.061 | DGA is assessed as acceptable. | Oil quality is poor.
33000 | 1966 | 45 | 205.4 | 52 | 189.7 | 2638.9 | 9.9 | 2.3 | 3.1 | 0.4 | 0 | 37 | 0.255 | 30 |  | 3 | 0.071 | DGA is assessed as acceptable. | Oil quality is poor.
33000 | 1966 | 45 | 771 | 62 | 495 | 5919 | 114 | 16 | 41 | 4 | 101 | 35 | 0.333 | 62 |  | 2 | 0.138 | Test results satisfactory; though C2H2 and acidity levels notable.
33000 | 1966 | 45 | 507 | 52 | 371 | 4442 | 37 | 9 | 27 | 4 | 59 | 17 | 0.321 | 72 |  | 2.1 | 0.146 | DGA satisfactory. | Oil quality is assessed as acceptable.
33000 | 1966 | 45 | 339 | 50 | 295 | 3338 | 0 | 4 | 16 | 6 | 18 | 22 | 0.343 | 58 |  | 2 | 0.146 | Test results satisfactory. | Oil quality is assessed as acceptable.
33000 | 1966 | 45 | 305 | 55 | 261 | 3707 | 0 | 4 | 33 | 2 | 5 | 38 | 0.352 | 59 |  | 1.9 | 0.137 | Test results satisfactory. | Oil quality is assessed as acceptable.
33000 | 1966 | 45 | 203 | 43 | 159 | 1584 | 0 | 2 | 33 | 2 | 7 | 26 | 0.051 | 52 |  | 10.5 | 0.034 | Test results satisfactory. Has transformer oil been processed/changed? | Oil quality is assessed as acceptable.
33000 | 1966 | 45 | 139 | 41.81 | 100 | 1630 | 0 | 1 | 34 | 1 | 3 | 27 | 0.052 | 57 |  | 10.5 | 0.037 | Test results are assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1966 | 45 | 210.1 | 48 | 135.1 | 2168.1 | 5.7 | 2.1 | 57.5 | 1.3 | 8.4 | 12 | 0.061 | 44 |  | 8 | 0.045 | The test results are assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1966 | 45 | 208 | 30 | 133.4 | 2426.2 | 0 | 8 | 55.7 | 8.2 | 2.7 | 15 | 0.062 | 75 |  | 8 | 0.039 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1966 | 45 | 140.4 | 19.2 | 113.8 | 2038.5 | 0 | 1.3 | 22.8 | 2.1 | 0.4 | 18 | 0.072 | 56 |  | 8 | 0.039 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1966 | 45 | 125.9 | 14 | 103.5 | 1286 | 0 | 1.3 | 20.5 | 0.2 | 0.4 | 16 | 0.057 | 68 |  | 8 | 0.035 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable. Corrosive IEC. Corrosive ASTM 4B.
33000 | 1966 | 45 | 243 | 35 | 234 | 2567 | 2 | 2 | 3 | 2 | 0 | 16 | 0.163 | 53 |  | 7 | 0.045 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1966 | 45 | 150 | 57 | 145 | 1872 | 0 | 1 | 3 | 1 | 0 | 25 | 0.151 | 38 |  | 5.8 | 0.044 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1966 | 45 | 213 | 52 | 206 | 2010 | 0 | 1 | 4 | 2 | 0 | 42 | 0.155 | 29 |  | 5.5 | 0.046 | DGA is assessed as acceptable. | Sample possibly moisture contaminated. Otherwise test results are satisfactory.
33000 | 1966 | 45 | 353 | 41.81 | 331 | 2965 | 16 | 2 | 3 | 1 | 0 | 57 | 0.171 | 30 |  | 6.2 | 0.045 | DGA is assessed as acceptable. | Moisture content of oil is very high. Possibly sample contamination. Other test results are assessed as acceptable.
33000 | 1966 | 45 | 228 | 27 | 193 | 2143 | 27 | 2 | 4 | 2 | 0 | 18 | 0.16 | 54 |  | 4.8 | 0.054 | Dissolved gas analysis appears normal after Buchholz Trip. | Oil quality is assessed as acceptable.
33000 | 1966 | 45 | 12 | 27 | 11 | 177 | 0 | 0 | 0 | 1 | 0 | 7 | 0.012 | 75 |  | 81.9 | 0.009 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1966 | 45 | 186 | 50 | 152.1 | 2040.6 | 18.3 | 1.4 | 13.9 | 0.3 | 0 | 51 | 0.01 | 26 |  | 48 | 0.008 | DGA is assessed as acceptable. | Moisture content is high. Oil was cloudy in appearance. Breakdown voltage is low. Other oil quality results are assessed as acceptable.
33000 | 1966 | 45 | 162.1 | 36 | 145.5 | 1605.2 | 0 | 1.3 | 14.9 | 0.3 | 0.1 | 10 | 0.011 | 75 |  | 19 | 0.019 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1966 | 45 | 201.4 | 43 | 148.3 | 2609.6 | 32.9 | 1.6 | 18.6 | 0 | 0 | 46 | 0.012 | 20 |  | 27 | 0.0098 | DGA is assessed as acceptable. | Moisture content is high. Breakdown voltage is low. Possible sample contamination. Other oil quality results are assessed as acceptable.
33000 | 1966 | 45 | 198.9 | 50 | 166.7 | 2177.9 | 11.6 | 1.5 | 18.6 | 0.5 | 0 | 21 | 0.02 | 65 |  | 25 | 0.02 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1966 | 45 | 230 | 25 | 120 | 996 | 30 | 6 | 15 | 1 | 58 | 9 | 0.162 | 64.5 |  | 40 | 0.052 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1966 | 45 | 313 | 50 | 177 | 1193 | 24 | 9 | 29 | 2 | 72 | 16 | 0.151 | 61 |  | 4 | 0.069 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1966 | 45 | 357 | 60 | 134 | 1050 | 40 | 10 | 29 | 1 | 143 | 21 | 0.114 | 46 |  | 3.9 | 0.065 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1966 | 45 | 417 | 51 | 152 | 1052 | 70 | 13 | 30 | 1 | 151 | 29 | 0.13 | 62 |  | 4 | 0.071 | Test results satisfactory. Acetylene gas possibly from tapchanger. | Oil quality is assessed as acceptable.
33000 | 1966 | 45 | 632 | 48 | 114 | 1178 | 116 | 22 | 50 | 1 | 329 | 20 | 0.129 | 56 |  | 4.4 | 0.058 | Test results satisfactory. Acetylene gas possibly from tapchanger. | Oil quality is assessed as acceptable.
33000 | 1966 | 45 | 311 | 40 | 166 | 1578 | 82 | 11 | 34 | 1 | 17 | 18 | 0.12 | 47 |  | 3.5 | 0.072 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1966 | 45 | 428.3 | 47 | 210.3 | 2384.8 | 23 | 7 | 35.5 | 5.9 | 146.6 | 16 | 0.131 | 75 |  | 3 | 0.085 | The test results are assessed as acceptable. Acetylene gas possibly from tapchanger. | Oil quality is assessed as acceptable.
33000 | 1966 | 45 | 422.1 | 36 | 282.7 | 2722.1 | 39.2 | 6.8 | 15.9 | 2.7 | 74.8 | 22 | 0.153 | 75 |  | 3.2 | 0.08 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1966 | 45 | 395.6 | 36 | 289.1 | 3146.7 | 52.4 | 4.2 | 8.2 | 1.1 | 40.6 | 20 | 0.177 | 63 |  | 3 | 0.067 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1966 | 45 | 312.2 | 48 | 264.7 | 2959.6 | 25.2 | 2 | 4.8 | 0.8 | 14.7 | 23 | 0.172 | 83 |  | 4 | 0.067 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable. Corrosive IEC. Corrosive ASTM 4A.
33000 | 1966 | 45 | 254.1 | 39 | 215.3 | 2592.4 | 20.4 | 2.2 | 3 | 1.2 | 12 | 35 | 0.158 | 89 |  | 4 | 0.053 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1966 | 45 | 164.2 | 29 | 76.6 | 1448.4 | 30.6 | 4.2 | 7.1 | 0.7 | 45 | 18 | 0.14 | 72 |  | 5 | 0.045 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1965 | 46 | 137 | 40 | 110 | 1327 | 0 | 2 | 24 | 1 | 0 | 27 | 0.098 | 52 |  | 9 | 0.0307 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1965 | 46 | 224 | 35 | 207 | 2095 | 0 | 2 | 15 | 0 | 0 | 43 | 0.099 | 31 |  | 8.2 | 0.037 | DGA is assessed as acceptable. | Moisture content of oil high. Possible sample contamination. Other oil quality results are assessed as acceptable.
33000 | 1965 | 46 | 157 | 35 | 142 | 1600 | 0 | 1 | 12 | 2 | 0 | 29 | 0.094 | 40 |  | 6.6 | 0.037 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1965 | 46 | 279 | 42 | 238.4 | 3028.6 | 4.3 | 6.2 | 27.5 | 2.3 | 0.3 | 25 | 0.093 | 30 |  | 4 | 0.055 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1965 | 46 | 314.2 | 38 | 275.6 | 3375.8 | 4.1 | 3.2 | 30.2 | 1.1 | 0 | 47 | 0.101 | 23 |  | 4.4 | 0.058 | DGA is assessed as acceptable. | Moisture content is high. Breakdown voltage is low.
33000 | 1965 | 46 | 268.8 | 36 | 238.1 | 3049 | 7.1 | 2 | 21 | 0.6 | 0 | 45 | 0.173 | 22 |  | 5 | 0.043 | DGA is assessed as acceptable. | Moisture content is high. Breakdown voltage is low. Other oil quality results are assessed as acceptable at present.
33000 | 1965 | 46 | 256.1 | 41.81 | 229.4 | 3033.4 | 4.6 | 0.9 | 20.8 | 0.4 | 0 | 28 | 0.123 | 23 |  | 5 | 0.05 | DGA is assessed as acceptable. | Breakdown voltage is low. Other oil quality results are assessed as acceptable. Corrosive IEC. Non-corrosive ASTM 3B.
33000 | 1965 | 46 | 240 | 33 | 216 | 3163.6 | 1.9 | 1 | 20.5 | 0.6 | 0 | 56 | 0.135 | 14 |  | 5 | 0.042 | DGA is assessed as acceptable. | Breakdown voltage is low. Other oil quality results are assessed as acceptable.
33000 | 1965 | 46 | 866.6 | 36 | 8.4 | 1057.8 | 26.5 | 13.6 | 76.3 | 14.5 | 727.3 | 15 | 0.001 | 64 |  | 150 | 0.004 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable. Particle contamination load is marginal.
33000 | 1965 | 46 | 222 | 30 | 194.1 | 2524.9 | 9 | 2 | 16.7 | 0.2 | 0 | 24 | 0.126 | 45 |  | 5 | 0.039 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1965 | 46 | 215 | 36 | 189 | 1774 | 0 | 1 | 24 | 1 | 0 | 29 | 0.132 | 33 |  | 70 | 0.0438 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1965 | 46 | 355 | 45 | 328 | 2424 | 0 | 2 | 24 | 1 | 0 | 26 | 0.138 | 57 |  | 5.1 | 0.046 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1965 | 46 | 469 | 72 | 439 | 2528 | 9 | 2 | 19 | 0 | 0 | 30 | 0.166 | 56 |  | 4.9 | 0.048 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1965 | 46 | 439 | 48 | 416 | 2942 | 12 | 2 | 9 | 0 | 0 | 30 | 0.155 | 52 |  | 5.5 | 0.039 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1965 | 46 | 438 | 43 | 401 | 3427 | 23 | 2 | 11 | 1 | 0 | 33 | 0.213 | 73 |  | 4.4 | 0.052 | Moisture content of oil is above defect level. Other test results are assessed as acceptable.
33000 | 1965 | 46 | 478.0848 | 41.81 | 440.7479 | 3699.2152 | 23.2466 | 3.0642 | 9.0747 | 1.3198 | 0.6316 | 34 | 0.265 | 38 |  | 3 | 0.067 | Test results suggest oil and insulation is badly degraded. RECOMMEND RESAMPLE IN 1 YEAR TO MONITOR TREND.
33000 | 1965 | 46 | 505.9 | 49 | 466.8 | 5525.9 | 24 | 3.7 | 9.6 | 1.4 | 0.4 | 36 | 0.296 | 44 |  | 3 | 0.058 | 2-furfural level is high but stable. Acidity level is high. Other test results are assessed as acceptable. RECOMMEND OIL CHANGE / TREATMENT. RECOMMEND RESAMPLE IN 1 YEAR TO MONITOR TREND.
33000 | 1965 | 46 | 67.8 | 33 | 9 | 485.6 | 17.7 | 5.6 | 2.3 | 0 | 33.2 | 21 | 0.01 | 47 |  | 100 | 0.008 | 2-furfural level is high but stable. Other test results are assessed as acceptable after oil treatment. RECOMMEND RESAMPLE IN 6 MONTHS TO MONITOR TREND.
33000 | 1965 | 46 | 653.6 | 46 | 599.3 | 6671.7 | 31.3 | 4.5 | 8 | 1.9 | 8.6 | 35 | 0.307 | 28 |  | 4 | 0.048 | DGA is assessed as acceptable. | Oil quality is poor.
33000 | 1965 | 46 | 678.7 | 35.2 | 563.4 | 7175.3 | 39.8 | 6.3 | 10.9 | 1.7 | 56.6 | 41 | 0.31 | 16 |  | 4 | 0.048 | Carbon oxide levels are increasing. Other dissolved gas levels are assessed as acceptable. | Oil quality is poor.
33000 | 1965 | 46 | 404 | 40 | 346 | 3077 | 44 | 3 | 6 | 2 | 3 | 24 | 0.218 | 64 |  | 9 | 0.0332 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1965 | 46 | 319 | 23 | 271 | 2886 | 32 | 4 | 8 | 4 | 0 | 22 | 0.206 | 43 |  | 5.5 | 0.0462 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1965 | 46 | 186 | 38 | 177 | 1908 | 0 | 3 | 4 | 2 | 0 | 27 | 0.187 | 48 |  | 3.7 | 0.07 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1965 | 46 | 170 | 27 | 163 | 1871 | 0 | 2 | 4 | 1 | 0 | 23 | 0.184 | 48 |  | 4.8 | 0.054 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1965 | 46 | 147 | 30 | 118 | 1742 | 21 | 3 | 4 | 1 | 0 | 34 | 0.177 | 55 |  | 2.9 | 0.076 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1965 | 46 | 199 | 25 | 173 | 1940 | 21 | 1 | 3 | 1 | 0 | 22 | 0.193 | 71 |  | 5.4 | 0.039 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1965 | 46 | 182.3 | 22 | 166.7 | 2771.2 | 6.4 | 1.8 | 6.2 | 1.2 | 0 | 18 | 0.204 | 60 |  | 5 | 0.051 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1965 | 46 | 167.3 | 42 | 152.4 | 2455.6 | 9.1 | 1.3 | 3.8 | 0.7 | 0 | 24 | 0.207 | 46 |  | 4 | 0.053 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1965 | 46 | 245.1 | 20 | 205.3 | 2878.4 | 20.7 | 3.2 | 13.8 | 2.1 | 0 | 21 | 0.213 | 34 |  | 3 | 0.0657 | DGA is assessed as acceptable | Acidity level is high but stable. Other oil quality results are assessed as acceptable.
33000 | 1965 | 46 | 174.9 | 30 | 162 | 2086 | 8.5 | 1.3 | 2.7 | 0.4 | 0 | 22 | 0.209 | 70 |  | 4 | 0.072 | DGA is assessed as acceptable. | Acidity level is high but stable. Other oil quality results are assessed as acceptable.
33000 | 1965 | 46 | 170.2 | 35 | 157.3 | 2333.8 | 7.8 | 1.6 | 2.4 | 1.1 | 0 | 24 | 0.22 | 33 |  | 3 | 0.069 | DGA is assessed as acceptable. | Acidity level is high. Breakdown voltage is low. DDF and Resistivity are assessed as acceptable. Corrosive IEC. Non-corrosive ASTM 3B.
33000 | 1965 | 46 | 154.5 | 36 | 144.2 | 1952.1 | 6 | 1.1 | 2.8 | 0.4 | 0 | 21 | 0.224 | 74 |  | 4 | 0.051 | DGA is assessed as acceptable. | Acidity level is high. Other oil quality results are assessed as acceptable. Corrosive IEC. Corrosive ASTM 4A.
33000 | 1965 | 46 | 145 | 40 | 131.4 | 1742.1 | 6.4 | 5 | 1.7 | 0.5 | 0 | 26 | 0.209 | 82 |  | 5 | 0.047 | DGA is assessed as acceptable. | Acidity level is high. Other oil quality results are assessed as acceptable. Corrosive IEC. Non-corrosive ASTM 3B.
33000 | 1965 | 46 | 146 | 30 | 126 | 1389 | 0 | 0 | 20 | 0 | 0 | 18 | 0.158 | 57 |  | 3.5 | 0.079 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1965 | 46 | 195 | 30 | 167 | 1502 | 0 | 2 | 23 | 0 | 3 | 17 | 0.15 | 55 |  | 3.5 | 0.062 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1965 | 46 | 215 | 42 | 193 | 1447 | 0 | 1 | 21 | 0 | 0 | 22 | 0.13 | 64 |  | 3.4 | 0.064 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1965 | 46 | 224 | 36 | 195 | 1952 | 0 | 1 | 27 | 0 | 1 | 20 | 0.173 | 47 |  | 2.9 | 0.065 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1965 | 46 | 381.9 | 50 | 320.5 | 2933.3 | 4.7 | 2.3 | 53.4 | 1 | 0 | 30 | 0.205 | 54 |  | 2 | 0.086 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1965 | 46 | 557.3 | 42 | 487.9 | 4633.9 | 15.3 | 2.9 | 50.4 | 0.8 | 0 | 29 | 0.223 | 32 |  | 2 | 0.114 | DGA is assessed as acceptable. | Acidity level is high but stable. Other oil quality results are assessed as acceptable.
33000 | 1965 | 46 | 454.2 | 40 | 404.3 | 4596.4 | 10.6 | 2.6 | 36 | 0.7 | 0 | 36 | 0.241 | 29 |  | 2 | 0.101 | DGA is assessed as acceptable. | Moisture content is slightly high. Breakdown voltage is slightly low. Other oil quality results are assessed as acceptable.
33000 | 1965 | 46 | 496.1 | 48 | 442.1 | 5673.7 | 7.4 | 3 | 40.7 | 2.9 | 0 | 30 | 0.266 | 30 |  | 2 | 0.095 | DGA is assessed as acceptable. | Oil quality is poor. Corrosive IEC. Non-corrosive ASTM 3A.
33000 | 1965 | 46 | 262 | 41.81 | 142 | 1412 | 9 | 28 | 75 | 8 | 0 | 16 | 0.023 | 62 |  | 30 | 0.02 | Test results satisfactory.
33000 | 1965 | 46 | 200 | 41.81 | 167 | 1265 | 0 | 1 | 31 | 0 | 1 | 12 | 0.037 | 54 |  | 21.8 | 0.022 | Test results satisfactory.
33000 | 1965 | 46 | 146 | 41.81 | 120 | 1080 | 0 | 1 | 25 | 0 | 0 | 16 | 0.036 | 75 |  | 19.1 | 0.016 | Test results are assessed as acceptable.
33000 | 1965 | 46 | 274.7 | 36 | 216.6 | 2377.8 | 2.4 | 1.7 | 52.8 | 0.7 | 0.5 | 12 | 0.041 | 75 |  | 13 | 0.023 | The test results are assessed as acceptable.
33000 | 1965 | 46 | 312.2 | 41.81 | 257.9 | 2583 | 4.5 | 1.3 | 47.9 | 0.6 | 0 | 18 | 0.05 | 52 |  | 13 | 0.024 | The test results are assessed as acceptable.
33000 | 1965 | 46 | 278.1 | 40 | 228.3 | 2782.1 | 0 | 4.6 | 45.2 | 0 | 0 | 13 | 0.043 | 72 |  | 14 | 0.019 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1965 | 46 | 307.6 | 34 | 252 | 2291 | 8 | 5 | 42 | 0.6 | 0 | 23 | 0.057 | 38 |  | 10 | 0.027 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1965 | 46 | 46.5 | 41.81 | 11.1 | 470.2 | 3.7 | 1.1 | 6.6 | 0.3 | 23.7 | 20 | 0.051 | 65 |  | 13 | 0.02 | DGA is assessed as acceptable | Oil quality is assessed as acceptable.
33000 | 1965 | 46 | 245.7 | 41.81 | 185.1 | 1772.1 | 19.6 | 3.7 | 35.9 | 0.9 | 0.5 | 10 | 0.054 | 46 |  | 12 | 0.02275 | DGA is assessed as acceptable | Oil quality is assessed as acceptable. PCB contaminated oil.
33000 | 1965 | 46 | 3.6 | 41.81 | 3.1 | 184.6 | 0 | 0.5 | 0 | 0 | 0 | 5 | 0.01 | 70 |  | 46 | 0.0198 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable. Tested to be uncontaminated by PCB.
33000 | 1965 | 46 | 10.9 | 41.81 | 10.1 | 239.3 | 0 | 0.5 | 0 | 0.3 | 0 | 3 | 0.038 | 75 |  | 15 | 0.0224 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable. Tested to be uncontaminated by PCB.
33000 | 1965 | 46 | 11.4 | 20 | 11 | 260.8 | 0 | 0.4 | 0 | 0 | 0 | 3 | 0.042 | 75 |  | 13 | 0.027 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1965 | 46 | 4.1 | 20 | 3.7 | 203.7 | 0 | 0.4 | 0 | 0 | 0 | 5 | 0.01 | 75 |  | 43 | 0.017 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1965 | 46 | 98.9 | 42 | 90.2 | 1181.7 | 2.6 | 1.6 | 1.8 | 2.7 | 0 | 8 | 0.058 | 82 |  | 5 | 0.066 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable. Corrosive IEC. Corrosive ASTM 4A.
33000 | 1965 | 46 | 112.2 | 41 | 104.3 | 1575.6 | 2.1 | 2.3 | 2.1 | 1.2 | 0.2 | 7 | 0.061 | 84 |  | 6 | 0.042 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1965 | 46 | 111 | 32 | 84 | 1555 | 0 | 0 | 27 | 0 | 0 | 13 | 0.072 | 53 |  | 7 | 0.039 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1965 | 46 | 192 | 41.81 | 163 | 1358 | 0 | 1 | 28 | 0 | 0 | 14 | 0.08 | 59 |  | 7 | 0.0361 | Dissolved gas analysis is assessed as acceptable. Oil quality is assessed as acceptable.
33000 | 1965 | 46 | 277 | 41.81 | 226 | 2303 | 0 | 2 | 47 | 1 | 1 | 25 | 0.118 | 62 |  | 5.6 | 0.041 | Dissolved gas analysis is assessed as acceptable. Oil quality is assessed as acceptable.
33000 | 1965 | 46 | 26 | 41.81 | 13 | 688 | 0 | 1 | 11 | 1 | 0 | 13 | 0.134 | 72 |  | 4.8 | 0.039 | Dissolved gas analysis is assessed as acceptable. Oil quality is assessed as acceptable.
33000 | 1965 | 46 | 66 | 41.81 | 42 | 588 | 0 | 1 | 7 | 16 | 0 | 22 | 0.12 | 56 |  | 4 | 0.059 | Dissolved gas analysis is assessed as acceptable. Oil quality is assessed as acceptable.
33000 | 1965 | 46 | 8 | 30 | 8 | 225 | 0 | 0 | 0 | 0 | 0 | 11 | 0.01 | 75 |  | 49 | 0.015 | Dissolved gas analysis is assessed as acceptable. Oil quality is assessed as acceptable.
33000 | 1965 | 46 | 170.4 | 41.81 | 146.7 | 1499.8 | 3.7 | 1.5 | 18 | 0.5 | 0 | 10 | 0.01 | 55 |  | 18 | 0.033 | Dissolved gas analysis is assessed as acceptable. Oil quality is assessed as acceptable.
33000 | 1965 | 46 | 116 | 37 | 99.6 | 1257.6 | 0 | 1.3 | 14.3 | 0.8 | 0 | 9 | 0.01 | 75 |  | 20 | 0.024 | Dissolved gas analysis is assessed as acceptable. Oil quality is assessed as acceptable.
33000 | 1965 | 46 | 1787 | 34 | 24 | 1020 | 105 | 34 | 123 | 31 | 1470 | 14 | 0.014 | 60 |  | 15 | 0.04 | Dissolved gas analysis is assessed as acceptable. Oil quality is assessed as acceptable. The test results are assessed as acceptable for a tapchanger.
33000 | 1965 | 46 | 1410.9 | 46 | 57.5 | 850.8 | 71.2 | 20.2 | 103.7 | 21.8 | 1136.5 | 19 | 0.017 | 42 |  | 12 | 0.058 | Dissolved gas analysis is assessed as acceptable. Oil quality is assessed as acceptable. The test results are assessed as acceptable for a tapchanger.
33000 | 1965 | 46 | 105.9 | 30 | 95 | 1208.8 | 0 | 1.3 | 9.1 | 0.5 | 0 | 15 | 0.01 | 75 |  | 27.3 | 0.021 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1965 | 46 | 87.3 | 40 | 74 | 933 | 4.5 | 1 | 7.5 | 0.3 | 0 | 8 | 0.01 | 75 |  | 22 | 0.021 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1965 | 46 | 165.6 | 41.81 | 146.8 | 1108.8 | 1.7 | 7.4 | 9.2 | 0.5 | 0 | 10 | 0.01 | 75 |  | 28 | 0.018 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable. Corrosive IEC. Corrosive ASTM 4A.
33000 | 1965 | 46 | 123.7 | 29 | 113 | 1241 | 0 | 0.7 | 10 | 0 | 0 | 18 | 0.016 | 55 |  | 24 | 0.02 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable. Corrosive IEC. Non-corrosive ASTM 3B.
33000 | 1965 | 46 | 94.3 | 34 | 82.7 | 1198 | 0 | 1.9 | 9.7 | 0 | 0 | 8 | 0.007 | 81 |  | 26 | 0.017 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1965 | 46 | 113.1 | 32 | 94.4 | 1227.8 | 2.8 | 3.9 | 11.6 | 0.4 | 0 | 10 | 0.008 | 69 |  | 31 | 0.013 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1965 | 46 | 318 | 41.81 | 297 | 4544 | 13 | 2 | 5 | 1 | 0 | 21 | 0.2 | 69 |  | 6 | 0.0557 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1965 | 46 | 264 | 41.81 | 257 | 3495 | 0 | 2 | 4 | 1 | 0 | 25 | 0.22 | 69 |  | 3.5 | 0.0661 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1965 | 46 | 453 | 41.81 | 449 | 6023 | 0 | 3 | 1 | 0 | 0 | 33 | 0.211 | 60 |  | 4 | 0.064 | DGA is assessed as acceptable. | Sample moisture content higher than previous; otherwise test results satisfactory.
33000 | 1965 | 46 | 633 | 41.81 | 618 | 7806 | 0 | 4 | 9 | 2 | 0 | 37 | 0.205 | 24 |  | 4.1 | 0.061 | DGA is assessed as acceptable. | Moisture content of oil high. Breakdown low. Other test results satisfactory.
33000 | 1965 | 46 | 1309 | 41.81 | 1140 | 12490 | 56 | 64 | 33 | 16 | 0 | 61 | 0.257 | 33 |  | 3.1 | 0.081 | Step increase in carbon oxide gas levels. | Moisture content of oil is very high. Acidity level is slightly high.
33000 | 1965 | 46 | 593 | 44 | 538 | 6490 | 10 | 13 | 20 | 12 | 0 | 40 | 0.247 | 66 |  | 2.5 | 0.111 | DGA is assessed as acceptable. | Moisture content of oil is high. Acidity level is high.
33000 | 1965 | 46 | 492 | 38 | 447 | 6681 | 3 | 10 | 21 | 11 | 0 | 35 | 0.266 | 46 |  | 2.7 | 0.092 | DGA is assessed as acceptable. | Moisture cotent of oil is high. Other test results are assessed as acceptable.
33000 | 1965 | 46 | 616 | 41.81 | 500 | 4787 | 19 | 22 | 62 | 13 | 0 | 28 | 0.283 | 72 |  | 2.5 | 0.095 | DGA is assessed as acceptable. | Other test results are assessed as acceptable.
33000 | 1965 | 46 | 818 | 40 | 637 | 6375 | 43 | 23 | 94 | 20 | 1 | 38 | 0.328 | 39 |  | 2 | 0.108 | DGA is assessed as acceptable. | Moisture content is high but stable.
33000 | 1965 | 46 | 533.7 | 44 | 419.8 | 5474.8 | 25.6 | 10.7 | 60.6 | 16 | 1 | 29 | 0.268 | 48 |  | 1.3 | 0.21 | DGA is assessed as acceptable. | Oil quality has deteriorated.
33000 | 1965 | 46 | 1015.4 | 54 | 566.7 | 5881.3 | 68.1 | 97.3 | 235.2 | 40.1 | 8 | 54 | 0.277 | 33 |  | 2 | 0.114 | DGA suggests high temperature oil overheating has occurred. | Moisture content is high. Acidity level is high. Other oil quality results are assessed as acceptable.
33000 | 1965 | 46 | 124 | 26 | 105 | 1101 | 0 | 0 | 18 | 1 | 0 | 18 | 0.146 | 72.5 |  | 6 | 0.0496 | Test results satisfactory. | Oil quality is assessed as acceptable.
33000 | 1965 | 46 | 415 | 40 | 231 | 1716 | 21 | 33 | 111 | 12 | 7 | 25 | 0.191 | 56 |  | 4.1 | 0.056 | Increased ethylene level. Possible metal hot spot. | Oil quality is assessed as acceptable.
33000 | 1965 | 46 | 179 | 30 | 160 | 1551 | 0 | 2 | 15 | 1 | 1 | 7 | 0.175 | 69 |  | 4.3 | 0.05 | DGA satisfactory. Has main tank oil been filtered? | Oil quality is assessed as acceptable.
33000 | 1965 | 46 | 331 | 40 | 298 | 2794 | 0 | 2 | 30 | 1 | 0 | 19 | 0.172 | 75 |  | 4.3 | 0.054 | Test results satisfactory. | Oil quality is assessed as acceptable.
33000 | 1965 | 46 | 119 | 36 | 103 | 1492 | 0 | 2 | 13 | 1 | 0 | 13 | 0.013 | 73 |  | 40.2 | 0.015 | Test results are assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1965 | 46 | 268.1 | 38 | 229.1 | 3986.7 | 4.6 | 1.9 | 31.7 | 0.3 | 0.5 | 23 | 0.195 | 52 |  | 3 | 0.08 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1965 | 46 | 281.3 | 43 | 248.1 | 3051.8 | 4.6 | 1.8 | 26.5 | 0.3 | 0 | 28 | 0.186 | 37 |  | 3 | 0.075 | DGA is assessed as acceptable. | Acidity level is stable. Oil quality is assessed as acceptable.
33000 | 1965 | 46 | 260.2 | 45 | 212 | 1994 | 23.7 | 1.6 | 22.4 | 0.5 | 0 | 24 | 0.224 | 73 |  | 2 | 0.084 | DGA is assessed as acceptable. | Oil quality is stable.
33000 | 1965 | 46 | 189 | 29 | 152 | 1318 | 0 | 1 | 35 | 0 | 1 | 17 | 0.162 | 70 |  | 6 | 0.052 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1965 | 46 | 222 | 38 | 174 | 1714 | 0 | 2 | 35 | 1 | 10 | 21 | 0.084 | 59 |  | 6.5 | 0.035 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1965 | 46 | 284 | 50 | 244 | 2011 | 7 | 2 | 30 | 0 | 1 | 23 | 0.113 | 72 |  | 4.4 | 0.044 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1965 | 46 | 352.3 | 52 | 290.3 | 2514 | 6.5 | 2.3 | 51.3 | 1.1 | 0.8 | 21 | 0.15 | 58 |  | 3 | 0.062 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1965 | 46 | 534.5 | 45 | 475.3 | 4969.1 | 6.7 | 2.6 | 48.5 | 1.1 | 0.3 | 27 | 0.154 | 31 |  | 2 | 0.097 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1965 | 46 | 573.9 | 42 | 451 | 5136.2 | 16.5 | 9.8 | 75 | 5.6 | 16 | 27 | 0.163 | 46 |  | 2 | 0.0985 | Carbon dioxide level is trending upwards. Other dissolved gas levels are assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1965 | 46 | 529.1 | 50 | 470.5 | 5341.3 | 7.2 | 3 | 44.5 | 2.6 | 1.3 | 36 | 0.187 | 46 |  | 3 | 0.091 | DGA is assessed as acceptable. | Acidity level is high. Other oil quality results are assessed as acceptable. Corrosive IEC. Non-corrosive ASTM 3B.
33000 | 1965 | 46 | 191 | 41.81 | 117 | 946 | 0 | 9 | 50 | 13 | 2 | 15 | 0.048 | 68 |  | 8 | 0.0338 | Test results satisfactory. | Oil quality is assessed as acceptable.
33000 | 1965 | 46 | 168 | 41.81 | 143 | 1174 | 0 | 5 | 16 | 3 | 1 | 16 | 0.01 | 58 |  | 45.3 | 0.014 | Test results satisfactory. TX has had oil change. | Oil quality is assessed as acceptable.
33000 | 1965 | 46 | 175.4 | 38 | 124.6 | 2223.9 | 2.1 | 5.3 | 38.6 | 4 | 0.8 | 18 | 0.01 | 53 |  | 27 | 0.016 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1965 | 46 | 159.9 | 43 | 120.8 | 1730 | 1.7 | 4 | 30.5 | 2.5 | 0.4 | 12 | 0.01 | 75 |  | 18 | 0.018 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1965 | 46 | 136.4 | 46 | 102.5 | 1226.8 | 4.3 | 2.4 | 22.7 | 1.8 | 2.7 | 15 | 0.019 | 75 |  | 22 | 0.021 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1965 | 46 | 1183 | 25 | 1082 | 8131 | 83 | 9 | 7 | 2 | 0 | 59 | 0.278 | 44 |  | 8 | 0.0249 | No evidence of damage caused by overheating. High moisture probably due to high temperature.RESAMPLE IN 3 MONTHS
33000 | 1965 | 46 | 839 | 41.81 | 761 | 5518 | 66 | 6 | 4 | 2 | 0 | 66 | 0.276 | 21 |  | 7.5 | 0.0314 | No evidence of damage caused by overheating. High moisture probably due to high temperature.RESAMPLE IN 3 MONTHS
33000 | 1965 | 46 | 1083 | 61 | 997 | 5872 | 71 | 6 | 7 | 2 | 0 | 51 | 0.314 | 54 |  | 5.5 | 0.0541 | High moisture consistent with acidity level and high operating temperature.
33000 | 1965 | 46 | 347 | 20 | 339 | 3317 | 0 | 3 | 4 | 1 | 0 | 11 | 0.264 | 59 |  | 4.9 | 0.0464 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1965 | 46 | 87 | 41.81 | 81 | 1910 | 0 | 2 | 3 | 1 | 0 | 17 | 0.25 | 52 |  | 4.7 | 0.049 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1965 | 46 | 202 | 45 | 178 | 2770 | 3 | 2 | 18 | 1 | 0 | 32 | 0.164 | 42 |  | 5 | 0.05 | DGA is assessed as acceptable. | Moisture content of oil is slightly high. Other test results are assessed as acceptable.
33000 | 1965 | 46 | 302.1 | 40 | 264 | 3663.7 | 5.9 | 2.5 | 29.3 | 0.4 | 0 | 25 | 0.183 | 39 |  | 3 | 0.083 | DGA is assessed as acceptable. | Other test results are assessed as acceptable.
33000 | 1965 | 46 | 222.5 | 35 | 199.3 | 2484.7 | 3.1 | 1.8 | 17.5 | 0.7 | 0.1 | 22 | 0.184 | 73 |  | 3.7 | 0.067 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1965 | 46 | 254.9 | 32 | 224 | 3060 | 8 | 2 | 20 | 0.6 | 0.3 | 22 | 0.187 | 55 |  | 3 | 0.091 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1965 | 46 | 245.8 | 35 | 218.8 | 2922 | 5.9 | 2 | 17.5 | 0.7 | 0.9 | 19 | 0.226 | 52 |  | 3 | 0.08 | DGA is assessed as acceptable. | Acidity level is high. Other oil quality results are assessed as acceptable.
33000 | 1965 | 46 | 242 | 42 | 219.4 | 3023.1 | 3.6 | 2.1 | 16.3 | 0.6 | 0 | 22 | 0.181 | 38 |  | 3 | 0.064 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable. Corrosive IEC. Non-corrosive ASTM 3B.
33000 | 1965 | 46 | 279.8 | 41.81 | 253.4 | 4779.2 | 0 | 2.8 | 21.8 | 1.8 | 0 | 35 | 0.201 | 31 |  | 3 | 0.074 | DGA is assessed as acceptable. | Acidity level is high. Breakdown voltage is low. DDF and Resistivity are assessed as acceptable.
33000 | 1965 | 46 | 230.1 | 55 | 205.2 | 2808.1 | 4.9 | 2.4 | 16.8 | 0.6 | 0.2 | 29 | 0.18 | 26 |  | 3 | 0.075 | DGA is assessed as acceptable. | Oil quality is poor.
33000 | 1965 | 46 | 274.4 | 48 | 248.7 | 3549.8 | 5.1 | 2.6 | 18 | 0 | 0 | 30 | 0.199 | 48 |  | 3 | 0.071 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1965 | 46 | 495 | 41.81 | 230 | 1813 | 54 | 13 | 27 | 1 | 170 | 19 | 0.117 | 63 |  | 6 | 0.045 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1965 | 46 | 464 | 42 | 181 | 1397 | 57 | 11 | 37 | 2 | 176 | 22 | 0.131 | 62 |  | 4.7 | 0.052 | DGA is assessed as acceptable. Acetylene gas possibly communicating from tapchanger. | Oil quality is assessed as acceptable.
33000 | 1965 | 46 | 786 | 40 | 194 | 2121 | 89 | 22 | 35 | 70 | 376 | 25 | 0.111 | 60 |  | 4.9 | 0.044 | Dissolved gas analysis suggests slight oil overheat. Acetylene gas possibly communicating from tapchanger. | Oil quality is assessed as acceptable.
33000 | 1965 | 46 | 684 | 41.81 | 134 | 1667 | 97 | 21 | 50 | 2 | 380 | 21 | 0.119 | 45 |  | 4.1 | 0.052 | Gas levels have remained stable. | Oil quality is assessed as acceptable.
33000 | 1965 | 46 | 377.4 | 42 | 154.4 | 1902 | 38 | 9 | 32.9 | 3 | 140.1 | 24 | 0.111 | 75 |  | 5 | 0.051 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1965 | 46 | 341.8 | 41 | 123.9 | 1988.3 | 50.1 | 13.2 | 28.2 | 0.2 | 126.2 | 32 | 0.099 | 32 |  | 4 | 0.05 | DGA is assessed as acceptable. | Moisture content is slightly high. Other oil quality results are assessed as acceptable.
33000 | 1965 | 46 | 413.4 | 41 | 141.7 | 2194.9 | 64.7 | 10.6 | 26.3 | 1.2 | 168.9 | 18 | 0.146 | 62 |  | 5 | 0.047 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1965 | 46 | 382 | 35 | 160 | 2785 | 71 | 10 | 24 | 1 | 116 | 35 | 0.095 | 33 |  | 5 | 0.046 | DGA is assessed as acceptable. | Breakdown voltage is slightly low. Other oil quality results are assessed as acceptable.
33000 | 1965 | 46 | 434.9 | 46 | 193.2 | 3135.3 | 63.9 | 12 | 27.4 | 1.5 | 136.9 | 24 | 0.098 | 51 |  | 5 | 0.05 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable. Corrosive IEC. Corrosive ASTM 4A.
33000 | 1965 | 46 | 341.4 | 49 | 149.6 | 3052.1 | 57.4 | 8.8 | 22.6 | 1.7 | 101.3 | 34 | 0.081 | 31 |  | 5 | 0.049 | DGA is assessed as acceptable. | Breakdown voltage is low. Other oil quality results are assessed as acceptable.
33000 | 1965 | 46 | 341.2 | 40 | 150.4 | 3013.1 | 46.1 | 9 | 24.5 | 1.3 | 109.9 | 24 | 0.104 | 57 |  | 5 | 0.044 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1965 | 46 | 294 | 56 | 147 | 2695.6 | 40.6 | 7.2 | 18.8 | 1.1 | 79.3 | 24 | 0.086 | 48 |  | 6 | 0.038 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1965 | 46 | 237.6 | 36 | 95.4 | 2196 | 32.8 | 5.6 | 18 | 1 | 84.8 | 25 | 0.088 | 37 |  | 6 | 0.04 | DGA is assessed as acceptable. | Breakdown voltage is slightly low. Other oil quality results are assessed as acceptable.
33000 | 1965 | 46 | 400 | 37 | 301 | 1946 | 25 | 5 | 33 | 1 | 35 | 23 | 0.242 | 69 |  | 4 | 0.0573 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1965 | 46 | 426 | 32 | 322 | 2105 | 33 | 5 | 28 | 1 | 37 | 16 | 0.294 | 54 |  | 7 | 0.0455 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1965 | 46 | 459 | 53 | 320 | 2163 | 51 | 6 | 35 | 1 | 46 | 25 | 0.223 | 50 |  | 3.3 | 0.071 | Test results satisfactory. Acetylene gas possibly from tapchanger. | Oil quality is assessed as acceptable.
33000 | 1965 | 46 | 315 | 74 | 207 | 1586 | 17 | 2 | 21 | 0 | 68 | 20 | 0.204 | 72 |  | 3.3 | 0.073 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1965 | 46 | 331.5 | 35 | 190.4 | 2307.2 | 23.8 | 4.7 | 29.6 | 3.9 | 79.1 | 27 | 0.21 | 39 |  | 3 | 0.081 | The test results are assessed as acceptable. Acetylene gas possibly from tapchanger. | Oil quality is assessed as acceptable.
33000 | 1965 | 46 | 464.9 | 37 | 251.8 | 2237.1 | 52.9 | 11.6 | 27.1 | 3.4 | 118.1 | 32 | 0.205 | 40 |  | 3 | 0.067 | DGA is assessed as acceptable. | Acidity is high but stable. Other oil quality results are assessed as acceptable.
33000 | 1965 | 46 | 415 | 36 | 224.3 | 3177.4 | 37.3 | 9.9 | 28.2 | 0 | 115.3 | 27 | 0.221 | 35 |  | 3 | 0.074 | DGA is assessed as acceptable. | Acidity level is high but stable. Other oil quality results are assessed as acceptable at present.
33000 | 1965 | 46 | 382.6 | 34.5 | 234.9 | 2352.8 | 31.7 | 7.6 | 22.1 | 0.8 | 85.5 | 32 | 0.181 | 30 |  | 2 | 0.1 | DGA is assessed as acceptable. | Breakdown voltage is low. Other oil quality results are assessed as acceptable.
33000 | 1965 | 46 | 360.7 | 56 | 231.3 | 2609.1 | 32.4 | 8.4 | 18.5 | 1.3 | 68.8 | 34 | 0.199 | 17 |  | 3 | 0.066 | DGA is assessed as acceptable. | Acidity level is high. Breakdown voltage is low. DDF and Resistivity are acceptable. Corrosive IEC. Corrosive ASTM 4A.
33000 | 1965 | 46 | 305.8 | 42 | 223.5 | 2504.9 | 11 | 3.1 | 17.2 | 0.8 | 50.2 | 28 | 0.187 | 68 |  | 3 | 0.067 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable. Corrosive IEC. Corrosive ASTM 4A.
33000 | 1965 | 46 | 371 | 50 | 212.2 | 2293.4 | 39.7 | 7.6 | 18.8 | 1 | 91.7 | 30 | 0.202 | 35 |  | 4 | 0.054 | DGA is assessed as acceptable. | Acidity level is high. Breakdown voltage is low. DDF and Resistivity are assessed as acceptable at present.
33000 | 1965 | 46 | 598 | 75 | 258 | 1496 | 69 | 14 | 39 | 1 | 217 | 41 | 0.206 | 55 |  | 3 | 0.087 | DGA is assessed as acceptable. Acetylene gas possibly from tapchanger. Oil quality is assessed as acceptable.
33000 | 1965 | 46 | 673 | 65 | 349 | 1834 | 39 | 11 | 40 | 1 | 233 | 20 | 0.184 | 40 |  | 4 | 0.062 | Gas levels stable. DGA is assessed as acceptable. Oil quality is assessed as acceptable.
33000 | 1965 | 46 | 1678 | 61 | 281 | 1825 | 228 | 272 | 565 | 51 | 281 | 29 | 0.198 | 48 |  | 3 | 0.08 | Extremely high hydrocarbon gas levels. DGA suggests high temperature overheating.RECOMMEND INVESTIGATE ASAP.
33000 | 1965 | 46 | 388 | 41.81 | 132 | 1259 | 0 | 14 | 152 | 20 | 70 | 17 | 0.218 | 42 |  | 3.9 | 0.058 | Transformer at Northgate for assesssment. EX DARRA.
33000 | 1965 | 46 | 514 | 41.81 | 167 | 911 | 76 | 18 | 53 | 2 | 198 | 34 | 0.016 | 38 |  | 38.5 | 0.012 | Moisture content of oil slightly high; possibly sample contamination. Other test results are assessed as acceptable. Acetylene gas possibly from tap changer.
33000 | 1965 | 46 | 760 | 42 | 163 | 1688 | 107 | 28 | 84 | 2 | 376 | 19 | 0.012 | 25 |  | 56.9 | 0.009 | DGA is assessed as acceptable. Oil quality is assessed as acceptable.
33000 | 1965 | 46 | 631 | 28 | 247 | 2741.3 | 68.3 | 13.9 | 77.3 | 7.9 | 216.6 | 34 | 0.014 | 29 |  | 43 | 0.009 | Moisture content of sample is high. Breakdown voltage of sample is slightly low. Dissolved gas analysis is assessed as acceptable. Acetylene gas possibly communicating from tapchanger. RECOMMEND RESAMPLE TO CONFIRM MOISTURE AND BREAKDOWN VOLTAGE.
33000 | 1965 | 46 | 461.8 | 44 | 219.6 | 2226.3 | 46.8 | 10 | 49.2 | 3.7 | 132.5 | 29 | 0.013 | 42 |  | 28 | 0.018 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1965 | 46 | 570.6 | 50 | 259.3 | 1980.6 | 51.3 | 12.3 | 64.7 | 0.3 | 182.7 | 18 | 0.016 | 66 |  | 20 | 0.022 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1965 | 46 | 454.5 | 48 | 225 | 1867.1 | 22.4 | 7.4 | 56.3 | 1.3 | 142.1 | 12 | 0.032 | 71 |  | 25 | 0.015 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1965 | 46 | 217 | 40 | 189 | 865 | 0 | 1 | 26 | 0 | 1 | 10 | 0.036 | 48 |  | 25 | 0.021 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1965 | 46 | 266 | 46 | 189 | 1152 | 40 | 2 | 34 | 1 | 0 | 25 | 0.047 | 51 |  | 15.3 | 0.024 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1965 | 46 | 172 | 42 | 141 | 1034 | 0 | 1 | 29 | 0 | 1 | 11 | 0.061 | 65 |  | 14.2 | 0.032 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1965 | 46 | 194 | 37 | 158 | 1030 | 16 | 1 | 19 | 0 | 0 | 13 | 0.041 | 75 |  | 14.2 | 0.018 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1965 | 46 | 513.5 | 38 | 200.1 | 1868.7 | 275 | 2 | 35.6 | 0.7 | 0.1 | 13 | 0.046 | 68 |  | 12 | 0.024 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1965 | 46 | 460.9 | 35 | 238.6 | 2185.5 | 186.1 | 2 | 32.4 | 0.6 | 1.2 | 21 | 0.049 | 49 |  | 9 | 0.029 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1965 | 46 | 404.6 | 40 | 230.3 | 1905 | 146 | 1.8 | 26.5 | 0 | 0 | 16 | 0.052 | 75 |  | 8 | 0.03 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1965 | 46 | 382.6 | 38 | 247.7 | 2051.7 | 102.5 | 2 | 30.1 | 0.3 | 0 | 16 | 0.074 | 36 |  | 8 | 0.032 | DGA is assessed as acceptable. | Breakdown voltage is marginal. Other oil quality results are assessed as acceptable.
33000 | 1965 | 46 | 340.2 | 46 | 241.3 | 2222.7 | 59.9 | 1.7 | 36.9 | 0.4 | 0 | 17 | 0.048 | 75 |  | 9 | 0.032 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable. Corrosive IEC. Corrosive ASTM 4A.
33000 | 1965 | 46 | 861.2 | 41.81 | 303 | 2680.3 | 512.3 | 2.9 | 41.6 | 1.4 | 0 | 19 | 0.066 | 73 |  | 5 | 0.05 | Hydrogen level is increased. | Oil quality is assessed as acceptable.
33000 | 1965 | 46 | 391.9 | 16 | 255.7 | 2257.9 | 98.1 | 1.8 | 35.6 | 0.7 | 0 | 17 | 0.061 | 58 |  | 7 | 0.033 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1965 | 46 | 721.8 | 42 | 297.8 | 2759.1 | 379.4 | 2 | 42 | 0.6 | 0 | 19 | 0.06 | 50 |  | 6 | 0.043 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1965 | 46 | 372 | 41.81 | 186 | 1546 | 21 | 19 | 54 | 4 | 88 | 19 | 0.109 | 70 |  | 7 | 0.037 | Gas levels considerably reduced.
33000 | 1965 | 46 | 225 | 48 | 202 | 1603 | 5 | 2 | 12 | 1 | 3 | 15 | 0.116 | 52 |  | 4.9 | 0.052 | DGA is assessed as acceptable.
33000 | 1965 | 46 | 164 | 40 | 143 | 1377 | 4 | 2 | 10 | 1 | 4 | 14 | 0.144 | 65 |  | 4.2 | 0.047 | DGA is assessed as acceptable.
33000 | 1965 | 46 | 188 | 50 | 175 | 1682 | 1 | 1 | 10 | 0 | 1 | 19 | 0.135 | 65 |  | 4.7 | 0.053 | DGA is assessed as acceptable.
33000 | 1965 | 46 | 308.8 | 52 | 279.2 | 2239.7 | 9 | 2.4 | 16.9 | 0.8 | 0.5 | 11 | 0.157 | 75 |  | 4 | 0.067 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1965 | 46 | 445.8 | 51 | 405.3 | 3161.3 | 19.7 | 3.5 | 16.2 | 0.9 | 0.2 | 19 | 0.148 | 64 |  | 3 | 0.066 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1965 | 46 | 437 | 40 | 408.6 | 2948.2 | 11.5 | 2.9 | 12.9 | 1 | 0.1 | 19 | 0.152 | 71 |  | 3.5 | 0.074 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1965 | 46 | 401.7 | 46 | 355.2 | 2786 | 27.4 | 3.1 | 10.5 | 0.6 | 4.9 | 16 | 0.217 | 75 |  | 3 | 0.067 | DGA is assessed as acceptable. | Acidity level is high. Other oil quality results are assessed as acceptable.
33000 | 1965 | 46 | 234 | 40 | 197 | 945 | 0 | 1 | 34 | 1 | 1 | 7 | 0.03 | 70 |  | 20 | 0.023 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1965 | 46 | 237 | 41 | 197 | 1042 | 0 | 0 | 39 | 1 | 0 | 11 | 0.063 | 51 |  | 14 | 0.025 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1965 | 46 | 248 | 48 | 180 | 1059 | 36 | 1 | 30 | 0 | 1 | 24 | 0.049 | 49 |  | 13 | 0.028 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1965 | 46 | 207 | 38 | 176 | 1079 | 0 | 1 | 29 | 0 | 1 | 11 | 0.054 | 54 |  | 12.8 | 0.029 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1965 | 46 | 221 | 64 | 192 | 1262 | 2 | 2 | 24 | 0 | 1 | 14 | 0.054 | 73 |  | 9.9 | 0.029 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1965 | 46 | 221.9 | 41.81 | 175.6 | 1902.6 | 5.5 | 2 | 35.1 | 1 | 2.7 | 10 | 0.064 | 60 |  | 9 | 0.028 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1965 | 46 | 272.6 | 40 | 212.6 | 2422.9 | 8.2 | 2 | 40.8 | 0.8 | 8.2 | 16 | 0.068 | 75 |  | 8 | 0.028 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1965 | 46 | 279.9 | 40 | 234.5 | 1983.2 | 7.4 | 1.9 | 31.4 | 0 | 4.7 | 12 | 0.073 | 75 |  | 8 | 0.03 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1965 | 46 | 229.7 | 35 | 191.5 | 1684.1 | 4.4 | 1.9 | 27.5 | 0.9 | 3.5 | 13 | 0.08 | 47 |  | 8 | 0.032 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1965 | 46 | 242.7 | 47 | 197.6 | 1962.9 | 4.7 | 1.5 | 33.8 | 0.9 | 4.2 | 12 | 0.07 | 75 |  | 8 | 0.032 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable. Corrosive IEC. Non-corrosive ASTM 3B.
33000 | 1965 | 46 | 278.6 | 41.81 | 229.5 | 2161 | 6.1 | 1.7 | 36.6 | 1 | 3.7 | 13 | 0.087 | 98 |  | 8 | 0.029 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1965 | 46 | 274.5 | 42 | 226.8 | 2312.3 | 5.2 | 1.6 | 37.1 | 0.6 | 3.2 | 15 | 0.077 | 72 |  | 7 | 0.032 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1965 | 46 | 161 | 46 | 158 | 1000 | 0 | 1 | 0 | 1 | 1 | 12 | 0.021 | 66 |  | 27.9 | 0.024 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1965 | 46 | 202 | 32 | 160 | 1394 | 15 | 1 | 26 | 0 | 0 | 37 | 0.022 | 42 |  | 37 | 0.009 | DGA is assessed as acceptable. | Moisture content is high. Possible sample contamination. Other results are assessed as acceptable.
33000 | 1965 | 46 | 159.5 | 38 | 123.3 | 1190.2 | 4.6 | 1.5 | 27.5 | 0.4 | 2.2 | 14 | 0.027 | 69 |  | 17 | 0.021 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1965 | 46 | 250.4 | 42 | 221.6 | 1248.5 | 5.4 | 1.4 | 20.6 | 0.3 | 1.1 | 22 | 0.025 | 47 |  | 17 | 0.02 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1965 | 46 | 312.6 | 46 | 278.7 | 1927.6 | 4.1 | 1.5 | 28.3 | 0 | 0 | 22 | 0.035 | 66 |  | 15 | 0.028 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1965 | 46 | 513.6 | 32 | 407 | 1738.1 | 47.1 | 5.9 | 38.7 | 1.7 | 13.2 | 18 | 0.041 | 74 |  | 17 | 0.021 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1965 | 46 | 293.4 | 40 | 263.1 | 1572.4 | 3.5 | 1.6 | 24.1 | 0.4 | 0.7 | 23 | 0.034 | 53 |  | 14 | 0.022 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1965 | 46 | 266 | 52 | 236.5 | 1965.1 | 0 | 1.2 | 27 | 1 | 0.3 | 30 | 0.053 | 25 |  | 16 | 0.022 | DGA is assessed as acceptable. | Breakdown voltage is low. Other oil quality results are assessed as acceptable.
33000 | 1965 | 46 | 273.7 | 38 | 239.9 | 1996.6 | 3.6 | 1.7 | 27 | 0.4 | 1.1 | 33 | 0.055 | 29 |  | 10 | 0.033 | DGA is assessed as acceptable. | Breakdown voltage is low. Other oil quality results are assessed as acceptable.
33000 | 1965 | 46 | 217.3 | 50 | 190.2 | 1490.8 | 3.2 | 1.4 | 22 | 0.2 | 0.3 | 28 | 0.041 | 28 |  | 16 | 0.022 | DGA is assessed as acceptable. | Breakdown voltage is low. Other oil quality results are assessed as acceptable.
33000 | 1964 | 47 | 186 | 27 | 149 | 1198 | 9 | 2 | 23 | 0 | 3 | 18 | 0.062 | 69 |  | 25 | 0.019 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1964 | 47 | 172 | 32 | 140 | 1340 | 0 | 3 | 24 | 5 | 0 | 17 | 0.076 | 67 |  | 9 | 0.034 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1964 | 47 | 187 | 43 | 151 | 3776 | 0 | 2 | 33 | 1 | 0 | 19 | 0.085 | 50 |  | 11.9 | 0.027 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1964 | 47 | 222 | 56 | 191 | 2653 | 1 | 1 | 29 | 0 | 0 | 27 | 0.089 | 30 |  | 7.8 | 0.028 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1964 | 47 | 237.9 | 47 | 191.9 | 2181.4 | 4 | 2.8 | 38.5 | 0.4 | 0.3 | 19 | 0.103 | 41 |  | 7 | 0.031 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1964 | 47 | 223.8 | 51 | 188.3 | 2239.9 | 4 | 1.4 | 29.3 | 0.5 | 0.3 | 33 | 0.096 | 36 |  | 6 | 0.036 | Dissolved gas analysis is assessed as acceptable. | Moisture content is high. Other oil quality results are assessed as acceptable.
33000 | 1964 | 47 | 424.5 | 50 | 369.9 | 3895.9 | 6.3 | 2.4 | 45.6 | 0 | 0.3 | 31 | 0.119 | 31 |  | 6 | 0.048 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1964 | 47 | 255.6 | 54 | 221.4 | 2660.2 | 2.9 | 1.5 | 29.6 | 0.2 | 0 | 25 | 0.131 | 56 |  | 5 | 0.045 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1964 | 47 | 331.1 | 45 | 290.4 | 2877.5 | 5.9 | 1.7 | 32.7 | 0.4 | 0 | 32 | 0.135 | 23 |  | 5 | 0.041 | DGA is assessed as acceptable. | Breakdown voltage is low. Other oil quality results are assessed as acceptable.
33000 | 1964 | 47 | 178.6 | 52 | 152 | 2091 | 3 | 1.4 | 22 | 0.2 | 0 | 30 | 0.145 | 30 |  | 5 | 0.039 | DGA is assessed as acceptable. | Breakdown voltage is low. Other oil quality results are assessed as acceptable. Corrosive IEC. Non-corrosive ASTM 3B.
33000 | 1964 | 47 | 134.9 | 44 | 117.3 | 1471.5 | 0 | 2.4 | 14.9 | 0.3 | 0 | 22 | 0.129 | 54 |  | 5 | 0.048 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable. Corrosive IEC. Corrosive ASTM 4A.
33000 | 1964 | 47 | 83 | 41.81 | 69 | 911 | 0 | 1 | 10 | 3 | 0 | 24 | 0.02 | 39 |  | 29.3 | 0.014 | Test results are assessed as acceptable.
33000 | 1964 | 47 | 49 | 41.81 | 33 | 821 | 3 | 2 | 9 | 1 | 1 | 6 | 0.014 | 63 |  | 41.3 | 0.011 | Test results are assessed as acceptable.
33000 | 1964 | 47 | 163 | 31 | 129 | 1476 | 0 | 1 | 33 | 0 | 0 | 41 | 0.132 | 47 |  | 4 | 0.061 | DGA is assessed as acceptable. | Moisture content of oil slightly high. Other test results satisfactory.
33000 | 1964 | 47 | 220 | 30 | 179 | 1806 | 0 | 2 | 36 | 1 | 2 | 23 | 0.132 | 36 |  | 3.6 | 0.061 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1964 | 47 | 273 | 42 | 232 | 1981 | 0 | 2 | 39 | 0 | 0 | 27 | 0.133 | 67 |  | 3.4 | 0.065 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1964 | 47 | 231 | 37 | 186 | 2142 | 3 | 4 | 35 | 3 | 0 | 23 | 0.159 | 47 |  | 2.9 | 0.065 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1964 | 47 | 346.5 | 52 | 285.4 | 2779.8 | 4.4 | 2 | 53.8 | 0.9 | 0 | 28 | 0.2 | 45 |  | 2 | 0.084 | DGA is assessed as acceptable. | Acidity level is high. Other oil quality results are assessed as acceptable.
33000 | 1964 | 47 | 456 | 44 | 384.7 | 5284.5 | 4.2 | 2.4 | 63.7 | 1 | 0 | 21 | 0.214 | 56 |  | 2.5 | 0.094 | DGA is assessed as acceptable. | Acidity level is high but stable. Other oil quality results are assessed as acceptable.
33000 | 1964 | 47 | 434.7 | 40 | 378.3 | 5269 | 5.1 | 2.5 | 48.8 | 0 | 0 | 53 | 0.252 | 14 |  | 1 | 0.162 | DGA is assessed as acceptable. | Oil quality is poor.
33000 | 1964 | 47 | 480 | 48 | 425.8 | 6428.4 | 4.8 | 2.8 | 46.2 | 0.4 | 0 | 56 | 0.246 | 15 |  | 2 | 0.103 | DGA is assessed as acceptable. | Oil quality is poor. Corrosive IEC. Non-corrosive ASTM 3B.
33000 | 1964 | 47 | 158 | 37 | 133 | 1372 | 0 | 1 | 23 | 1 | 0 | 16 | 0.099 | 28 |  | 7.5 | 0.033 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1964 | 47 | 168 | 44 | 142 | 1331 | 0 | 0 | 24 | 0 | 2 | 22 | 0.114 | 44 |  | 7.4 | 0.032 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable. PCB contaminated oil.
33000 | 1964 | 47 | 194 | 32 | 167 | 1349 | 0 | 1 | 26 | 0 | 0 | 21 | 0.098 | 65 |  | 6.6 | 0.04 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1964 | 47 | 184 | 36 | 152 | 1571 | 0 | 2 | 29 | 1 | 0 | 28 | 0.105 | 54 |  | 7.6 | 0.035 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable. PCB contaminated oil.
33000 | 1964 | 47 | 184 | 38 | 160 | 1528 | 0 | 1 | 23 | 0 | 0 | 25 | 0.12 | 75 |  | 5.9 | 0.04 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1964 | 47 | 183.3 | 40 | 146.3 | 2195.8 | 0 | 1.4 | 34.4 | 0.6 | 0.6 | 21 | 0.145 | 60 |  | 5 | 0.042 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1964 | 47 | 293.5 | 38 | 242.4 | 3534.3 | 3.7 | 1.8 | 44.6 | 0.5 | 0.5 | 30 | 0.158 | 55 |  | 5 | 0.046 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1964 | 47 | 226.1 | 40 | 202.6 | 1822.6 | 0 | 1.3 | 22.2 | 0 | 0 | 20 | 0.132 | 75 |  | 4 | 0.046 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1964 | 47 | 214.2 | 21 | 189.3 | 1714 | 3 | 1.5 | 20.1 | 0.3 | 0 | 21 | 0.176 | 75 |  | 3 | 0.086 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable. Corrosive IEC. Non-corrosive ASTM 2C.
33000 | 1964 | 47 | 214.5 | 41.81 | 191.6 | 1941.3 | 3.6 | 0.1 | 18.9 | 0.3 | 0 | 22 | 0.201 | 54 |  | 4 | 0.05 | DGA is assessed as acceptable. | Acidity level is high. Other oil quality results are assessed as acceptable.
33000 | 1964 | 47 | 193.7 | 42 | 170.4 | 1779.3 | 2.1 | 2.1 | 19 | 0.1 | 0 | 26 | 0.18 | 60 |  | 4 | 0.048 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1964 | 47 | 188.3 | 30 | 168.8 | 1774.8 | 0 | 1.1 | 18.2 | 0.2 | 0 | 18 | 0.164 | 55 |  | 4 | 0.055 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1964 | 47 | 226 | 36 | 179 | 1596 | 0 | 1 | 46 | 0 | 0 | 13 | 0.162 | 66 |  | 2.5 | 0.137 | Test results satisfactory. | Oil quality is assessed as acceptable.
33000 | 1964 | 47 | 285 | 35 | 217 | 1984 | 0 | 3 | 59 | 4 | 2 | 22 | 0.137 | 57 |  | 1.8 | 0.168 | Test results satisfactory. | Oil quality is assessed as acceptable.
33000 | 1964 | 47 | 328 | 32 | 263 | 2411 | 0 | 2 | 62 | 1 | 0 | 27 | 0.136 | 55 |  | 2.4 | 0.152 | Test results satisfactory. | Oil quality is assessed as acceptable.
33000 | 1964 | 47 | 367 | 40 | 282 | 2161 | 5 | 2 | 77 | 0 | 1 | 22 | 0.139 | 67 |  | 1.5 | 0.171 | Test results are assessed as acceptable.
33000 | 1964 | 47 | 436.9 | 35 | 366.3 | 2517.4 | 6.5 | 2.5 | 60.8 | 0.8 | 0 | 13 | 0.184 | 74 |  | 1 | 0.197 | DDF approaching acceptance limit. Other test results are assessed as acceptable.
33000 | 1964 | 47 | 414 | 32 | 351.9 | 2807.7 | 6.2 | 1.4 | 53.6 | 0.9 | 0 | 26 | 0.182 | 54 |  | 1 | 0.2 | Acidity and DDF levels are trending upwards. Other test results are assessed as acceptable.
33000 | 1964 | 47 | 331.4 | 30 | 271.4 | 2857 | 5.4 | 1.9 | 51.9 | 0.6 | 0.2 | 26 | 0.201 | 75 |  | 2 | 0.159 | DGA is assessed as acceptable. | Acidity level is high. Other oil quality results are assessed as acceptable.
33000 | 1964 | 47 | 298.3 | 38 | 254.5 | 2481.3 | 4 | 1.5 | 38 | 0.3 | 0 | 17 | 0.244 | 75 |  | 2 | 0.143 | DGA is assessed as acceptable. | Acidity level is high. Other oil quality results are assessed as acceptable.
33000 | 1964 | 47 | 318.7 | 39 | 277 | 2422.2 | 3.8 | 1.5 | 36.1 | 0.3 | 0 | 23 | 0.207 | 72 |  | 2 | 0.141 | DGA is assessed as acceptable. | Acidity level is high. Other oil quality results are assessed as acceptable. Corrosive IEC. Non-corrosive ASTM 3A.
33000 | 1964 | 47 | 295.1 | 41.81 | 255.1 | 2651.3 | 0 | 2.6 | 37.4 | 0 | 0 | 19 | 0.236 | 70 |  | 2 | 0.115 | DGA is assessed as acceptable. | Acidity level is high. Other oil quality results are assessed as acceptable.
33000 | 1964 | 47 | 324.3 | 36 | 280.8 | 2984.7 | 0 | 1.6 | 41.4 | 0.5 | 0 | 20 | 0.213 | 69 |  | 2 | 0.099 | DGA is assessed as acceptable. | Acidity level is high. Other oil quality results are assessed as acceptable.
33000 | 1964 | 47 | 345 | 40 | 199 | 1888 | 43 | 4 | 14 | 2 | 83 | 10 | 0.06 | 60 |  | 15 | 0.011 | Test results satisfactory. | Oil quality is assessed as acceptable.
33000 | 1964 | 47 | 263 | 35 | 214 | 1734 | 0 | 2 | 44 | 3 | 0 | 31 | 0.123 | 36 |  | 3 | 0.075 | Test results satisfactory. | Oil quality is assessed as acceptable.
33000 | 1964 | 47 | 133 | 54 | 94 | 1670 | 0 | 1 | 38 | 0 | 0 | 11 | 0.146 | 40 |  | 3.6 | 0.067 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1964 | 47 | 403 | 41.81 | 358 | 3434 | 5 | 3 | 36 | 1 | 0 | 15 | 0.018 | 62 |  | 30.5 | 0.011 | Test results satisfactory. | Oil quality is assessed as acceptable.
33000 | 1964 | 47 | 151 | 40 | 127 | 1586 | 0 | 1 | 23 | 0 | 0 | 12 | 0.02 | 62 |  | 17 | 0.017 | Carbon oxides have decreased. Test results are assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1964 | 47 | 150 | 60 | 126 | 1225 | 0 | 1 | 23 | 0 | 0 | 9 | 0.025 | 75 |  | 18 | 0.016 | Test results are assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1964 | 47 | 134 | 25 | 110 | 1223 | 0 | 1 | 23 | 0 | 0 | 5 | 0.027 | 73 |  | 16 | 0.017 | Test results are assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1964 | 47 | 171.3 | 26 | 149.5 | 1200.5 | 4.2 | 1 | 16.2 | 0.2 | 0.2 | 18 | 0.153 | 75 |  | 2.7 | 0.091 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1964 | 47 | 20.2 | 26 | 6.9 | 698.7 | 1 | 0.8 | 1.5 | 1.3 | 8.7 | 16 | 0.01 | 38 |  | 296 | 0.002 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1964 | 47 | 228 | 28 | 154 | 1668 | 0 | 3 | 58 | 2 | 11 | 16 | 0.116 | 72 |  | 4 | 0.056 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1964 | 47 | 333 | 40 | 275 | 2325 | 0 | 1 | 57 | 0 | 0 | 29 | 0.112 | 54 |  | 4 | 0.058 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1964 | 47 | 325 | 40 | 281 | 2105 | 2 | 2 | 40 | 0 | 0 | 22 | 0.122 | 66 |  | 2.4 | 0.083 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1964 | 47 | 22.2 | 41.81 | 9.7 | 174.2 | 0 | 1 | 1.9 | 1.1 | 8.5 | 6 | 0 | 75 |  | 41 | 0.017 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1964 | 47 | 7.9 | 27 | 5.7 | 164.9 | 2 | 0.2 | 0 | 0 | 0 | 10 | 0.01 | 75 |  | 28 | 0.017 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1964 | 47 | 12.5 | 28 | 10.3 | 739.9 | 0 | 1 | 0 | 0 | 1.2 | 24 | 0.01 | 37 |  | 172 | 0.004 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1964 | 47 | 5.3 | 28 | 5.1 | 160.2 | 0 | 0.2 | 0 | 0 | 0 | 8 | 0.01 | 75 |  | 24 | 0.021 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1964 | 47 | 161 | 45 | 157 | 2061 | 0 | 1 | 1 | 0 | 2 | 18 | 0.053 | 66 |  | 30 | 0.014 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1964 | 47 | 211 | 39 | 193 | 2400 | 0 | 1 | 13 | 1 | 3 | 9 | 0.037 | 50 |  | 30 | 0.016 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1964 | 47 | 266 | 41.81 | 207 | 1921 | 35 | 4 | 13 | 1 | 6 | 10 | 0.05 | 58 |  | 19.7 | 0.016 | DGA is assessed as acceptable. No evidence of abnormality in main tank oil sample. | Oil quality is assessed as acceptable.
33000 | 1964 | 47 | 168 | 66 | 131 | 1834 | 0 | 3 | 19 | 1 | 14 | 15 | 0.058 | 54 |  | 18.9 | 0.022 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1964 | 47 | 236 | 42 | 111 | 1489 | 11 | 7 | 21 | 3 | 83 | 8 | 0.044 | 72 |  | 15.9 | 0.02 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1964 | 47 | 166.9 | 39 | 124.4 | 2453.6 | 9.9 | 1.8 | 17.4 | 1.3 | 12.1 | 9 | 0.041 | 75 |  | 13 | 0.02 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1964 | 47 | 222.1 | 45 | 190.8 | 2413.6 | 10.1 | 1.9 | 11.6 | 1 | 6.7 | 16 | 0.04 | 52 |  | 14 | 0.019 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1964 | 47 | 208 | 48 | 183 | 2592 | 13 | 3 | 5 | 2 | 2 | 23 | 0.066 | 63 |  | 18 | 0.019 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1964 | 47 | 153 | 40 | 136 | 2613 | 8 | 2 | 4 | 1 | 2 | 12 | 0.06 | 63 |  | 10 | 0.032 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1964 | 47 | 239 | 44 | 228 | 2885 | 0 | 2 | 7 | 1 | 1 | 11 | 0.084 | 67 |  | 13.1 | 0.024 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1964 | 47 | 273 | 45 | 255 | 2759 | 7 | 3 | 7 | 1 | 0 | 11 | 0.082 | 68 |  | 9.9 | 0.026 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1964 | 47 | 276.5 | 39 | 240.7 | 3696.3 | 24.5 | 2.9 | 5.8 | 1.8 | 0.8 | 13 | 0.092 | 75 |  | 9 | 0.028 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1964 | 47 | 595.5 | 35 | 356.9 | 3505.2 | 106.5 | 91.7 | 24.6 | 7.8 | 8 | 22 | 0.092 | 31 |  | 8 | 0.028 | Dissolved gas levels are stable. | Oil quality is assessed as acceptable.
33000 | 1964 | 47 | 595.1 | 25 | 360.4 | 3521.1 | 107.2 | 88.6 | 23.8 | 7.5 | 7.6 | 27 | 0.105 | 43 |  | 8 | 0.028 | Dissolved gas levels are stable. . | Oil quality is assessed as acceptable.
33000 | 1964 | 47 | 305.9 | 45 | 264.9 | 3271.9 | 19.8 | 9.9 | 7.3 | 3 | 1 | 18 | 0.09 | 58 |  | 8 | 0.029 | Dissolved gas levels are reduced. Dissolved gas analysis is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1964 | 47 | 255 | 41.81 | 235 | 1433 | 0 | 1 | 17 | 1 | 1 | 19 | 0.097 | 65 |  | 7 | 0.038 | DGA is assessed as acceptable.
33000 | 1964 | 47 | 234 | 45 | 221 | 1766 | 0 | 2 | 10 | 0 | 1 | 20 | 0.105 | 52 |  | 1.1 | 0.254 | Loss tangent of oil outside recommended limits. RECOMMEND RESAMPLE IN 1 YEAR TO MONITOR.
33000 | 1964 | 47 | 302 | 40 | 282 | 2028 | 6 | 2 | 11 | 0 | 1 | 14 | 0.135 | 70 |  | 1.4 | 0.248 | Oil quality poor. Other test results satisfactory. RECOMMEND RESAMPLE IN 1 YEAR TO MONITOR.
33000 | 1964 | 47 | 299 | 46 | 281 | 2110 | 5 | 2 | 10 | 0 | 1 | 25 | 0.127 | 43 |  | 0.94 | 0.305 | Oil quality poor. Other test results are assessed as acceptable.
33000 | 1964 | 47 | 257 | 50 | 242 | 1646 | 6 | 1 | 8 | 0 | 0 | 21 | 0.117 | 47 |  | 0.81 | 0.387 | Oil quality poor. Other test results are assessed as acceptable.
33000 | 1964 | 47 | 284 | 50 | 264 | 1800 | 10 | 1 | 8 | 0 | 1 | 20 | 0.122 | 66 |  | 0.78 | 0.352 | Oil quality is poor. Other test results are assessed as acceptable.
33000 | 1964 | 47 | 547.7 | 54 | 509.5 | 3307.7 | 27.1 | 3.2 | 6.7 | 1.1 | 0.1 | 14 | 0.166 | 69 |  | 0.55 | 0.59 | DGA is assessed as acceptable.
33000 | 1964 | 47 | 897.4 | 49 | 820.4 | 5244.1 | 65.7 | 2 | 7.7 | 1.4 | 0.2 | 39 | 0.19 | 68 |  | 0.43307 | 0.6622 | DGA is assessed as acceptable.
33000 | 1964 | 47 | 721.6 | 44 | 675.3 | 4461.9 | 35.8 | 3.8 | 5.1 | 1.6 | 0 | 26 | 0.186 | 45 |  | 0.4 | 0.764 | DGA is assessed as acceptable. | DDF is high and Resistivity is low. Other oil quality results are assessed as acceptable.
33000 | 1964 | 47 | 718.7 | 47 | 676.6 | 5209 | 30.5 | 4.3 | 6.1 | 1.2 | 0 | 20 | 0.182 | 75 |  | 0.34 | 0.828 | DGA is assessed as acceptable. | DDF is high and Resistivity is low. Other oil quality results are assessed as acceptable.
33000 | 1964 | 47 | 600.2 | 48 | 562.4 | 4506 | 29.3 | 3.5 | 4.3 | 0.7 | 0 | 26 | 0.226 | 50 |  | 0.28 | 0.866 | DGA is assessed as acceptable. | Acidity level is high. DDF is high and Resistivity is low. Oil is very dark in appearance.
33000 | 1964 | 47 | 526 | 45 | 454 | 4506 | 51 | 11 | 6 | 4 | 0 | 19 | 0.233 | 62 |  | 0.177 | 1.588 | DGA is assessed as acceptable. | Breakdown voltage is assessed as acceptable. Acidity level is high. DDF is high and Resistivity is low.
33000 | 1964 | 47 | 311 | 47 | 287.3 | 3183.3 | 15.7 | 2.7 | 3.3 | 1.8 | 0.2 | 26 | 0.213 | 55 |  | 0.177 | 1.437 | DGA is assessed as acceptable. | Breakdown voltage is assessed as acceptable. DDF is high and Resistivity is low. Acidity level is high.
33000 | 1964 | 47 | 310.7 | 52 | 286.6 | 3015.2 | 16.5 | 2.8 | 3.3 | 1.3 | 0.2 | 27 | 0.215 | 72 |  | 0.185 | 1.521 | DGA is assessed as acceptable. | Breakdown voltage is assessed as acceptable. Acidity level is high. DDF is high and Resistivity is low.
33000 | 1964 | 47 | 355.2 | 50 | 327.1 | 3306.9 | 20.5 | 2.6 | 3.6 | 1.3 | 0.1 | 27 | 0.216 | 43 |  | 0.121 | 1.99 | DGA is assessed as acceptable. | Oil quality is poor.
33000 | 1964 | 47 | 275.5 | 50 | 256.6 | 2815.1 | 12.5 | 3.1 | 2.4 | 0.9 | 0 | 26 | 0.213 | 48 |  | 0.12 | 1.871 | DGA is assessed as acceptable. | Oil quality is poor.
33000 | 1964 | 47 | 172 | 41.81 | 155 | 711 | 0 | 1 | 15 | 1 | 0 | 11 | 0.027 | 64 |  | 51.4 | 0.011 | DGA levels low as transformer is in storage at Northgate.
33000 | 1964 | 47 | 191 | 49 | 157 | 1302 | 0 | 3 | 27 | 1 | 3 | 16 | 0.017 | 66 |  | 26.3 | 0.019 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1964 | 47 | 215 | 48 | 179 | 1596 | 4 | 2 | 29 | 1 | 0 | 12 | 0.027 | 58 |  | 22.2 | 0.018 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1964 | 47 | 158 | 28 | 130 | 1099 | 1 | 2 | 22 | 1 | 2 | 9 | 0.031 | 73 |  | 32 | 0.013 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1964 | 47 | 248 | 56 | 192 | 2057 | 13 | 5 | 34 | 2 | 2 | 18 | 0.025 | 49 |  | 29.6 | 0.012 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1964 | 47 | 264.1 | 43 | 219.4 | 2492.1 | 3.2 | 5.6 | 32.5 | 3.4 | 0 | 15 | 0.028 | 53 |  | 17 | 0.018 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1964 | 47 | 291.2 | 44 | 233.8 | 2286.3 | 21.5 | 2 | 30.6 | 1.6 | 1.7 | 17 | 0.038 | 58 |  | 12 | 0.022 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1964 | 47 | 390.4 | 49 | 339.6 | 3254.2 | 7.2 | 5.9 | 35.9 | 0.9 | 0.9 | 20 | 0.04 | 75 |  | 16 | 0.02 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable. Corrosive IEC. Non-corrosive ASTM 3B.
33000 | 1964 | 47 | 234.8 | 40 | 198.7 | 2245.9 | 2.7 | 0.5 | 31.6 | 0 | 1.3 | 17 | 0.046 | 46 |  | 16 | 0.017 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1964 | 47 | 1080.8 | 60 | 12.9 | 712.5 | 303.1 | 53.4 | 73.5 | 3.8 | 634.1 | 44 | 0.001 | 18 |  | 866 | 0.001 | DGA is assessed as acceptable. | Breakdown voltage is low. Other oil quality results are assessed as acceptable. Particle contamination load is high.
33000 | 1964 | 47 | 227.3 | 42 | 200.1 | 1926.9 | 0 | 1.5 | 25.2 | 0.5 | 0 | 19 | 0.043 | 84 |  | 14 | 0.021 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1963 | 48 | 513 | 41.81 | 426 | 6173 | 46 | 11 | 13 | 7 | 10 | 38 | 0.253 | 52 |  | 6 | 0.042 | DGA is assessed as acceptable.
33000 | 1963 | 48 | 759 | 41.81 | 648 | 9110 | 61 | 15 | 15 | 8 | 12 | 41 | 0.3165 | 64 |  | 7.4 | 0.034 | Moisture and acidity levels of oil high. Other test results satisfactory.
33000 | 1963 | 48 | 945 | 41.81 | 781 | 9150 | 120 | 18 | 10 | 9 | 7 | 49 | 0.404 | 32 |  | 8 | 0.027 | Acidity level is high. Moisture content of oil is high. 2-Furfural is above 1PPM. Other test results are assessed as acceptable.
33000 | 1963 | 48 | 576.3 | 41.81 | 436 | 8321.7 | 99.5 | 12.1 | 14.1 | 10.8 | 3.8 | 28 | 0.482 | 41 |  | 5 | 0.039 | 2-furfural level is high and trending upwards suggesting accelerated rate of insulation degradation. Acidity level of sample is high. Other test results are assessed as acceptable. RECOMMEND RESAMPLE IN 6 MONTHS TO MONITOR TREND. RECOMMEND OIL CHANGE
33000 | 1963 | 48 | 908.3 | 41.81 | 741.5 | 9090.9 | 128.7 | 14.7 | 11.5 | 9.1 | 2.8 | 50 | 0.464 | 26 |  | 6.1 | 0.039 | DGA is assessed as acceptable. | Oil quality is poor.
33000 | 1963 | 48 | 504.4 | 41.81 | 415 | 5664.8 | 67 | 7.4 | 6.7 | 6.1 | 2.2 | 54 | 0.465 | 58 |  | 4 | 0.046 | DGA is assessed as acceptable. | Moisture content is high. Acidity level is high. Other oil quality results are assessed as acceptable.
33000 | 1963 | 48 | 550.7 | 41.81 | 467.1 | 6656.3 | 62 | 7.7 | 7.4 | 5.3 | 1.2 | 34 | 0.651 | 70 |  | 5 | 0.045 | DGA is assessed as acceptable. | Moisture content is high. Acidity level is high. Other oil quality results are assessed as acceptable at present.
33000 | 1963 | 48 | 612.4 | 41.81 | 526.1 | 7169 | 64.9 | 10.4 | 6 | 4.9 | 0.1 | 35 | 0.475 | 29 |  | 7 | 0.032 | DGA is assessed as acceptable. | Acidity level is high. Breakdown voltage is low. DDF and Resistivity are assessed as acceptable. Corrosive IEC. Non-corrosive ASTM 3B.
33000 | 1963 | 48 | 394.5 | 20 | 343.9 | 6648.7 | 37.3 | 3.7 | 4.7 | 4.9 | 0 | 36 | 0.515 | 40 |  | 7 | 0.03 | DGA is assessed as acceptable. | Acidity level is high. Other oil quality results are assessed as acceptable.
33000 | 1963 | 48 | 376.3 | 20 | 322.7 | 5889.6 | 38.5 | 5.6 | 5.3 | 4.2 | 0 | 37 | 0.512 | 46 |  | 7 | 0.029 | DGA is assessed as acceptable. | Acidity level is high. Other oil quality results are assessed as acceptable.
33000 | 1963 | 48 | 700 | 41.81 | 376 | 2592 | 140 | 34 | 89 | 4 | 57 | 15 | 0.136 | 38 |  | 7 | 0.033 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1963 | 48 | 200 | 55 | 177 | 1284 | 0 | 2 | 20 | 1 | 0 | 21 | 0.032 | 46 |  | 36.9 | 0.014 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable. PCB contaminated oil.
33000 | 1963 | 48 | 167 | 29 | 139 | 1319 | 0 | 3 | 24 | 1 | 0 | 17 | 0.017 | 45 |  | 36 | 0.014 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1963 | 48 | 203 | 42 | 172 | 1701 | 0 | 2 | 28 | 1 | 0 | 14 | 0.031 | 72 |  | 36.9 | 0.016 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable. PCB contaminated oil.
33000 | 1963 | 48 | 230 | 48 | 189 | 1569 | 12 | 2 | 26 | 1 | 0 | 15 | 0.025 | 75 |  | 32.1 | 0.013 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1963 | 48 | 217.8 | 41 | 167.1 | 2276.9 | 0 | 2 | 47.2 | 1.2 | 0.3 | 17 | 0.023 | 38 |  | 23 | 0.015 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1963 | 48 | 8 | 24 | 5.7 | 83 | 2.2 | 0.1 | 0 | 0 | 0 | 15 | 0.01 | 72 |  | 96 | 0.007 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1963 | 48 | 14.1 | 24 | 8.1 | 254.4 | 3.1 | 0.7 | 0.2 | 0.6 | 1.4 | 18 | 0.01 | 41 |  | 80 | 0.008 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1963 | 48 | 75.7 | 40 | 66.5 | 1159.5 | 6.8 | 1.1 | 0.7 | 0.1 | 0.5 | 21 | 0 | 38 |  | 45 | 0.012 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1963 | 48 | 75 | 40 | 68.6 | 1458 | 4.5 | 1.3 | 0.6 | 0 | 0 | 12 | 0.01 | 75 |  | 37 | 0.0098 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1963 | 48 | 126.9 | 42 | 112.2 | 1508.4 | 5.5 | 6.9 | 1 | 1.1 | 0.2 | 15 | 0.002 | 37 |  | 40 | 0.01 | DGA is assessed as acceptable. | Breakdown voltage is low. Other oil quality results are assessed as acceptable. Corrosive IEC. Corrosive ASTM 4A.
33000 | 1963 | 48 | 87.3 | 41.81 | 71.1 | 1471.2 | 8.3 | 2.9 | 2.4 | 2.6 | 0 | 31 | 0.004 | 22 |  | 38 | 0.009 | DGA is assessed as acceptable. | Breakdown voltage is low. Other oil quality results are assessed as acceptable.
33000 | 1963 | 48 | 61.3 | 40 | 48.5 | 1451.4 | 5.8 | 2.2 | 1.8 | 3 | 0 | 59 | 0.004 | 28 |  | 33 | 0.009 | DGA is assessed as acceptable. | Breakdown voltage is low. Other oil quality results are assessed as acceptable. Oil appears cloudy.
33000 | 1963 | 48 | 33.9 | 50 | 27.3 | 728 | 4.8 | 0.9 | 0.5 | 0.4 | 0 | 16 | 0.006 | 80 |  | 26 | 0.01 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1963 | 48 | 67 | 50 | 56.5 | 1212.8 | 7.2 | 1.6 | 0.8 | 0.9 | 0 | 19 | 0.006 | 79 |  | 28 | 0.011 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1963 | 48 | 13.4 | 50 | 9.8 | 346.5 | 2.8 | 0.3 | 0.2 | 0.3 | 0 | 11 | 0.005 | 59 |  | 26 | 0.011 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1963 | 48 | 65.4 | 32 | 51 | 1046.4 | 10.2 | 1.4 | 1.9 | 0.9 | 0 | 50 | 0.006 | 19 |  | 34 | 0.009 | DGA is assessed as acceptable. | Breakdown voltage is low. Oil is cloudy in appearance. Other oil quality results are assessed as acceptable at present.
33000 | 1963 | 48 | 211 | 40 | 181 | 1313 | 0 | 1 | 29 | 0 | 0 | 18 | 0.096 | 74 |  | 6 | 0.0495 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1963 | 48 | 366 | 40 | 315 | 1961 | 4 | 2 | 41 | 1 | 3 | 19 | 0.145 | 46 |  | 3.8 | 0.059 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1963 | 48 | 318 | 41.81 | 295 | 1435 | 0 | 1 | 22 | 0 | 0 | 16 | 0.144 | 65 |  | 3.9 | 0.061 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1963 | 48 | 257 | 41.81 | 234 | 1481 | 0 | 1 | 22 | 0 | 0 | 21 | 0.141 | 57 |  | 3.6 | 0.067 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1963 | 48 | 361 | 41.81 | 334 | 1673 | 0 | 1 | 26 | 0 | 0 | 20 | 0.116 | 64 |  | 3.6 | 0.066 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1963 | 48 | 622 | 41.81 | 564 | 3854 | 9 | 3 | 44 | 1 | 1 | 35 | 0.145 | 61 |  | 2.9 | 0.08 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1963 | 48 | 419 | 38 | 345 | 4655 | 8 | 2 | 62 | 1 | 1 | 13 | 0.189 | 75 |  | 3 | 0.083 | DGA is consistent with main tank sample. | Oil quality is assessed as acceptable.
33000 | 1963 | 48 | 297.8 | 32 | 218.5 | 3477.3 | 14.8 | 2 | 60.1 | 1.4 | 1 | 20 | 0.198 | 59 |  | 2 | 0.084 | DGA is assessed as acceptable. | Acidity level is high. Other oil quality results are assessed as acceptable.
33000 | 1963 | 48 | 368 | 40 | 310.9 | 3402.9 | 4.5 | 1.8 | 49.7 | 0.7 | 0.4 | 18 | 0.197 | 62 |  | 2 | 0.086 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1963 | 48 | 390.3 | 45 | 324.8 | 3879.4 | 11.5 | 2.4 | 49.9 | 1 | 0.7 | 25 | 0.213 | 68 |  | 2 | 0.105 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1963 | 48 | 374.2 | 46 | 325.1 | 3469 | 8.4 | 1.8 | 37.7 | 1.2 | 0 | 17 | 0.22 | 66 |  | 2 | 0.095 | DGA is assessed as acceptable. | Acidity level is high but relatively stable. Other oil quality results are assessed as acceptable.
33000 | 1963 | 48 | 380.4 | 55 | 341.1 | 3297.9 | 4.5 | 2 | 32.4 | 0.4 | 0 | 18 | 0.225 | 59 |  | 2 | 0.105 | DGA is assessed as acceptable. | Acidity level is high. Other oil quality results are assessed as acceptable. Corrosive IEC. Non-corrosive ASTM 3B.
33000 | 1963 | 48 | 224 | 41.81 | 196.2 | 2806.4 | 3.2 | 1.6 | 22.3 | 0.7 | 0 | 14 | 0.251 | 68 |  | 2 | 0.097 | DGA is assessed as acceptable. | Acidity level is high but stable. Other oil quality results are assessed as acceptable.
33000 | 1963 | 48 | 167.9 | 47 | 146.7 | 1758.1 | 5 | 1.4 | 13.4 | 1.1 | 0.3 | 17 | 0.218 | 85 |  | 2 | 0.095 | DGA is assessed as acceptable. | Acidity level is high. Other oil quality results are assessed as acceptable.
33000 | 1963 | 48 | 235.2 | 42 | 198.2 | 1902.7 | 9.9 | 2.2 | 16.3 | 0 | 8.6 | 18 | 0.244 | 62 |  | 2 | 0.097 | DGA is assessed as acceptable. | Acidity level is high. Other oil quality results are assessed as acceptable.
33000 | 1963 | 48 | 9 | 25 | 8 | 187 | 0 | 0 | 1 | 0 | 0 | 8 | 0.026 | 47 |  | 50 | 0.028 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1963 | 48 | 324 | 40 | 225 | 1392 | 39 | 2 | 26 | 1 | 31 | 10 | 0.036 | 54 |  | 14.4 | 0.027 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1963 | 48 | 304 | 48 | 185 | 1503 | 35 | 3 | 27 | 1 | 53 | 11 | 0.034 | 58 |  | 13.1 | 0.028 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1963 | 48 | 268 | 50 | 181 | 1454 | 11 | 3 | 25 | 1 | 47 | 9 | 0.033 | 56 |  | 9.4 | 0.036 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1963 | 48 | 428 | 40 | 330 | 2736 | 17 | 7 | 33 | 3 | 38 | 9 | 0.036 | 75 |  | 5.3 | 0.072 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1963 | 48 | 296 | 40 | 216.6 | 1591.5 | 17.6 | 2.9 | 40.1 | 6.4 | 12.4 | 15 | 0.044 | 75 |  | 3 | 0.14 | The test results are assessed as acceptable. Acetylene gas possibly communicating from tapchanger. | Oil quality is assessed as acceptable.
33000 | 1963 | 48 | 322.1 | 40 | 264.7 | 1662.2 | 20.3 | 2.5 | 26.1 | 2.7 | 5.8 | 14 | 0.05 | 75 |  | 2 | 0.14 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1963 | 48 | 446.6 | 36 | 311.6 | 2152.3 | 92.6 | 3.4 | 29 | 0.9 | 9.1 | 8 | 0.047 | 75 |  | 3 | 0.112 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1963 | 48 | 321.6 | 39 | 250.8 | 1908.8 | 16.2 | 2.2 | 33.5 | 4 | 14.9 | 12 | 0.049 | 75 |  | 4 | 0.102 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable. Corrosive IEC. Non-corrosive 3B.
33000 | 1963 | 48 | 413.1 | 41.81 | 282.2 | 2154.3 | 94.2 | 2.5 | 27.2 | 2.3 | 4.7 | 10 | 0.047 | 76 |  | 3 | 0.112 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1963 | 48 | 294.1 | 48 | 220.7 | 1714.6 | 40.1 | 2.4 | 22.1 | 2.2 | 6.6 | 13 | 0.052 | 86 |  | 3 | 0.102 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1963 | 48 | 345.4 | 41 | 278.5 | 1933.2 | 26 | 9.2 | 25 | 1.4 | 5.3 | 14 | 0.049 | 76 |  | 3 | 0.096 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1963 | 48 | 27.2 | 40 | 18 | 380.6 | 0 | 0.6 | 4 | 0.2 | 4.4 | 12 | 0.037 | 64 |  | 3 | 0.102 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1963 | 48 | 186 | 26 | 114 | 702 | 34 | 2 | 19 | 0 | 17 | 6 | 0.016 | 51 |  | 40 | 0.033 | DGA is assessed as acceptable. Oil quality is assessed as acceptable.
33000 | 1963 | 48 | 446 | 34 | 230 | 940 | 89 | 5 | 28 | 1 | 93 | 17 | 0.033 | 50 |  | 37.2 | 0.013 | Increased level of C2H2. Possibly from tapchanger ? Otherwise test results are satisfactory.
33000 | 1963 | 48 | 490 | 34 | 149 | 1253 | 51 | 14 | 3 | 52 | 221 | 18 | 0.039 | 43 |  | 12 | 0.048 | DGA is assessed as acceptable. Acetylene gas possibly from tapchanger. Oil quality is assessed as acceptable.
33000 | 1963 | 48 | 715 | 40 | 209 | 1287 | 114 | 17 | 61 | 3 | 311 | 14 | 0.026 | 47 |  | 29.2 | 0.016 | DGA is assessed as acceptable. Acetylene possibly from tapchanger. Oil quality is assessed as acceptable.
33000 | 1963 | 48 | 495 | 42 | 211 | 1676 | 11 | 4 | 54 | 1 | 214 | 9 | 0.021 | 58 |  | 39.4 | 0.011 | DGA is assessed as acceptable. Oil quality is assessed as acceptable.
33000 | 1963 | 48 | 512.2 | 28 | 274.9 | 1782.8 | 62 | 7.5 | 54.8 | 5 | 108 | 22 | 0.024 | 36 |  | 20 | 0.018 | The test results are assessed as acceptable. Acetylene gas possibly communicating from tapchanger.
33000 | 1963 | 48 | 410.2 | 43 | 282.8 | 1871.4 | 35.6 | 5.1 | 33.3 | 2 | 51.4 | 14 | 0.018 | 48 |  | 22 | 0.015 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1963 | 48 | 421.3 | 47 | 295.2 | 2166 | 35 | 5.3 | 37 | 0 | 48.8 | 17 | 0.028 | 51 |  | 19 | 0.018 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1963 | 48 | 380.1 | 48 | 243.6 | 2159 | 30.4 | 4.8 | 37.4 | 1.6 | 62.3 | 16 | 0.035 | 55 |  | 16 | 0.018 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1963 | 48 | 176 | 41.81 | 110 | 760 | 36 | 3 | 12 | 1 | 14 | 7 | 0.017 | 70 |  | 10 | 0.0291 | Test results satisfactory.
33000 | 1963 | 48 | 55 | 41.81 | 46 | 1098 | 0 | 1 | 5 | 3 | 0 | 21 | 0.122 | 65 |  | 5.1 | 0.061 | Test results satisfactory.
33000 | 1963 | 48 | 360 | 41.81 | 178 | 1032 | 39 | 6 | 29 | 2 | 106 | 22 | 0.033 | 46 |  | 14.3 | 0.035 | Acetylene level quite high; tapchanger ? RECOMMEND RESAMPLE IN 6 MONTHS.
33000 | 1963 | 48 | 41 | 41.81 | 3 | 584 | 0 | 1 | 10 | 2 | 25 | 20 | 0.028 | 54 |  | 12.2 | 0.031 | Test results satisfactory.
33000 | 1963 | 48 | 293 | 34 | 272 | 1327 | 0 | 2 | 19 | 0 | 0 | 11 | 0.096 | 53 |  | 6 | 0.046 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1963 | 48 | 494 | 47 | 423 | 2051 | 29 | 2 | 0 | 39 | 1 | 15 | 0.125 | 59 |  | 6.1 | 0.048 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1963 | 48 | 443 | 40 | 353 | 1972 | 52 | 3 | 32 | 2 | 1 | 24 | 0.119 | 57 |  | 7.3 | 0.047 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1963 | 48 | 523 | 41.81 | 437 | 2496 | 53 | 3 | 29 | 1 | 0 | 14 | 0.122 | 58 |  | 5.6 | 0.037 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1963 | 48 | 703 | 40 | 617 | 3530 | 35 | 5 | 45 | 1 | 0 | 16 | 0.148 | 55 |  | 6.1 | 0.037 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1963 | 48 | 1025 | 76 | 928 | 5580 | 36 | 8 | 51 | 2 | 0 | 18 | 0.169 | 42 |  | 5 | 0.049 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1963 | 48 | 710.6 | 34 | 633.2 | 6068.4 | 23 | 4.7 | 47.5 | 1.9 | 0.3 | 20 | 0.175 | 57 |  | 5 | 0.045 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1963 | 48 | 861.6 | 33 | 784.5 | 6442 | 29.7 | 4.7 | 40.4 | 2.1 | 0.2 | 27 | 0.177 | 64 |  | 5 | 0.043 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1963 | 48 | 212 | 43 | 175 | 2040 | 30 | 2 | 4 | 1 | 0 | 19 | 0.195 | 44 |  | 6 | 0.049 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1963 | 48 | 259 | 42 | 249 | 2648 | 0 | 2 | 7 | 1 | 0 | 17 | 0.169 | 61 |  | 6 | 0.037 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1963 | 48 | 254 | 40 | 236 | 2701 | 0 | 2 | 12 | 4 | 0 | 15 | 0.178 | 53 |  | 4.4 | 0.051 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1963 | 48 | 334 | 56 | 298 | 2620 | 8 | 3 | 21 | 3 | 1 | 24 | 0.168 | 67 |  | 3.8 | 0.06 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1963 | 48 | 1293 | 41.81 | 306 | 2912 | 212 | 274 | 437 | 52 | 12 | 17 | 0.18 | 44 |  | 3.7 | 0.054 | DGA suggests oil overheating. Possible connection/contact overheat. | Oil quality is assessed as acceptable.
33000 | 1963 | 48 | 408 | 42 | 271 | 3280 | 29 | 15 | 76 | 13 | 4 | 20 | 0.177 | 48 |  | 3.9 | 0.061 | Dissolved gas analysis suggests hot spot in oil. (Overheated Transition resistors) | Oil quality is assessed as acceptable.
33000 | 1963 | 48 | 450 | 46 | 238 | 3344 | 34 | 65 | 82 | 26 | 5 | 26 | 0.163 | 57 |  | 4 | 0.061 | Gas levels have remained fairly stable. | Oil quality is assessed as acceptable.
33000 | 1963 | 48 | 320 | 46 | 216 | 2557 | 12 | 26 | 48 | 16 | 2 | 13 | 0.166 | 68 |  | 3.8 | 0.055 | Dissolved gas analysis is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1963 | 48 | 380.7 | 47 | 319 | 4124.6 | 19.7 | 7.8 | 25.6 | 8.3 | 0.3 | 21 | 0.175 | 64 |  | 4 | 0.06 | Dissolved gas analysis is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1963 | 48 | 495 | 51 | 432.5 | 4965.6 | 30.8 | 6.8 | 19 | 5.8 | 0.1 | 40 | 0.164 | 27 |  | 3 | 0.067 | Dissolved gas analysis is assessed as acceptable. | Moisture content is high. Breakdown voltage is low. Possible sample contamination.
33000 | 1963 | 48 | 534.8 | 59 | 470.2 | 5216 | 31.3 | 7.5 | 19.1 | 6.5 | 0.2 | 35 | 0.178 | 23 |  | 3.8 | 0.064 | DGA is assessed as acceptable. | Moisture content is high. Breakdown voltage is low. Possible sample contamination. Other oil quality results are assessed as acceptable.
33000 | 1963 | 48 | 610.5 | 60 | 549 | 6699.3 | 34.6 | 6.3 | 14.4 | 4.5 | 1.7 | 31 | 0.177 | 32 |  | 4 | 0.067 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1963 | 48 | 532.9 | 44 | 475.8 | 4894.1 | 42.9 | 4.8 | 6.6 | 2.8 | 0 | 27 | 0.178 | 47 |  | 4 | 0.058 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1963 | 48 | 457.4 | 48 | 406.3 | 4832.4 | 38.9 | 5 | 4.7 | 2.5 | 0 | 33 | 0.158 | 28 |  | 4 | 0.059 | DGA is assessed as acceptable. | Breakdown voltage is low. Other oil quality results are assessed as acceptable.
33000 | 1963 | 48 | 292.6 | 52 | 258.4 | 3787.1 | 26.4 | 3.4 | 2.7 | 1.7 | 0 | 23 | 0.144 | 56 |  | 5 | 0.05 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable. Corrosive IEC. Corrosive ASTM 4A.
33000 | 1963 | 48 | 250.5 | 47 | 224.2 | 3326.1 | 21.4 | 2.8 | 2.1 | 0 | 0 | 23 | 0.141 | 50 |  | 5 | 0.048 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1963 | 48 | 194 | 41.81 | 187 | 1893 | 0 | 2 | 2 | 1 | 2 | 13 | 0.071 | 60 |  | 50 | 0.0083 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1963 | 48 | 247 | 46 | 239 | 2090 | 0 | 2 | 2 | 1 | 3 | 12 | 0.055 | 71 |  | 7 | 0.043 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1963 | 48 | 457 | 56 | 257 | 2411 | 40 | 38 | 105 | 15 | 2 | 16 | 0.048 | 65 |  | 8.8 | 0.035 | Ethylene gas level quite high. Possibly hot spot. Recommend resample in 6 mths.
33000 | 1963 | 48 | 704 | 42 | 286 | 3026 | 49 | 129 | 206 | 31 | 3 | 13 | 0.058 | 60 |  | 7.6 | 0.0297 | Ethylene gas level increasing. Possible hot spot. RECOMMEND RESAMPLE IN 1 YEAR TO MONITOR TRENDS. Acetylene gas possibly from tapchanger.
33000 | 1963 | 48 | 860 | 46 | 302 | 2778 | 26 | 108 | 361 | 60 | 3 | 16 | 0.063 | 43 |  | 6.6 | 0.036 | Hydrocarbon gas levels increasing; possible hot spot. Oil quality is assessed as acceptable. RECOMMEND RESAMPLE IN 1 YEAR TO MONITOR TREND.
33000 | 1963 | 48 | 575 | 48 | 276 | 2681 | 22 | 49 | 189 | 35 | 4 | 14 | 0.061 | 75 |  | 6.6 | 0.037 | Ethane gas level has decreased. Oil quality is assessed as acceptable.
33000 | 1963 | 48 | 635 | 52 | 421.5 | 4059.2 | 25.4 | 17.5 | 128 | 40.1 | 2.5 | 33 | 0.071 | 57 |  | 5 | 0.045 | Dissolved gas levels are reduced. Dissolved gas analysis is assessed as acceptable. | Moisture content is slightly high. Other oil quality results are assessed as acceptable.
33000 | 1963 | 48 | 749.3 | 62 | 600.1 | 5623.6 | 47.4 | 15.7 | 58.7 | 24.8 | 2.6 | 20 | 0.074 | 55 |  | 6 | 0.052 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1963 | 48 | 549.8 | 46 | 466.6 | 4352.7 | 41.9 | 10.9 | 21.3 | 9.1 | 0 | 14 | 0.083 | 62 |  | 6 | 0.042 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1963 | 48 | 363.5 | 37 | 293.2 | 3439.6 | 34.4 | 12.2 | 14.7 | 7.5 | 1.5 | 19 | 0.08 | 60 |  | 5 | 0.045 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1963 | 48 | 567.6 | 50 | 443 | 4528.8 | 43.4 | 27.3 | 20.4 | 31.1 | 2.4 | 24 | 0.083 | 46 |  | 5 | 0.048 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1963 | 48 | 388.1 | 55 | 329.7 | 3893.1 | 31.8 | 5.3 | 8.7 | 8.3 | 4.3 | 21 | 0.093 | 43 |  | 5 | 0.048 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable. Corrosive IEC. Corrosive ASTM 4A.
33000 | 1963 | 48 | 359.1 | 50 | 314 | 3698.6 | 26.8 | 4.9 | 6 | 5.6 | 1.8 | 22 | 0.113 | 75 |  | 5 | 0.051 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1963 | 48 | 0 | 41.81 | [7 empty] | 21 | 0.139 | 48 |  | 4.5 | 0.038 | Tested at workshop. Oil satisfactory.
33000 | 1963 | 48 | 358 | 41.81 | 305 | 2706 | 0 | 5 | 43 | 3 | 2 | 26 | 0.037 | 44 |  | 30 | 0.019 | Test results satisfactory. Acidity result suggests an oil change has been carried out since last test.
33000 | 1963 | 48 | 369 | 51 | 308 | 2427 | 14 | 3 | 37 | 1 | 6 | 21 | 0.071 | 43 |  | 20.7 | 0.017 | Test results satisfactory.
33000 | 1963 | 48 | 346 | 53 | 295 | 2769 | 6 | 4 | 34 | 1 | 6 | 30 | 0.054 | 51 |  | 16.9 | 0.015 | Test results satisfactory.
33000 | 1963 | 48 | 348 | 42 | 281 | 3239 | 21 | 3 | 35 | 1 | 7 | 25 | 0.058 | 65 |  | 11.4 | 0.026 | Test results are assessed as acceptable.
33000 | 1963 | 48 | 803 | 40 | 367 | 3388 | 217 | 58 | 93 | 4 | 64 | 30 | 0.062 | 45 |  | 9.9 | 0.025 | Dissolved gas analysis suggests possible hot spot in oil. RECOMMEND INVESTIGATE.
33000 | 1963 | 48 | 750 | 40 | 682 | 4966 | 54 | 5 | 7 | 1 | 1 | 33 | 0.233 | 64 |  | 5 | 0.045 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1963 | 48 | 369 | 37 | 358 | 3094 | 0 | 3 | 6 | 1 | 1 | 28 | 0.228 | 69 |  | 1.5 | 0.162 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1963 | 48 | 266 | 47 | 245 | 3960 | 0 | 2 | 15 | 1 | 3 | 31 | 0.27 | 58 |  | 4.9 | 0.056 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1963 | 48 | 780 | 72 | 673 | 7237 | 46 | 24 | 25 | 9 | 3 | 61 | 0.321 | 28 |  | 0.23 | 1.1 | Significant increase in carbon dioxide and 2-furfural levels. Oil quality very poor. RECOMMEND OIL CHANGE OR OIL RECLAMANATION.
33000 | 1963 | 48 | 1096 | 41.81 | 495 | 8051 | 68 | 317 | 48 | 164 | 4 | 54 | 0.28 | 29 |  | 0.115 | 2.3 | Moisture content of oil is very high. 2-furfural level is very high. Carbon dioxide gas level is high. Oil quality poor. RECOMMEND OIL CHANGE/RECLAMATION. RECOMMEND RESAMPLE IN 6 MONTHS TO MONITOR METHANE AND ETHANE.
33000 | 1963 | 48 | 1185 | 65 | 480 | 7762 | 50 | 247 | 104 | 302 | 2 | 49 | 0.326 | 51 |  | 0.107 | 2.15 | 2-fufural level is extremely high suggesting advanced insulation degradation. Moisture content very high. Dissolve gas analysis suggests oil overheating has occurred. RECOMMEND OIL CHANGE. RECOMMEND INVESTIGATE.
33000 | 1963 | 48 | 2807 | 53 | 1149 | 10707 | 177 | 703 | 199 | 578 | 1 | 45 | 0.376 | 26 |  | 0.11 | 2.348 | 2-furfural level is extremely high. Dissolved gas analysis suggests mild oil overheating has occurred. Oil quality is poor. Test results suggests advanced stage of insulation degradation. RECOMMEND RESAMPLE IN 1 YEAR TO MONITOR CONDITION.
33000 | 1963 | 48 | 179 | 27 | 172 | 1860 | 0 | 1 | 3 | 0 | 3 | 26 | 0.213 | 69 |  | 7 | 0.0318 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1963 | 48 | 185 | 40 | 174 | 1725 | 0 | 2 | 4 | 0 | 5 | 25 | 0.204 | 47 |  | 5.5 | 0.041 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1963 | 48 | 119 | 46 | 103 | 1723 | 0 | 2 | 6 | 1 | 7 | 18 | 0.202 | 53 |  | 5.5 | 0.045 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1963 | 48 | 260 | 46 | 220 | 2353 | 22 | 2 | 8 | 0 | 8 | 29 | 0.196 | 48 |  | 4.6 | 0.044 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1963 | 48 | 248.7 | 46 | 219.3 | 2784 | 7 | 2.5 | 10.6 | 0.7 | 8.6 | 28 | 0.198 | 31 |  | 4 | 0.058 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1963 | 48 | 180.7 | 42 | 162.8 | 2770.8 | 4.4 | 1.9 | 6.9 | 0.8 | 3.9 | 26 | 0.184 | 46 |  | 4 | 0.051 | 2-furfural level is high suggesting advanced state of insulation degradation. Other test results are assessed as acceptable. RECOMMEND RESAMPLE IN 1 YEAR TO MONITOR CONDITION.
33000 | 1963 | 48 | 124.5 | 28 | 108.6 | 2015.7 | 1.5 | 4.6 | 3.5 | 0 | 6.3 | 20 | 0.189 | 71 |  | 5 | 0.043 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1962 | 49 | 245 | 40 | 204 | 1661 | 0 | 1 | 37 | 1 | 2 | 12 | 0.1 | 63 |  | 3.5 | 0.071 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1962 | 49 | 290 | 50 | 245 | 2157 | 0 | 3 | 41 | 1 | 0 | 14 | 0.132 | 52 |  | 4.4 | 0.058 | Dissolved gas analysis is assessed as acceptable. Oil quality is assessed as acceptable.
33000 | 1962 | 49 | 472 | 41.81 | 240 | 3172 | 38 | 5 | 52 | 1 | 136 | 26 | 0.138 | 32 |  | 4.9 | 0.049 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1962 | 49 | 313 | 46 | 183 | 2252 | 28 | 3 | 31 | 1 | 67 | 25 | 0.124 | 67 |  | 4.3 | 0.059 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1962 | 49 | 373.8 | 42 | 209 | 2349.9 | 28.5 | 4.8 | 44.6 | 1 | 85.9 | 18 | 0.146 | 65 |  | 4 | 0.059 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1962 | 49 | 315.2 | 38 | 242.3 | 2482.6 | 14.2 | 2.7 | 26 | 1.7 | 28.3 | 19 | 0.131 | 65 |  | 4 | 0.055 | Dissolved gas analysis is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1962 | 49 | 341.7 | 42 | 180.4 | 2250.3 | 102.9 | 3.6 | 21.4 | 0 | 33.4 | 15 | 0.182 | 75 |  | 4 | 0.061 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1962 | 49 | 182.2 | 52 | 145.9 | 1800.1 | 4.8 | 2 | 15.5 | 0.9 | 13.1 | 18 | 0.137 | 68 |  | 4 | 0.058 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable. Corrosive IEC. Corrosive ASTM 4A.
33000 | 1962 | 49 | 170 | 27 | 145 | 1034 | 0 | 1 | 24 | 0 | 0 | 13 | 0.044 | 64 |  | 20 | 0.033 | Test results satisfactory.
33000 | 1962 | 49 | 218 | 40 | 170 | 1840 | 0 | 1 | 45 | 1 | 1 | 14 | 0.042 | 67 |  | 8 | 0.043 | Test results satisfactory.
33000 | 1962 | 49 | 356 | 41.81 | 285 | 2250 | 14 | 7 | 48 | 2 | 0 | 17 | 0.05 | 57 |  | 8.1 | 0.036 | Test results satisfactory.
33000 | 1962 | 49 | 71 | 46 | 64 | 619 | 0 | 1 | 6 | 0 | 0 | 16 | 0.018 | 63 |  | 33.2 | 0.021 | Test results satisfactory. TX had an oil change ??
33000 | 1962 | 49 | 272 | 60 | 239 | 1899 | 3 | 2 | 27 | 1 | 0 | 21 | 0.034 | 62 |  | 15 | 0.021 | Test results are assessed as acceptable.
33000 | 1962 | 49 | 510 | 41.81 | 138 | 1699 | 141 | 40 | 78 | 6 | 107 | 32 | 0.104 | 33 |  | 4.5 | 0.071 | No indication in oil sample of abnormality. Oil test results satisfactory. (Cooling fin)
33000 | 1962 | 49 | 333 | 41.81 | 104 | 1557 | 73 | 27 | 49 | 4 | 76 | 22 | 0.155 | 50 |  | 8 | 0.026 | D.G.A. Tends to indicate arc or persistent sparking in light of recent history. Warrants further investigation.
33000 | 1962 | 49 | 170 | 30 | 145 | 1709 | 0 | 2 | 22 | 1 | 0 | 16 | 0.024 | 54 |  | 23 | 0.03 | Test results satisfactory.
33000 | 1962 | 49 | 152 | 50 | 122 | 1867 | 0 | 1 | 28 | 1 | 0 | 24 | 0.037 | 52 |  | 22.1 | 0.021 | Test results satisfactory.
33000 | 1962 | 49 | 185 | 38 | 152 | 2360 | 0 | 2 | 30 | 1 | 0 | 39 | 0.093 | 18 |  | 22.5 | 0.016 |  | Moisture content of oil high; dielectric strength low. Other test results are assessed as acceptable.
33000 | 1962 | 49 | 131 | 52 | 100 | 2007 | 0 | 1 | 29 | 1 | 0 | 24 | 0.028 | 56 |  | 25.8 | 0.013 | Test results are assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1962 | 49 | 209.5 | 50 | 156.7 | 1829.9 | 0 | 1.8 | 48 | 1.5 | 1.5 | 16 | 0.029 | 75 |  | 11 | 0.038 | The test results are assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1962 | 49 | 162 | 36 | 122.5 | 2020.1 | 1.8 | 1.5 | 34.4 | 0.7 | 1.1 | 12 | 0.033 | 75 |  | 14 | 0.024 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1962 | 49 | 174.9 | 40 | 150.1 | 1721.9 | 0 | 1.3 | 23.5 | 0 | 0 | 13 | 0.036 | 68 |  | 14 | 0.023 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1962 | 49 | 170.8 | 37 | 145.8 | 1614.4 | 0 | 1.5 | 23.3 | 0.2 | 0 | 13 | 0.042 | 75 |  | 13 | 0.025 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1962 | 49 | 193.2 | 34 | 157.2 | 2589.7 | 0 | 1.6 | 34.4 | 0 | 0 | 13 | 0.04 | 83 |  | 14 | 0.025 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1962 | 49 | 183.5 | 41.81 | 146.8 | 2204.7 | 0 | 1.2 | 34.2 | 0.8 | 0.5 | 12 | 0.044 | 75 |  | 13 | 0.026 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1962 | 49 | 151.2 | 40 | 118.2 | 1851.1 | 1.7 | 1.6 | 29 | 0.4 | 0.3 | 13 | 0.047 | 53 |  | 11 | 0.026 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1962 | 49 | 158.9 | 32 | 129.5 | 1881.4 | 0 | 1.1 | 27.9 | 0.4 | 0 | 14 | 0.038 | 45 |  | 14 | 0.023 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1962 | 49 | 246 | 41.81 | 218 | 1930 | 0 | 2 | 25 | 1 | 0 | 18 | 0.2 | 45 |  | 3.3 | 0.077 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1962 | 49 | 340 | 41.81 | 307 | 2556 | 0 | 2 | 29 | 2 | 0 | 27 | 0.221 | 75 |  | 2.1 | 0.099 | DGA is assessed as acceptable | Acidity level of oil is slightly high. Other test results are assessed as acceptable.
33000 | 1962 | 49 | 304.6 | 41.81 | 243.8 | 3001.2 | 4.5 | 6.4 | 46.3 | 3.3 | 0.3 | 22 | 0.265 | 58 |  | 2 | 0.083 | DGA is assessed as acceptable. | Acidity level of sample is high. Other test results are assessed as acceptable.
33000 | 1962 | 49 | 329.6 | 41.81 | 292.5 | 3879.2 | 6.1 | 2.8 | 26.9 | 0.9 | 0.4 | 54 | 0.253 | 14 |  | 3 | 0.095 | DGA is assessed as acceptable. | Oil quality is poor. Moisture content is high. Breakdown voltage is low.
33000 | 1962 | 49 | 239.4 | 41.81 | 210.8 | 1923.1 | 3.8 | 3.3 | 20.3 | 1.2 | 0 | 29 | 0.297 | 37 |  | 3 | 0.084 | DGA is assessed as acceptable. | Oil quality is poor.
33000 | 1962 | 49 | 199.4 | 25 | 177.5 | 1988.2 | 1.6 | 3 | 16.6 | 0.7 | 0 | 20 | 0.307 | 69 |  | 2 | 0.083 | DGA is assessed as acceptable. | Acidity level is high. Other oil quality results are assessed as acceptable.
33000 | 1962 | 49 | 91.5 | 41.81 | 78.6 | 1535.3 | 0 | 0.3 | 12.6 | 0 | 0 | 34 | 0.285 | 48 |  | 2 | 0.084 | DGA is assessed as acceptable. | Acidity level is high but stable. Other oil quality results are assessed as acceptable.
33000 | 1962 | 49 | 244.7 | 22 | 205.2 | 2790.5 | 15.4 | 4.2 | 19 | 0.9 | 0 | 28 | 0.292 | 35 |  | 3 | 0.077 | DGA is assessed as acceptable. | Breakdown voltage is low. Acidity level is high.
33000 | 1962 | 49 | 460 | 34 | 431 | 6208 | 15 | 4 | 7 | 3 | 0 | 33 | 0.257 | 51 |  | 4 | 0.064 | Test results satisfactory. | Oil quality is poor.
33000 | 1962 | 49 | 236 | 45 | 228 | 3920 | 0 | 2 | 4 | 2 | 0 | 29 | 0.276 | 45 |  | 2.8 | 0.083 | Test results satisfactory. | Acidity level is high.
33000 | 1962 | 49 | 248 | 41.81 | 241 | 3675 | 0 | 2 | 4 | 1 | 0 | 18 | 0.266 | 53 |  | 3.1 | 0.076 | Test results satisfactory. | Acidity level is high.
33000 | 1962 | 49 | 226 | 30 | 219 | 3291 | 0 | 2 | 4 | 1 | 0 | 42 | 0.265 | 42 |  | 2.9 | 0.079 | Test results satisfactory. | High moisture content possibly sample contamination.
33000 | 1962 | 49 | 202 | 41.81 | 189 | 2967 | 7 | 2 | 3 | 1 | 0 | 49 | 0.262 | 40 |  | 3.2 | 0.076 | DGA is assessed as acceptable. | Moisture content of oil is high; acidity level high. Other test results are assessed as acceptable.
33000 | 1962 | 49 | 384.8 | 48 | 360.7 | 3772.6 | 12.6 | 3.7 | 5.7 | 2.1 | 0 | 64 | 0.297 | 23 |  | 3 | 0.087 | Dissolved gas analysis is assessed as acceptable. | Oil quality is poor.
33000 | 1962 | 49 | 321.1 | 22 | 297.9 | 4280.2 | 11.3 | 4 | 5.8 | 2.1 | 0 | 56 | 0.307 | 16 |  | 2 | 0.113 | DGA is assessed as acceptable. | Oil quality is poor.
33000 | 1962 | 49 | 283 | 40 | 267.6 | 4720 | 7 | 3 | 4.1 | 1.3 | 0 | 35 | 0.266 | 73 |  | 3 | 0.083 | DGA is assessed as acceptable. | Oil quality is poor.
33000 | 1962 | 49 | 292.1 | 43 | 276.6 | 4068.3 | 5.6 | 3.7 | 4.7 | 1.5 | 0 | 33 | 0.26 | 47 |  | 2 | 0.089 | DGA is assessed as acceptable. | Moisture content is high. Acidity level is high. Other oil quality results are assessed as acceptable.
33000 | 1962 | 49 | 218.7 | 41.81 | 203.9 | 4069.7 | 5.7 | 3 | 3.5 | 0.6 | 2 | 27 | 0.3 | 52 |  | 3 | 0.0756 | DGA is assessed as acceptable. | Acidity level is high. Other oil quality results are assessed as acceptable.
33000 | 1962 | 49 | 199.6 | 42 | 189.2 | 2970.4 | 4.7 | 2.4 | 2.2 | 1.1 | 0 | 27 | 0.271 | 40 |  | 3 | 0.085 | DGA is assessed as acceptable. | Acidity level is high. Other oil quality results are assessed as acceptable. Corrosive IEC. Corrosive ASTM 4A.
33000 | 1962 | 49 | 198.4 | 55 | 186.7 | 3207.5 | 5.7 | 2.6 | 2.5 | 0.9 | 0 | 27 | 0.316 | 60 |  | 2.4 | 0.084 | DGA is assessed as acceptable. | Acidity level is high. Other oil quality results are assessed as acceptable.
33000 | 1962 | 49 | 190 | 44 | 177.3 | 3163.5 | 5.4 | 2.6 | 3.7 | 1 | 0 | 34 | 0.297 | 30 |  | 3 | 0.07 | DGA is assessed as acceptable. | Acidity level is high. Breakdown voltage is slightly low. Other oil quality results are assessed as acceptable.
33000 | 1962 | 49 | 282 | 41.81 | 253 | 2023 | 0 | 1 | 27 | 0 | 1 | 20 | 0.026 | 59 |  | 4 | 0.0655 | Test satisfactory. | Oil quality is assessed as acceptable.
33000 | 1962 | 49 | 321 | 41.81 | 222 | 1840 | 38 | 3 | 22 | 1 | 35 | 18 | 0.1075 | 53 |  | 4.4 | 0.065 | Test results satisfactory. | Oil quality is assessed as acceptable.
33000 | 1962 | 49 | 561 | 41.81 | 411 | 2818 | 36 | 6 | 28 | 1 | 79 | 29 | 0.124 | 34 |  | 4.2 | 0.058 | DGA is assessed as acceptable. | Other test results are assessed as acceptable.
33000 | 1962 | 49 | 324.8 | 48 | 189.8 | 1594.4 | 22.2 | 4.7 | 24.9 | 0.5 | 82.7 | 15 | 0.139 | 47 |  | 4 | 0.06 | DGA is assessed as acceptable. | Other test results are assessed as acceptable.
33000 | 1962 | 49 | 211.6 | 43 | 156.8 | 1482.1 | 8.9 | 2.3 | 13.8 | 1.3 | 28.5 | 19 | 0.115 | 42 |  | 4 | 0.061 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1962 | 49 | 280.9 | 36 | 181 | 1796.4 | 28.6 | 3.4 | 19.4 | 0.7 | 47.8 | 25 | 0.123 | 75 |  | 3 | 0.075 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1962 | 49 | 258.1 | 38 | 134.7 | 1567 | 20.4 | 4.2 | 21.1 | 0.5 | 77.2 | 18 | 0.112 | 42 |  | 3 | 0.066 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1962 | 49 | 46 | 27 | 34 | 731 | 0 | 0 | 12 | 0 | 0 | 22 | 0.04 | 46 |  | 40 | 0.022 | Dissolved gas analysis is assessed as acceptable. Oil quality is assessed as acceptable.
33000 | 1962 | 49 | 54 | 36 | 28 | 1352 | 0 | 1 | 23 | 2 | 0 | 20 | 0.036 | 61 |  | 20 | 0.017 | Dissolved gas analysis is assessed as acceptable. Oil quality is assessed as acceptable.
33000 | 1962 | 49 | 275 | 48 | 230 | 4889 | 0 | 3 | 39 | 3 | 0 | 33 | 0.059 | 47 |  | 21 | 0.02 | Dissolved gas analysis is assessed as acceptable. Oil quality is assessed as acceptable.
33000 | 1962 | 49 | 282 | 58 | 238 | 3271 | 0 | 2 | 38 | 4 | 0 | 30 | 0.059 | 19 |  | 14.1 | 0.021 | Dielectric strength of oil is low. Possibly sample contamination. Other test results are assessed as acceptable. RECOMMEND RESAMPLE IN 3 MONTHS TO CHECK DIELECTRIC STRENGTH.
33000 | 1962 | 49 | 412.3 | 64 | 280.7 | 3417.9 | 9.8 | 11.1 | 93.1 | 13.2 | 4.4 | 34 | 0.084 | 34 |  | 9.8417 | 0.033055 | 2-furfural level is high but stable. Other test results are assessed as acceptable. RECOMMEND RESAMPLE IN 1 YEAR TO MONITOR CONDITION.
33000 | 1962 | 49 | 262.4 | 54 | 209.1 | 2653.7 | 4.2 | 2.3 | 42.4 | 4.2 | 0.2 | 37 | 0.073 | 34 |  | 10 | 0.027 | Dissolved gas analysis is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1962 | 49 | 1079 | 44 | 232 | 2353 | 246 | 64 | 156 | 8 | 373 | 28 | 0.086 | 42 |  | 11 | 0.024 | Dissolved hydrocarbon gas levels have increased. DGA indicates an arcing signature. | Oil quality is assessed as acceptable.
33000 | 1962 | 49 | 990 | 44 | 235 | 2461 | 167 | 54 | 160 | 10 | 364 | 31 | 0.087 | 23 |  | 10 | 0.026 | Dissolved hydrocarbon gas levels have increased. DGA indicates an arcing signature. However gases may be communicating through board of Type L tapchanger. | Moisture content is slightly high. Other oil quality results are assessed as acceptable.
33000 | 1962 | 49 | 356 | 45 | 123 | 1191 | 22 | 69 | 122 | 20 | 0 | 18 | 0.038 | 66 |  | 15 | 0.0231 | DGA suggests possible overheated joint. | Oil quality is assessed as acceptable.
33000 | 1962 | 49 | 218 | 40 | 192 | 1262 | 0 | 2 | 22 | 1 | 1 | 19 | 0.045 | 66 |  | 12.9 | 0.027 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1962 | 49 | 186 | 38 | 160 | 1411 | 2 | 1 | 23 | 0 | 0 | 16 | 0.053 | 73 |  | 9.6 | 0.025 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1962 | 49 | 245.3 | 33 | 206.7 | 1957.7 | 2 | 1.7 | 34.2 | 0.7 | 0 | 14 | 0.05 | 68 |  | 7 | 0.036 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1962 | 49 | 290.9 | 30 | 252.8 | 2169.4 | 0 | 1.7 | 35.5 | 0.9 | 0 | 18 | 0.066 | 39 |  | 6.9 | 0.041 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1962 | 49 | 344.5 | 38 | 215.5 | 1940.2 | 14.2 | 14.4 | 86.1 | 14.3 | 0 | 12 | 0.136 | 65 |  | 6 | 0.038 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1962 | 49 | 451.2 | 40 | 303.1 | 2312.2 | 4 | 19.5 | 105.8 | 18.8 | 0 | 15 | 0.088 | 75 |  | 6 | 0.049 | DGA is assessed as acceptable at present. | Oil quality is assessed as acceptable. Corrosive IEC. Non-corrosive ASTM 3B.
33000 | 1962 | 49 | 271.7 | 37 | 220.6 | 2483.3 | 1.8 | 1.9 | 43.3 | 4.1 | 0 | 15 | 0.099 | 41 |  | 5 | 0.042 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1962 | 49 | 906.1 | 35 | 6.7 | 823.5 | 28.3 | 14 | 75.1 | 13.4 | 768.6 | 17 | 0.002 | 51 |  | 499 | 0.002 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable. Particle contamination load is high.
33000 | 1962 | 49 | 290.4 | 32 | 251.7 | 2342.1 | 5.5 | 2.5 | 29.9 | 0.8 | 0 | 16 | 0.093 | 63 |  | 5 | 0.048 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1962 | 49 | 2050 | 30 | 382 | 1692 | 244 | 226 | 471 | 47 | 680 | 16 | 0.126 | 59 |  | 4.5 | 0.056 | Gas levels high. Tap changer?
33000 | 1962 | 49 | 1029 | 98 | 441 | 2253 | 0 | 142 | 365 | 61 | 20 | 28 | 0.114 | 40 |  | 7 | 0.033 | Gas levels have remained stable. RECOMMEND RESAMPLE IN 12 MONTHS.
33000 | 1962 | 49 | 771 | 41 | 459 | 2526 | 38 | 45 | 187 | 41 | 1 | 28 | 0.124 | 53 |  | 5.4 | 0.044 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1962 | 49 | 601 | 46 | 327 | 2775 | 13 | 63 | 158 | 39 | 1 | 24 | 0.136 | 52 |  | 5.9 | 0.041 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1962 | 49 | 271 | 35 | 118 | 1120 | 11 | 32 | 97 | 12 | 1 | 15 | 0.047 | 60 |  | 20 | 0.016 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1962 | 49 | 269 | 40 | 160 | 1225 | 0 | 19 | 79 | 10 | 1 | 36 | 0.052 | 23 |  | 15 | 0.028 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1962 | 49 | 195 | 40 | 171 | 1411 | 0 | 1 | 21 | 2 | 0 | 22 | 0.064 | 58 |  | 11.2 | 0.024 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1962 | 49 | 295 | 41.81 | 141 | 1225 | 19 | 23 | 64 | 9 | 39 | 47 | 0.074 | 29 |  | 11.5 | 0.026 | Increased hydrocarbon gas levels. RECOMMEND RESAMPLE IN SIX MONTHS.
33000 | 1962 | 49 | 415 | 41.81 | 179 | 1747 | 20 | 12 | 84 | 9 | 111 | 26 | 0.076 | 52 |  | 12.4 | 0.023 | Acetylene gas level increasing. Possibly from tapchanger? SHOULD BE INVESTIGATED.
33000 | 1962 | 49 | 506 | 41.81 | 272 | 3095 | 48 | 8 | 57 | 4 | 117 | 53 | 0.062 | 23 |  | 12.7 | 0.023 | Moisture content of oil high;breakdown low; Other test results satisfactory. Possibly sample contamination
33000 | 1962 | 49 | 880 | 50 | 242 | 2381 | 122 | 73 | 171 | 17 | 255 | 26 | 0.061 | 55 |  | 12.6 | 0.025 | Increased ethylene gas level. RECOMMEND RESAMPLE IN 6 MONTHS
33000 | 1962 | 49 | 901 | 41.81 | 194 | 2570 | 104 | 89 | 302 | 30 | 182 | 35 | 0.06 | 68 |  | 13.3 | 0.022 | Ethylene level increasing. RECOMMEND RESAMPLE IN 12 MONTHS.
33000 | 1962 | 49 | 388 | 41.81 | 156 | 3252 | 52 | 8 | 53 | 11 | 108 | 40 | 0.039 | 31 |  | 19.7 | 0.014 | Moisture content of oil is high. 2-Furfural level is above 1PPM. Other test results are assessed as acceptable.
33000 | 1962 | 49 | 492.9 | 41.81 | 74.3 | 1734.4 | 32.8 | 87 | 191.9 | 30.9 | 76 | 37 | 0.026 | 19 |  | 14 | 0.019 | DGA suggests high temperature oil overheating has occurred. | Moisture content is high. Breakdown voltage is low. Possible sample contamination. Other oil quality results are assessed as acceptable.
33000 | 1962 | 49 | 273 | 41.81 | 240 | 2097 | 0 | 2 | 30 | 0 | 1 | 17 | 0.158 | 63 |  | 3 | 0.095 | Test results satisfactory.
33000 | 1962 | 49 | 320 | 41.81 | 291 | 1928 | 0 | 2 | 26 | 1 | 0 | 18 | 0.152 | 48 |  | 2.8 | 0.089 | Test results satisfactory.
33000 | 1962 | 49 | 519 | 41.81 | 474 | 4625 | 0 | 3 | 40 | 1 | 1 | 25 | 0.192 | 72 |  | 4.6 | 0.055 | Test results satisfactory.
33000 | 1962 | 49 | 316 | 41.81 | 276 | 2553 | 7 | 2 | 27 | 1 | 3 | 39 | 0.182 | 22 |  | 2.8 | 0.087 | Moisture content of oil is high. Dielectric strength is low; possibly sample contamination. Other test results are assessed as acceptable.
33000 | 1962 | 49 | 405.1 | 66 | 361.8 | 2894.7 | 10.3 | 2.5 | 29.1 | 0.9 | 0.5 | 38 | 0.226 | 28 |  | 3 | 0.072 |  | Breakdown voltage of sample is slightly low. Moisture content and acidity level of sample is high. Other test results are assessed as acceptable.
33000 | 1962 | 49 | 416.9 | 42 | 380.9 | 3598.3 | 10.7 | 2 | 22.4 | 0.7 | 0.2 | 32 | 0.233 | 54 |  | 3 | 0.108 | 2-furfural level is trending upwards. Other test results are assessed as relatively stable.
33000 | 1962 | 49 | 379.6 | 41.81 | 336 | 4560.4 | 10.4 | 2.4 | 27.6 | 1.1 | 2.1 | 24 | 0.266 | 44 |  | 3 | 0.064 | DGA is assessed as acceptable. | Acidity level is high. Other oil quality results are assessed as acceptable.
33000 | 1962 | 49 | 659.2 | 58 | 614.5 | 7052.4 | 16.5 | 3.8 | 23.3 | 1.1 | 0 | 46 | 0.304 | 20 |  | 3 | 0.077 | DGA is assessed as acceptable. | Oil quality is poor.
33000 | 1962 | 49 | 595.3 | 47 | 559 | 6131.6 | 16.1 | 3.2 | 15.4 | 1.6 | 0 | 30 | 0.278 | 42 |  | 4 | 0.067 | DGA is assessed as acceptable. | Acidity level is high. Other oil quality results are assessed as acceptable. Corrosive IEC. Corrosive ASTM 4A.
33000 | 1962 | 49 | 488 | 41.81 | 455.3 | 6117.7 | 19.9 | 4.2 | 8.6 | 0 | 0 | 27 | 0.325 | 44 |  | 3 | 0.062 | DGA is assessed as acceptable. | Acidity level is high. Other oil quality results are assessed as acceptable.
33000 | 1962 | 49 | 191.6 | 36 | 178.2 | 2839.2 | 7 | 1.5 | 4.1 | 0.8 | 0 | 26 | 0.27 | 58 |  | 4 | 0.052 | DGA is assessed as acceptable. | Acidity level is high. Other oil quality results are assessed as acceptable.
33000 | 1962 | 49 | 166 | 41.81 | 137 | 1182 | 0 | 1 | 28 | 0 | 0 | 17 | 0.024 | 62 |  | 400 | 0.029 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1962 | 49 | 157 | 20 | 136 | 1106 | 0 | 1 | 19 | 0 | 1 | 9 | 0.029 | 44 |  | 19.7 | 0.029 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1962 | 49 | 426 | 41.81 | 173 | 1392 | 32 | 10 | 43 | 2 | 166 | 26 | 0.056 | 46 |  | 16.7 | 0.025 | Acetylene level increased significantly. Tap changer oil mixing?
33000 | 1962 | 49 | 468 | 20 | 162 | 1568 | 63 | 14 | 63 | 2 | 164 | 15 | 0.05 | 50 |  | 19.2 | 0.025 | Test results satisfactory. Acetylene gas possibly from tapchanger.
33000 | 1962 | 49 | 320 | 41.81 | 230 | 1645 | 20 | 5 | 35 | 1 | 29 | 18 | 0.043 | 51 |  | 16.6 | 0.022 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1962 | 49 | 237 | 41.81 | 184 | 1522 | 4 | 2 | 34 | 1 | 12 | 11 | 0.043 | 67 |  | 11.6 | 0.033 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1962 | 49 | 365.3 | 41.81 | 154.1 | 3080.7 | 15.5 | 3.5 | 54.3 | 1.7 | 136.2 | 21 | 0.036 | 52 |  | 12 | 0.031 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1962 | 49 | 286.9 | 41.81 | 162.7 | 2394.5 | 12.4 | 3.3 | 40.2 | 0.4 | 67.9 | 10 | 0.05 | 75 |  | 11 | 0.03227 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1962 | 49 | 294.1 | 36 | 166.7 | 2061.2 | 16.2 | 4.6 | 33.4 | 2.5 | 70.7 | 17 | 0.045 | 69 |  | 11 | 0.03 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1962 | 49 | 303 | 47 | 146.7 | 2212.2 | 9.6 | 3.6 | 32.3 | 0.9 | 109.9 | 16 | 0.047 | 93 |  | 12 | 0.026 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable. Corrosive IEC. Corrosive ASTM 4A.
33000 | 1962 | 49 | 107 | 26 | 87 | 1110 | 0 | 1 | 19 | 0 | 0 | 19 | 0.022 | 64 |  | 30 | 0.017 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1962 | 49 | 121 | 40 | 100 | 1125 | 0 | 1 | 20 | 0 | 0 | 14 | 0.022 | 75 |  | 18.7 | 0.023 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1962 | 49 | 184.5 | 50 | 150.6 | 1198.8 | 0 | 1.6 | 31.6 | 0.4 | 0.3 | 8 | 0.029 | 64 |  | 13 | 0.03 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1962 | 49 | 131.7 | 41.81 | 97.2 | 1594.3 | 0 | 1.4 | 31.3 | 0 | 1.8 | 9 | 0.034 | 75 |  | 18 | 0.019 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1962 | 49 | 146.9 | 41.81 | 122.6 | 1373.1 | 0 | 1.3 | 23 | 0 | 0 | 10 | 0.041 | 75 |  | 16 | 0.0196 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1962 | 49 | 137.7 | 14 | 117 | 1207.9 | 0 | 1 | 19.4 | 0.3 | 0 | 12 | 0.035 | 66 |  | 17 | 0.02 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable. Corrosive IEC. Non-corrosive ASTM 3B.
33000 | 1962 | 49 | 137.3 | 41.81 | 110.2 | 1385.5 | 1.5 | 1.5 | 23.7 | 0.2 | 0.2 | 9 | 0.045 | 88 |  | 15 | 0.018 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1962 | 49 | 150.9 | 30 | 125.2 | 1464.7 | 0 | 0.9 | 24.5 | 0.3 | 0 | 11 | 0.037 | 42 |  | 16 | 0.018 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1962 | 49 | 344 | 45 | 219 | 1694 | 27 | 5 | 42 | 1 | 50 | 13 | 0.084 | 43 |  | 6 | 0.048 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1962 | 49 | 441 | 45 | 296 | 1271 | 37 | 4 | 27 | 1 | 76 | 15 | 0.062 | 58 |  | 9.3 | 0.027 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1962 | 49 | 644 | 35 | 234 | 1522 | 160 | 14 | 40 | 1 | 195 | 16 | 0.072 | 61 |  | 8.6 | 0.028 | Test results satisfactory. Acetylene gas possibly from tapchanger. | Oil quality is assessed as acceptable.
33000 | 1962 | 49 | 616 | 41.81 | 199 | 1753 | 123 | 14 | 38 | 1 | 241 | 13 | 0.072 | 66 |  | 9.3 | 0.028 | DGA is assessed as acceptable. Acetylene gas possibly from tapchanger. | Oil quality is assessed as acceptable.
33000 | 1962 | 49 | 740.1 | 56 | 300.5 | 2379.8 | 160.4 | 19.4 | 46.4 | 0.7 | 212.7 | 24 | 0.081 | 42 |  | 7 | 0.034 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1962 | 49 | 592.7 | 55 | 406.4 | 4366.6 | 43 | 8.8 | 36.2 | 5.4 | 92.9 | 28 | 0.074 | 28 |  | 8.0329 | 0.032582 | DGA is assessed as acceptable. | Breakdown voltage is slightly low. Possible sample contamination. Otherwise the test results are consistent with main tank sample.
33000 | 1962 | 49 | 660.6 | 55 | 460.3 | 4502.2 | 52.6 | 8.4 | 37.4 | 5.8 | 96.1 | 25 | 0.084 | 34 |  | 7.9632 | 0.034815 | DGA is assessed as acceptable. Acetylene gas possibly communicating from tapchanger. | Oil quality is assessed as acceptable.
33000 | 1962 | 49 | 550.8 | 54 | 410.6 | 3942.5 | 40.2 | 7.4 | 27.6 | 4.1 | 60.9 | 26 | 0.076 | 66 |  | 6 | 0.04 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1962 | 49 | 475.6 | 61 | 292.5 | 3186.4 | 51.2 | 10 | 24.5 | 1.5 | 95.9 | 28 | 0.077 | 32 |  | 6 | 0.031 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1962 | 49 | 371.3 | 48 | 145.8 | 2048.4 | 53.4 | 14.4 | 34.4 | 3.2 | 120.1 | 12 | 0.061 | 54 |  | 8 | 0.028 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1962 | 49 | 86 | 56 | 56.2 | 1091.4 | 0 | 1.7 | 9.9 | 1.9 | 16.3 | 13 | 0.058 | 88 |  | 8 | 0.03 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1962 | 49 | 70.8 | 42 | 56.2 | 928.4 | 0 | 1.7 | 7.8 | 0 | 5.1 | 14 | 0.05 | 76 |  | 11 | 0.023 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1961 | 50 | 42.5 | 18 | 35.1 | 870.6 | 1.5 | 0.8 | 4.8 | 0.3 | 0 | 18 | 0.057 | 51 |  | 8 | 0.028 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1961 | 50 | 275 | 36 | 233 | 1664 | 0 | 2 | 39 | 1 | 0 | 17 | 0.138 | 66 |  | 7 | 0.042 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1961 | 50 | 266 | 35 | 226 | 1759 | 0 | 2 | 35 | 3 | 0 | 16 | 0.123 | 64 |  | 4.5 | 0.0499 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1961 | 50 | 211 | 62 | 186 | 1233 | 0 | 2 | 22 | 1 | 0 | 25 | 0.143 | 53 |  | 5.4 | 0.046 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1961 | 50 | 246 | 42 | 208 | 1458 | 13 | 2 | 23 | 0 | 0 | 20 | 0.146 | 75 |  | 4.6 | 0.045 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1961 | 50 | 307.1 | 44 | 269 | 2286 | 6.1 | 2.1 | 29.1 | 0.8 | 0 | 17 | 0.196 | 75 |  | 4 | 0.054 | Dissolved gas analysis is assessed as acceptable. | Acidity level is trending upwards. Other oil quality results are assessed as acceptable.
33000 | 1961 | 50 | 354.7 | 43 | 308.9 | 2509.5 | 11.4 | 2.3 | 30.8 | 1 | 0.3 | 23 | 0.18 | 65 |  | 4 | 0.058 | Dissolved gas analysis is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1961 | 50 | 7891 | 32 | 1678 | 7832 | 502 | 2287 | 2231 | 1087 | 106 | 32 | 0.2 | 50 |  | 4 | 0.072 | Dissolved gas analysis suggests high energy discharge has occurred. (Thermal fault 300-700 degrees C). | Moisture content is slightly high. Acidity level is high. Other oil quality results are assessed as acceptable.
33000 | 1961 | 50 | 11475 | 44 | 2603 | 9502 | 886 | 3378 | 3060 | 1460 | 88 | 32 | 0.201 | 34 |  | 3 | 0.075 | DGA suggests oil overheating has occurred (300 - 700C). Increased carbon oxide levels suggests insulation involved. | Moisture content is slightly high. Acidity level is high. Other oil quality results are assessed as acceptable.
33000 | 1961 | 50 | 497 | 25 | 427 | 4383 | 62 | 3 | 4 | 1 | 0 | 30 | 0.216 | 62 |  | 7 | 0.04 | DGA satisfactory.
33000 | 1961 | 50 | 356 | 49 | 318 | 3472 | 30 | 2 | 4 | 1 | 1 | 23 | 0.231 | 57 |  | 8 | 0.03 | Test results satisfactory.
33000 | 1961 | 50 | 331 | 50 | 251 | 5220 | 38 | 8 | 26 | 6 | 2 | 23 | 0.246 | 39 |  | 4.9 | 0.056 | Test results satisfactory.
33000 | 1961 | 50 | 1742 | 61 | 676 | 5717 | 116 | 608 | 51 | 291 | 0 | 63 | 0.294 | 23 |  | 0.123 | 2.38 | Moisture and acidity levels are high. 2-furfural level is above 1ppm. Oil quality poor. RECOMMEND OIL CHANGE OR OIL RECLAMANATION.
33000 | 1961 | 50 | 149 | 51 | 50 | 883 | 23 | 47 | 10 | 18 | 1 | 30 | 0.025 | 36 |  | 4.4 | 0.147 | Test results are assessed as acceptable. Oil quality is low after oil change.
33000 | 1961 | 50 | 5495 | 55 | 490 | 4400 | 738 | 1950 | 1094 | 1220 | 3 | 36 | 0.048 | 28 |  | 0.421 | 0.832 | DDF and resistivity are outside acceptance limits. Moisture content of sample is high. 2-furfural level is high suggesting advanced rate of insulation degradation. Dissolved gas analysis suggests high temperature oil overheating has occurred. RECOMMEN
33000 | 1961 | 50 | 371 | 41.81 | 314 | 3004 | 47 | 3 | 2 | 1 | 4 | 31 | 0.183 | 45 |  | 5 | 0.046 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1961 | 50 | 586 | 41.81 | 443 | 4092 | 102 | 21 | 12 | 5 | 3 | 27 | 0.206 | 47 |  | 5.1 | 0.044 | Main tank dissolved gas analysis is satisfactory.
33000 | 1961 | 50 | 244 | 41.81 | 194 | 2425 | 0 | 13 | 18 | 15 | 4 | 26 | 0.197 | 53 |  | 5.9 | 0.038 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1961 | 50 | 156 | 41.81 | 133 | 1793 | 0 | 3 | 10 | 6 | 4 | 19 | 0.194 | 46 |  | 5.5 | 0.046 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1961 | 50 | 487 | 41.81 | 232 | 1826 | 78 | 81 | 69 | 9 | 18 | 32 | 0.224 | 41 |  | 3.9 | 0.06 | Sampled after buchholz trip.
33000 | 1961 | 50 | 606 | 41.81 | 277 | 2250 | 32 | 83 | 145 | 30 | 39 | 39 | 0.204 | 40 |  | 4.6 | 0.049 | Moisture content of oil is high. RECOMMEND RESAMPLE IN 6 MONTHS TO MONITOR GAS LEVELS.
33000 | 1961 | 50 | 292.3 | 46 | 263 | 3589.7 | 8.9 | 3.4 | 12.6 | 1.6 | 2.8 | 35 | 0.183 | 22 |  | 4 | 0.048 | Moisture content of sample is high. Breakdown voltage of sample is low. 2-furfural level is high suggesting accelerated rate of insulation degradation. Dissolved gas analysis is assessed as acceptable. RECOMMEND RESAMPLE IN 1 YEAR TO MONITOR CONDITION
33000 | 1961 | 50 | 276.5 | 41.81 | 251.8 | 4329.5 | 7.6 | 3 | 10.4 | 1.4 | 2.3 | 38 | 0.173 | 27 |  | 4 | 0.058 | 2-furfural level is high and trending upwards suggesting advanced state of insulation degradation. Oil quality is poor. Dissolved gas analysis is assessed as acceptable. RECOMMEND RESAMPLE IN 1 YEAR TO MONITOR CONDITION.
33000 | 1961 | 50 | 179.5 | 26 | 157 | 2959.1 | 4.1 | 5.2 | 7 | 0 | 6.2 | 25 | 0.181 | 41 |  | 5 | 0.044 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1961 | 50 | 257 | 30 | 232 | 2513 | 19 | 2 | 2 | 1 | 1 | 43 | 0.326 | 33 |  | 6.5 | 0.026 | D.G.A. Results satisfactory. Moisture content high - recommend resample using glass syringe to confirm.
33000 | 1961 | 50 | 257 | 41.81 | 232 | 2513 | 19 | 2 | 2 | 1 | 1 | 26 | 0.328 | 34 |  | 6.5 | 0.039 | Retested oil satisfactory.
33000 | 1961 | 50 | 245 | 40 | 218 | 2617 | 17 | 2 | 4 | 2 | 2 | 42 | 0.326 | 57 |  | 4.8 | 0.044 | DGA satisfactory.
33000 | 1961 | 50 | 332 | 62 | 302 | 2998 | 21 | 3 | 4 | 1 | 1 | 28 | 0.381 | 57 |  | 5.5 | 0.041 | Acidity content of oil high. Other test results satisfactory.
33000 | 1961 | 50 | 320 | 54 | 301 | 2706 | 11 | 2 | 3 | 1 | 2 | 49 | 0.327 | 35 |  | 5.3 | 0.045 | Oil sample taken before oil change.
33000 | 1961 | 50 | 376 | 62 | 354 | 3601 | 5 | 3 | 11 | 1 | 2 | 44 | 0.062 | 54 |  | 21.1 | 0.015 | Moisture content of oil high. Other test results satisfactory.
33000 | 1961 | 50 | 176 | 45 | 154 | 2942 | 0 | 3 | 14 | 1 | 4 | 29 | 0.054 | 37 |  | 21.1 | 0.017 | Moisture content of oil slightly high. Other test results satisfactory.
33000 | 1961 | 50 | 186 | 41.81 | 156 | 2509 | 6 | 2 | 15 | 1 | 6 | 32 | 0.056 | 29 |  | 15 | 0.019 | Moisture content of oil is slightly high. Other test results are assessed as acceptable.
33000 | 1961 | 50 | 234.6 | 54 | 198.3 | 2596.5 | 6 | 2.7 | 20.6 | 1.1 | 5.9 | 33 | 0.071 | 26 |  | 9 | 0.027 | Dissolved gas analysis is assessed as acceptable. Moisture content of oil is high. Breakdown voltage of oil is low. 2-furfural level is high suggesting accelerated rate of insulation degradation. RECOMMEND RESAMPLE IN 1 YEAR TO MONITOR CONDITION.
33000 | 1960 | 51 | 859 | 41.81 | 678 | 6088 | 64 | 23 | 81 | 12 | 1 | 49 | 0.216 | 32 |  | 7 | 0.034 | Slightly high moisture level though consistent with high acidity.
33000 | 1960 | 51 | 806 | 41.81 | 635 | 5342 | 45 | 23 | 90 | 12 | 1 | 47 | 0.22 | 38 |  | 5 | 0.049 | Moisture content of oil slightly high. DGA satisfactory.
33000 | 1960 | 51 | 272 | 41.81 | 166 | 4205 | 0 | 12 | 80 | 13 | 1 | 16 | 0.208 | 54 |  | 6.2 | 0.035 | Test results satisfactory.
33000 | 1960 | 51 | 65 | 41.81 | 60 | 513 | 0 | 1 | 4 | 0 | 0 | 19 | 0.021 | 61 |  | 32.4 | 0.018 | Test results satisfactory.
33000 | 1960 | 51 | 292 | 41.81 | 152 | 1508 | 0 | 34 | 92 | 13 | 1 | 21 | 0.01 | 47 |  | 40.6 | 0.023 | Test results are assessed as acceptable.
33000 | 1960 | 51 | 156.3 | 25 | 90.4 | 1344.5 | 0 | 9.2 | 47.5 | 9 | 0.2 | 11 | 0.01 | 49 |  | 26 | 0.022 | The test results are assessed as acceptable.
33000 | 1960 | 51 | 2095 | 41.81 | 1543 | 12218 | 337 | 112 | 94 | 9 | 0 |  | 0.062 | 42 |  | 5 | 0.037 | Samples taken after known tapchanger insulation breakdown.
33000 | 1960 | 51 | 1225 | 41.81 | 10 | 677 | 13 | 265 | 754 | 117 | 66 |  | 0.07 | 26 |  | 2.3 | 0.017 | Samples taken after known tapchanger insulation breakdown.
33000 | 1960 | 51 | 190 | 41.81 | 128 | 1128 | 48 | 3 | 2 | 2 | 7 | 9 | 0.033 | 52 |  | 130 | 0.0033 | Test results satisfactory.
33000 | 1960 | 51 | 146 | 20 | 123 | 952 | 0 | 2 | 19 | 2 | 0 | 33 | 0.041 | 30 |  | 30.6 | 0.014 | Test results satisfactory.
33000 | 1960 | 51 | 778 | 41.81 | 596 | 6029 | 94 | 35 | 41 | 12 | 0 | 27 | 0.166 | 46 |  | 40 | 0.064 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1960 | 51 | 1382 | 41.81 | 1156 | 8254 | 105 | 45 | 57 | 18 | 1 | 24 | 0.177 | 36 |  | 2.7 | 0.087 | CO level quite high. Recommend resample in 12 MONTHS.
33000 | 1960 | 51 | 1031 | 41.81 | 861 | 7788 | 71 | 35 | 48 | 16 | 0 | 26 | 0.168 | 38 |  | 2.3 | 0.116 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1960 | 51 | 413 | 41.81 | 374 | 3426 | 17 | 2 | 15 | 5 | 0 | 29 | 0.147 | 62 |  | 2.7 | 0.099 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1960 | 51 | 190 | 41.81 | 162 | 2412 | 17 | 2 | 5 | 4 | 0 | 23 | 0.19 | 45 |  | 3.3 | 0.073 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1960 | 51 | 29 | 41.81 | 23 | 759 | 2 | 2 | 2 | 0 | 0 | 17 | 0.123 | 69 |  | 3.8 | 0.062 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1960 | 51 | 147.9 | 50 | 137.6 | 2228.4 | 4.7 | 2.3 | 2.3 | 1 | 0 | 26 | 0.133 | 26 |  | 3 | 0.082 | DGA is assessed as acceptable. | Breakdown voltage of sample is low. Other test results are assessed as acceptable.
33000 | 1960 | 51 | 164.5 | 50 | 153 | 2011.5 | 5.1 | 2.2 | 2.7 | 1.5 | 0 | 28 | 0.119 | 66 |  | 3 | 0.068 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1960 | 51 | 218.2 | 41.81 | 164 | 2333.7 | 48.7 | 2.4 | 1.7 | 1.1 | 0.3 | 28 | 0.206 | 26 |  | 3 | 0.068 | DGA is assessed as acceptable. | Acidity level is high. Breakdown voltage is low. Other oil quality results are assessed as acceptable at present.
33000 | 1960 | 51 | 251.8 | 41.81 | 232.8 | 2594.6 | 9.1 | 7.1 | 2 | 0.8 | 0 | 28 | 0.151 | 41 |  | 4 | 0.074 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable. Corrosive IEC. Corrosive ASTM 4A.
33000 | 1960 | 51 | 197.5 | 20 | 185 | 2698.9 | 6.4 | 3.2 | 1.7 | 1.2 | 0 | 26 | 0.169 | 28 |  | 4 | 0.06 | DGA is assessed as acceptable. | Breakdown voltage is low. Other oil quality results are assessed as acceptable.
33000 | 1960 | 51 | 214.9 | 32 | 196.7 | 2721.6 | 11.3 | 2.8 | 2.8 | 1.3 | 0 | 31 | 0.159 | 41 |  | 3 | 0.067 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1960 | 51 | 210 | 42 | 173 | 1643 | 0 | 1 | 34 | 1 | 1 | 17 | 0.109 | 60 |  | 7 | 0.038 | Test results satisfactory. | Oil quality is assessed as acceptable.
33000 | 1960 | 51 | 245 | 40 | 197 | 2209 | 0 | 2 | 45 | 1 | 0 | 27 | 0.113 | 22 |  | 4.5 | 0.048 | Test results satisfactory. | Oil quality is assessed as acceptable.
33000 | 1960 | 51 | 321 | 41.81 | 276 | 1833 | 14 | 1 | 29 | 1 | 0 | 17 | 0.111 | 32 |  | 5 | 0.048 | Test results satisfactory. | Oil quality is assessed as acceptable.
33000 | 1960 | 51 | 286 | 43 | 255 | 1730 | 0 | 2 | 29 | 0 | 0 | 28 | 0.111 | 43 |  | 4.2 | 0.035 | Test results satisfactory. | Oil quality is assessed as acceptable.
33000 | 1960 | 51 | 256 | 41.81 | 217 | 2018 | 4 | 3 | 31 | 1 | 0 | 27 | 0.133 | 57 |  | 3.5 | 0.073 | Test results are assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1960 | 51 | 398.3 | 48 | 339.9 | 2388.6 | 8.1 | 3 | 45.8 | 1.2 | 0.3 | 26 | 0.171 | 46 |  | 3 | 0.067 | The test results are assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1960 | 51 | 414.3 | 42 | 356.9 | 3662.2 | 8 | 3.2 | 44.2 | 2 | 0 | 23 | 0.171 | 70 |  | 3.2 | 0.077 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1960 | 51 | 322.4 | 41.81 | 278.9 | 3028.5 | 8.6 | 2.9 | 31.4 | 0.6 | 0 | 20 | 0.2 | 71 |  | 3 | 0.07 | DGA is assessed as acceptable. | Acidity level is high. Other oil quality results are assessed as acceptable.
33000 | 1960 | 51 | 288 | 50 | 257.7 | 2439.6 | 5.3 | 2.6 | 21.6 | 0.8 | 0 | 25 | 0.181 | 64 |  | 3 | 0.084 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable. Corrosive IEC. Non-corrosive ASTM 3B.
33000 | 1960 | 51 | 255.9 | 52 | 224.6 | 2689.8 | 4.7 | 2.1 | 23.3 | 1.2 | 0 | 19 | 0.22 | 83 |  | 3 | 0.068 | DGA is assessed as acceptable. | Acidity level is high. Other oil quality results are assessed as acceptable.
33000 | 1960 | 51 | 250.1 | 48 | 219 | 2668.6 | 6.6 | 2.5 | 21.4 | 0.6 | 0 | 22 | 0.21 | 70 |  | 3 | 0.07 | DGA is assessed as acceptable. | Acidity level is high. Other oil quality results are assessed as acceptable.
33000 | 1960 | 51 | 112 | 28 | 93 | 1372 | 5 | 1 | 12 | 0 | 1 | 23 | 0.057 | 32 |  | 19 | 0.017 | Dissolved gas analysis is assessed as acceptable. Oil quality is assessed as acceptable.
33000 | 1960 | 51 | 5 | 25 | 5 | 140 | 0 | 0 | 0 | 0 | 0 | 7 | 0.01 | 68 |  | 132.5 | 0.006 | Dissolved gas analysis is assessed as acceptable. Oil quality is assessed as acceptable.
33000 | 1960 | 51 | 72 | 50 | 67 | 866 | 2 | 0 | 2 | 1 | 0 | 19 | 0.011 | 75 |  | 63.3 | 0.014 | Dissolved gas analysis is assessed as acceptable. Oil quality is assessed as acceptable.
33000 | 1960 | 51 | 198.9 | 52 | 161.6 | 2104.1 | 6.7 | 1.6 | 27.4 | 1.4 | 0.2 | 15 | 0.01 | 51 |  | 23 | 0.022 | Dissolved gas analysis is assessed as acceptable. Oil quality is assessed as acceptable.
33000 | 1960 | 51 | 168.6 | 48 | 141.2 | 1807.8 | 4.5 | 1.4 | 20.5 | 1 | 0 | 22 | 0.01 | 54 |  | 26 | 0.015 | Dissolved gas analysis is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1960 | 51 | 188.7 | 48 | 158.1 | 1879.4 | 4 | 2 | 24.6 | 0 | 0 | 18 | 0.011 | 67 |  | 23 | 0.022 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1960 | 51 | 226.7 | 42 | 193.7 | 2022.8 | 5.4 | 1.6 | 25.5 | 0.5 | 0 | 19 | 0.013 | 31 |  | 24 | 0.019 | DGA is assessed as acceptable. | Breakdown voltage is low. Other oil quality results are assessed as acceptable.
33000 | 1960 | 51 | 182.2 | 50 | 155 | 1847 | 4 | 2 | 21 | 0.2 | 0 | 21 | 0.015 | 51 |  | 15 | 0.043 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable. Corrosive IEC. Corrosive ASTM 4B.
33000 | 1960 | 51 | 88 | 44 | 71.8 | 1109.1 | 2.5 | 2.5 | 10.4 | 0.8 | 0 | 14 | 0.009 | 82 |  | 22 | 0.019 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable. Corrosive IEC. Corrosive ASTM 4A
33000 | 1960 | 51 | 0 | 41.81 | [7 empty] | 18 | 0.148 | 33 |  | 6 | 0.047 |  | Oil quality is assessed as acceptable.
33000 | 1960 | 51 | 256 | 41.81 | 226 | 1882 | 0 | 1 | 27 | 1 | 1 | 19 | 0.125 | 69 |  | 2.5 | 0.07 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1960 | 51 | 295 | 41.81 | 255 | 2607 | 0 | 2 | 37 | 0 | 1 | 24 | 0.173 | 64 |  | 3.7 | 0.069 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable. PCB contaminated oil.
33000 | 1960 | 51 | 382 | 41.81 | 311 | 3658 | 19 | 4 | 42 | 6 | 0 | 38 | 0.186 | 60 |  | 2.1 | 0.096 | Test results are assessed as acceptable for age of transformer. | Oil quality is assessed as acceptable.
33000 | 1960 | 51 | 360.4 | 40 | 290.3 | 3346.9 | 9.1 | 2 | 57.4 | 1.3 | 0.3 | 29 | 0.206 | 42 |  | 3 | 0.076 | DGA is assessed as acceptable. | Acidity and 2-furfural levels are trending upwards. Other test results are assessed as acceptable.
33000 | 1960 | 51 | 360 | 46 | 301.1 | 3878.9 | 10.5 | 2.1 | 45.3 | 0.8 | 0.2 | 33 | 0.225 | 40 |  | 3 | 0.083 | DGA is assessed as acceptable. | Acidity and 2-furfural levels are high. Other test results are assessed as acceptable.
33000 | 1960 | 51 | 335.9 | 42 | 301.7 | 3070.7 | 8.4 | 1.8 | 24 | 0 | 0 | 25 | 0.3 | 46 |  | 2 | 0.08 | DGA is assessed as acceptable. | Acidity level is high. Other oil quality results are assessed as acceptable.
33000 | 1960 | 51 | 291.2 | 52 | 257.7 | 3112.1 | 6.7 | 1.7 | 24.5 | 0.6 | 0 | 30 | 0.252 | 59 |  | 3 | 0.075 | DGA is assessed as acceptable. | Acidity level is high. Corrosive IEC. Non-corrosive ASTM 3B.
33000 | 1960 | 51 | 829 | 57 | 722 | 6384 | 62 | 17 | 16 | 12 | 0 | 36 | 0.307 | 55 |  | 0.9 | 0.348 | Loss tangent and resistivity outside limits recommended by AS 1883-1976. AS 1883 Recommends oil replacement.
33000 | 1960 | 51 | 899 | 50 | 760 | 4636 | 91 | 24 | 14 | 10 | 0 | 42 | 0.311 | 37 |  | 0.9 | 0.286 | D.G.A. Satisfactory. Oil quality poor. Loss tangent and resistivity outside limits recommended by AS1883-1976. AS1883 RECOMMENDS OIL REPLACEMENT.
33000 | 1960 | 51 | 1294 | 70 | 1092 | 5217 | 108 | 57 | 20 | 17 | 0 | 67 | 0.37 | 24 |  | 1.5 | 0.259 | D.G.A. Satisfactory. High acidity and poor oil quality. Oil change should be considered.
33000 | 1960 | 51 | 915 | 50 | 739 | 6034 | 75 | 41 | 29 | 31 | 0 | 48 | 0.404 | 38 |  | 1 | 0.305 | Oil sample prior to oil change.
33000 | 1960 | 51 | 39 | 52 | 33 | 552 | 0 | 2 | 3 | 1 | 0 | 26 | 0.031 | 27 |  | 21.7 | 0.029 | Test results satisfactory.RESAMPLE IN 3 MONTHS TO MONITOR CHANGES.
33000 | 1960 | 51 | 277 | 52 | 253 | 3050 | 0 | 1 | 20 | 3 | 0 | 41 | 0.048 | 49 |  | 13.8 | 0.035 | Test results satisfactory.
33000 | 1960 | 51 | 301 | 41.81 | 242 | 6413 | 16 | 2 | 40 | 1 | 0 | 44 | 0.071 | 45 |  | 10.1 | 0.031 | Moisture content of oil high. Other test results satisfactory. Transformer has history of high moisture levels.
33000 | 1960 | 51 | 467 | 56 | 368 | 10313 | 41 | 3 | 54 | 1 | 0 | 52 | 0.088 | 17 |  | 13.7 | 0.027 | Moisture content of oil is high. Dielectric strength low. 2-furfural is above 1ppm. Carbon oxide gas levels are high. RECOMMEND RESAMPLE IN 6 MONTHS TO MONITOR.
33000 | 1960 | 51 | 415 | 44 | 321 | 11470 | 22 | 3 | 68 | 1 | 0 | 36 | 0.078 | 39 |  | 10.7 | 0.033 | Moisture content of oil is high. 2-furfural level is above 1ppm. Carbon dioxide levels are high. RECOMMEND RESAMPLE IN 1 YEAR TO MONITOR TREND.
33000 | 1960 | 51 | 627 | 69 | 365 | 11398 | 95 | 23 | 92 | 5 | 47 | 49 | 0.081 | 31 |  | 12.3 | 0.023
33000 | 1960 | 51 | 555.8 | 51 | 437.5 | 13064 | 27.3 | 6.3 | 81.3 | 3.1 | 0.3 | 50 | 0.097 | 17 |  | 11 | 0.024 | DGA is assessed as acceptable. | Moisture content of sample is high. Dielectric strenght is outside acceptance limit.
33000 | 1960 | 51 | 753.4 | 50 | 605.2 | 19791.2 | 39.8 | 7.1 | 97.8 | 3.5 | 0 | 56 | 0.114 | 13 |  | 8.9129 | 0.04488 | Carbon dioxide level is high. | The test results are consistent with main tank sample. Moisture content of sample is high. Breakdown voltage of sample is low.
33000 | 1960 | 51 | 701.6 | 50 | 521.8 | 19074.9 | 74.4 | 6.6 | 95.7 | 3.1 | 0 | 58 | 0.112 | 15 |  | 11.6584 | 0.02783 |  | Moisture content of sample is high. Breakdown voltage of sample is low.
33000 | 1960 | 51 | 723.5 | 69 | 496.3 | 15133.8 | 148.6 | 5.5 | 71 | 2 | 0.1 | 52 | 0.109 | 13 |  | 12 | 0.028 | Dissolved gas levels are relatively stable. | Oil quality is poor.
33000 | 1960 | 51 | 852 | 41.81 | 430 | 3194 | 102 | 15 | 60 | 1 | 244 | 31 | 0.09 | 72 |  | 7 | 0.04 | DGA is assessed as acceptable. Acetylene gas possibly from tapchanger. | Moisture content of oil slightly high. Other test results satisfactory.
33000 | 1960 | 51 | 837 | 41.81 | 276 | 2721 | 219 | 20 | 48 | 1 | 273 | 17 | 0.08 | 65 |  | 6.9 | 0.031 | Test results are assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1960 | 51 | 662 | 41.81 | 300 | 2712 | 107 | 13 | 41 | 1 | 200 | 26 | 0.074 | 56 |  | 5.1 | 0.046 | Test results are assessed as acceptable. Acetylene gas possibly from tapchanger. | Oil quality is assessed as acceptable.
33000 | 1960 | 51 | 109 | 40 | 58 | 1118 | 0 | 1 | 16 | 1 | 33 | 18 | 0.087 | 64 |  | 3 | 0.07 | Dissolved gas levels are reduced. | Other test results are assessed as acceptable.
33000 | 1960 | 51 | 69.5 | 26 | 39.9 | 1821.3 | 15.9 | 0.9 | 8.1 | 0.8 | 3.9 | 41 | 0.067 | 36 |  | 6.2 | 0.045 | DGA is assessed as acceptable. | Moisture content is high. Breakdown voltage is slightly low. Other oil quality results are assessed as acceptable.
33000 | 1960 | 51 | 59 | 26 | 43.4 | 964.1 | 4.5 | 0.8 | 7.5 | 0.4 | 2.4 | 23 | 0.078 | 49 |  | 5 | 0.053 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1960 | 51 | 14.7 | 41.81 | 13.7 | 192.3 | 0 | 0.3 | 0.4 | 0.1 | 0.2 | 7 | 0 | 65 |  | 54 | 0.015 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1960 | 51 | 12.7 | 20 | 7 | 314.6 | 4.9 | 0.6 | 0.1 | 0.1 | 0 | 16 | 0.01 | 72 |  | 25 | 0.031 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1960 | 51 | 12.2 | 20 | 11.6 | 209.4 | 0 | 0.4 | 0.1 | 0.1 | 0 | 9 | 0.01 | 75 |  | 42 | 0.019 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1960 | 51 | 535 | 64 | 200 | 2086 | 62 | 12 | 37 | 2 | 222 | 23 | 0.1 | 37 |  | 7.7 | 0.037 | DGA is assessed as acceptable. Acetylene gas possibly communicating from tapchanger. | Oil quality is assessed as acceptable.
33000 | 1960 | 51 | 599 | 52 | 286 | 2697 | 76 | 11 | 36 | 2 | 188 | 25 | 0.073 | 57 |  | 9.4 | 0.034 | DGA is assessed as acceptable. Acetylene gas possibly communicating from tapchanger. | Oil quality is assessed as acceptable.
33000 | 1960 | 51 | 1119 | 50 | 261 | 3112 | 182 | 31 | 60 | 2 | 583 | 28 | 0.074 | 55 |  | 7 | 0.036 | DGA is assessed as acceptable. Acetylene gas possibly communicating from tapchanger. | Oil quality is assessed as acceptable.
33000 | 1960 | 51 | 40.5 | 22 | 23.1 | 866 | 0 | 1.3 | 6.6 | 0.6 | 8.9 | 13 | 0.038 | 75 |  | 11 | 0.031 | The test results are assessed as acceptable at present.
33000 | 1960 | 51 | 623.6 | 54 | 469.6 | 7030.3 | 59.4 | 10.2 | 18.4 | 3.5 | 62.5 | 46 | 0.04 | 19 |  | 10.7657 | 0.028468 | DGA is assessed as acceptable | Moisture content of sample is high. Breakdown voltage of sample is low.
33000 | 1960 | 51 | 506.9 | 44 | 377.3 | 5730 | 46 | 8.1 | 16.5 | 2 | 57 | 26 | 0.038 | 33 |  | 8 | 0.036 | Dissolved gas levels are reduced slightly.
33000 | 1960 | 51 | 527.9 | 44 | 388.6 | 5885.9 | 49.1 | 7.9 | 17.1 | 4.3 | 60.9 | 29 | 0.042 | 25 |  | 8 | 0.037 | The test results are assessed as relatively stable.
33000 | 1960 | 51 | 731.6 | 48 | 464.6 | 7022.4 | 71.7 | 14.4 | 31.2 | 3.9 | 145.8 | 34 | 0.045 | 16 |  | 8 | 0.034 | DGA is assessed as acceptable. | Breakdown voltage is very low. Moisture content is slightly high.
33000 | 1960 | 51 | 701 | 52 | 564 | 4794 | 123 | 4 | 8 | 2 | 0 | 47 | 0.141 | 52 |  | 10 | 0.0238 | D.G.A. Satisfactory. | Moisture level due to operating temperature of transformer.
33000 | 1960 | 51 | 437 | 44 | 344 | 3539 | 84 | 3 | 5 | 1 | 0 | 26 | 0.223 | 64 |  | 7 | 0.0437 | D.G.A. Satisfactory. | Acidity level double; checked and confirmed.
33000 | 1960 | 51 | 543 | 40 | 439 | 3263 | 96 | 3 | 4 | 1 | 0 | 42 | 0.266 | 68 |  | 3.3 | 0.065 | DGA satisfactory. | Acidity and moisture level slightly high.
33000 | 1960 | 51 | 7 | 41.81 | 6 | 176 | 0 | 1 | 0 | 0 | 0 | 10 | 0.013 | 64 |  | 63.3 | 0.006 | Test results satisfactory after oil change. (New oil.)
33000 | 1960 | 51 | 244 | 54 | 150 | 3087 | 90 | 2 | 2 | 0 | 0 | 43 | 0.036 | 22 |  | 23.8 | 0.014 | DGA is assessed as acceptable. | Moisture content is high; dielectric strength is low possibly sample contamination. Other test results are assessed as acceptable.
33000 | 1960 | 51 | 509.3 | 56 | 331.7 | 6110.7 | 49.6 | 24.1 | 91.9 | 12 | 0 | 29 | 0.032 | 25 |  | 16 | 0.019 | Dissolved gas analysis suggests high temperature oil overheating has occurred. | Breakdown voltage of sample is low.
33000 | 1960 | 51 | 472.1 | 50 | 298.4 | 5763.5 | 64.6 | 19 | 77.9 | 11.4 | 0.8 | 40 | 0.029 | 21 |  | 15.1767 | 0.020383 | DGA is assessed as acceptable. | Moisture content of sample is high. Breakdown voltage of sample is low. Other test results are assessed as acceptable at present.
33000 | 1960 | 51 | 299.8 | 50 | 189.3 | 3896.4 | 43.7 | 14.4 | 45.2 | 7.2 | 0 | 42 | 0.031 | 17 |  | 19.3 | 0.016 | DGA is assessed as acceptable. | Breakdown voltage is low. Moisture content is high.
33000 | 1960 | 51 | 357.4 | 49 | 231.5 | 4373.3 | 36.5 | 18.6 | 61.4 | 8.7 | 0.7 | 36 | 0.031 | 28 |  | 11 | 0.026 | DGA is assessed as acceptable. | Moisture content is high. Breakdown voltage is low. Other oil quality results are assessed as acceptable.
33000 | 1960 | 51 | 319 | 48 | 211 | 4034.3 | 32.7 | 13.8 | 54.1 | 6.7 | 0.7 | 35 | 0.033 | 24 |  | 13 | 0.02 | DGA is assessed as acceptable. | Moisture content is high. Breakdown voltage is low. Other oil quality results are assessed as acceptable.
33000 | 1960 | 51 | 273.4 | 42 | 168.5 | 3655.2 | 24.4 | 16 | 57 | 7.5 | 0 | 34 | 0.032 | 24 |  | 14 | 0.018 | DGA is assessed as acceptable. | Moisture content is slightly high. Breakdown voltage is low. Other oil quality results are assessed as acceptable.
33000 | 1960 | 51 | 234.8 | 42 | 132.3 | 2813.2 | 20.4 | 16.2 | 56 | 9.2 | 0.7 | 38 | 0.033 | 32 |  | 7 | 0.038 | DGA is assessed as acceptable. | Moisture content is high. Breakdown voltage is low. Other oil quality results are assessed as acceptable.
33000 | 1960 | 51 | 813 | 33 | 683 | 4112 | 57 | 23 | 42 | 7 | 1 | 29 | 0.154 | 62 |  | 3.5 | 0.094 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1960 | 51 | 515 | 22 | 441 | 2572 | 32 | 12 | 25 | 4 | 1 | 18 | 0.159 | 46 |  | 3 | 0.082 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1960 | 51 | 920 | 41.81 | 545 | 3488 | 69 | 75 | 203 | 22 | 6 | 30 | 0.188 | 58 |  | 3.6 | 0.075 | Gas analysis suggest high temperature hot spot. | Oil quality is assessed as acceptable.
33000 | 1960 | 51 | 675 | 54 | 400 | 2371 | 30 | 55 | 162 | 18 | 10 | 86 | 0.196 | 27 |  | 3.7 | 0.064 | Gas levels remained stable. | Moisture content abnormally high. Possibly sampling problem.
33000 | 1960 | 51 | 316 | 55 | 196 | 1792 | 0 | 16 | 89 | 11 | 4 | 28 | 0.164 | 67 |  | 2.9 | 0.08 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1960 | 51 | 1050 | 41.81 | 334 | 3193 | 38 | 148 | 462 | 55 | 13 | 35 | 0.167 | 58 |  | 2.3 | 0.089 | Gas analysis suggests hot spot in oil. | Moisture content of oil is high.
33000 | 1960 | 51 | 1242 | 41.81 | 515 | 3882 | 54 | 144 | 457 | 56 | 16 | 39 | 0.201 | 51 |  | 2.6 | 0.092 | Hydrocarbon gas levels have remained stable. | Moisture content of oil is high.
33000 | 1960 | 51 | 1584 | 48 | 589 | 4592 | 112 | 207 | 587 | 70 | 19 | 31 | 0.189 | 41 |  | 2.5 | 0.095 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1960 | 51 | 1623.9 | 48 | 862.9 | 8111.3 | 84.6 | 121.3 | 473.3 | 77.1 | 4.7 | 5 | 0.23 | 39 |  | 2 | 0.104 | 2-furfural and carbon dioxide levels are high and trending upwards suggesting advanced state of insulation degradation. | Acidity level of sample is high.
33000 | 1960 | 51 | 1074.5 | 19 | 499.2 | 5612.6 | 52.6 | 90.4 | 358.1 | 63.9 | 10.3 | 29 | 0.235 | 43 |  | 2 | 0.116 | Dissolved gas levels are relatively stable. | Acidity level is high. Other oil quality results are assessed as acceptable.
33000 | 1960 | 51 | 798 | 57 | 734 | 5883 | 44 | 5 | 10 | 4 | 1 | 57 | 0.594 | 21 |  | 2.5 | 0.078 | Very high acidity and poor dielectric strength.OIL CHANGE SHOULD BE CONSIDERED
33000 | 1960 | 51 | 312 | 40 | 302 | 3671 | 0 | 3 | 6 | 1 | 0 | 40 | 0.58 | 53 |  | 2.3 | 0.1 | Very high acidity. Oil change is recommended.
33000 | 1960 | 51 | 632 | 38 | 587 | 4632 | 31 | 4 | 8 | 2 | 0 | 48 | 0.47 | 41 |  | 3 | 0.085 | Acidity level high. Other test results satisfactory.
33000 | 1960 | 51 | 698 | 41.81 | 640 | 4088 | 48 | 3 | 6 | 1 | 0 | 49 | 0.38 | 39 |  | 2.7 | 0.081 | DGA is assessed as acceptable. | Acidity level is high.
33000 | 1960 | 51 | 220 | 41.81 | 203 | 2597 | 0 | 2 | 9 | 2 | 4 | 34 | 0.408 | 43 |  | 2.7 | 0.086 | DGA is assessed as acceptable. | Acidity level is high.
33000 | 1959 | 52 | 264 | 41.81 | 258 | 2387 | 0 | 2 | 2 | 1 | 1 | 24 | 0.293 | 61 |  | 3.9 | 0.065 | DGA is assessed as acceptable. | Acidity content of oil high. Other test results satisfactory.
33000 | 1959 | 52 | 167 | 41.81 | 162 | 2052 | 0 | 2 | 3 | 0 | 0 | 19 | 0.262 | 69 |  | 4.1 | 0.067 | DGA is assessed as acceptable. | Acidity level of oil slightly high. Other test results satisfactory.
33000 | 1959 | 52 | 306 | 48 | 279 | 3688 | 19 | 2 | 4 | 2 | 0 | 26 | 0.289 | 71 |  | 3.7 | 0.056 | DGA is assessed as acceptable. | Acidity level is high. Other test results are assessed as acceptable.
33000 | 1959 | 52 | 191.1 | 44 | 181.2 | 4616 | 0 | 2.9 | 5.6 | 1.4 | 0 | 16 | 0.223 | 72 |  | 4 | 0.062 | DGA is assessed as acceptable. | Acidity level of sample is high. Other test results are assessed as acceptable.
33000 | 1959 | 52 | 225.1 | 41.81 | 212.5 | 4620.9 | 5.2 | 2.5 | 4 | 0.9 | 0 | 24 | 0.223 | 47 |  | 3 | 0.074 | DGA is assessed as acceptable. | Acidity level is high but stable. Other oil quality results are assessed as acceptable.
33000 | 1959 | 52 | 171 | 41.81 | 161.4 | 2734.4 | 3.9 | 2 | 2.6 | 1.1 | 0 | 24 | 0.243 | 52 |  | 4 | 0.061 | DGA is assessed as acceptable. | Acidity level is high. Other oil quality results are assessed as acceptable.
33000 | 1959 | 52 | 164.8 | 25 | 155.3 | 2524.8 | 4.6 | 1.7 | 2.4 | 0.8 | 0 | 30 | 0.257 | 25 |  | 3 | 0.064 | DGA is assessed as acceptable. | Acidity level is high. Other oil quality results are assessed as acceptable.
33000 | 1959 | 52 | 201.8 | 22 | 182.1 | 3566.7 | 13.2 | 3 | 2.7 | 0.8 | 0 | 37 | 0.256 | 33 |  | 3 | 0.083 | DGA is assessed as acceptable. | Breakdown voltage is low. Acidity level is high.
33000 | 1959 | 52 | 236.8 | 41.81 | 223.9 | 4156.3 | 6.6 | 2.6 | 3.1 | 0.6 | 0 | 28 | 0.262 | 55 |  | 4 | 0.066 | DGA is assessed as acceptable. | Acidity level is high. Other oil quality results are assessed as acceptable. Corrosive IEC. Corrosive ASTM 4A.
33000 | 1959 | 52 | 167 | 41.81 | 157.3 | 2956 | 4.1 | 2 | 2.7 | 0.9 | 0 | 31 | 0.25 | 59 |  | 5 | 0.048 | DGA is assessed as acceptable. | Acidity level is high. Other oil quality results are assessed as acceptable.
33000 | 1959 | 52 | 1292 | 40 | 744 | 3939 | 141 | 139 | 63 | 204 | 1 | 61 | 0.279 | 18 |  | 0.6 | 0.648 | Oil appears to be of very poor quality and unacceptable by AS 1883 standards. Test 25/8/88 confirms high moisture (75)
33000 | 1959 | 52 | 1395 | 41.81 | 790 | 3761 | 179 | 147 | 66 | 213 | 0 | 66 | 0.338 | 48 |  | 0.6 | 0.643 | Oil poor quality; D.G.A. suggests slight overheating taking place.
33000 | 1959 | 52 | 1518 | 50 | 802 | 3497 | 299 | 148 | 67 | 202 | 0 | 85 | 0.336 | 34 |  | 0.7 | 0.68 | D.G.A. Stable. Extremely poor oil quality.
33000 | 1959 | 52 | 1083 | 35 | 655 | 3239 | 112 | 113 | 40 | 163 | 0 | 63 | 0.315 | 24 |  | 0.5 | 0.717 | Oil quality bad. DGA satisfactory.
33000 | 1959 | 52 | 1763 | 41 | 1099 | 4375 | 296 | 150 | 42 | 176 | 0 | 74 | 0.329 | 50 |  | 0.4 | 0.748 | Oil quality bad. Moisture content high. Acidity level quite high. DGA remains stable.
33000 | 1959 | 52 | 934 | 54 | 600 | 3050 | 76 | 101 | 29 | 128 | 0 | 107 | 0.353 | 58 |  | 0.5 | 0.642 | Oil quality bad. Moisture content high. Acidity level quite high. DGA remains stable.
33000 | 1959 | 52 | 536 | 46 | 347 | 4950 | 95 | 27 | 20 | 45 | 2 | 29 | 0.167 | 38 |  | 6 | 0.0698 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1959 | 52 | 425 | 34 | 332 | 4050 | 53 | 9 | 10 | 18 | 3 | 26 | 0.155 | 52 |  | 4 | 0.0606 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1959 | 52 | 616 | 45 | 418 | 6710 | 135 | 18 | 21 | 23 | 1 | 52 | 0.167 | 45 |  | 4.4 | 0.046 | Moisture and acidity levels of oil high. DGA satisfactory.
33000 | 1959 | 52 | 534 | 62 | 445 | 7610 | 41 | 6 | 28 | 3 | 11 | 56 | 0.206 | 55 |  | 5.4 | 0.05 | Moisture and acidity levels are high. 2-furfural is above 1ppm. Other test results are assessed as acceptable.
33000 | 1959 | 52 | 1105.1 | 52 | 904.5 | 14360.8 | 135.7 | 15.9 | 35.2 | 11 | 2.8 | 50 | 0.2415 | 21 |  | 4 | 0.066 | 2-furfural level is trending upwards suggesting accelerated rate of insulation degradation. Oil quality is poor. Dissolved gas analysis is assessed as acceptable. RECOMMEND RESAMPLE IN 1 YEAR TO MONITOR CONDITION.
33000 | 1959 | 52 | 1444.4 | 50 | 1069.7 | 11404.8 | 222.3 | 77.7 | 37.5 | 36.9 | 0.3 | 77 | 0.28 | 13 |  | 3.5108 | 0.07524 | 2-furfural and carbon dioxide levels are very high suggesting advanced state of insulation degradation. Moisture content of sample is high. Breakdown voltage of sample is low. Acidity level of sample is high. RECOMMEND OIL CHANGE / TREATMENT. RECOMME
33000 | 1959 | 52 | 1394.4 | 50 | 1056.2 | 11117.5 | 182.5 | 79.1 | 37.5 | 38.6 | 0.5 | 76 | 0.286 | 16 |  | 3.3281 | 0.07964 | The test results are consistent with main tank sample. Moisture content of sample is high. Breakdown voltage of sample is low. Acidity level of sample is high. Carbon dioxide level is high.
33000 | 1959 | 52 | 1269.9 | 82 | 966.7 | 8360 | 200.6 | 49.6 | 25.3 | 26.5 | 1.2 | 59 | 0.293 | 18 |  | 4 | 0.076 | Dissolved gas levels are relatively stable. | Oil quality is poor.
33000 | 1959 | 52 | 1278 | 41.81 | 587 | 3423 | 530 | 69 | 21 | 70 | 1 | 29 | 0.222 | 48 |  | 0.9 | 0.366 | Oil quality poor; H2 level quite high. Resample to confirm poor oil quality; then consider possible oil replacement.
33000 | 1959 | 52 | 1209 | 41.81 | 604 | 3360 | 442 | 68 | 22 | 73 | 0 | 42 | 0.212 | 52 |  | 0.9 | 0.31 | Oil quality poor. Hydrogen level quite high.
33000 | 1959 | 52 | 1372 | 41.81 | 765 | 2898 | 421 | 86 | 21 | 76 | 3 | 51 | 0.237 | 13 |  | 1.5 | 0.23 | Oil quality poor. Breakdown strength of oil low. Gas levels stable. Recheck breakdown strength on site?
33000 | 1959 | 52 | 1751 | 41.81 | 747 | 3597 | 780 | 96 | 25 | 103 | 0 | 51 | 0.323 | 21 |  | 0.5 | 0.484 | Acidity and moisture level high. Oil quality and breakdown level unacceptable STRONGLY RECOMMEND OIL CHANGE.
33000 | 1959 | 52 | 4139 | 41.81 | 585 | 4418 | 2121 | 234 | 275 | 16 | 908 | 37 | 0.051 | 55 |  | 19.6 | 0.019 | Fault gas levels high in main tank. Suggests fault in main tank.
33000 | 1959 | 52 | 101 | 55 | 90 | 2769 | 0 | 3 | 3 | 1 | 4 | 22 | 0.057 | 60 |  | 35 | 0.011 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1959 | 52 | 40 | 52 | 29 | 3079 | 0 | 3 | 5 | 2 | 1 | 20 | 0.055 | 60 |  | 25 | 0.014 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1959 | 52 | 399 | 45 | 347 | 3440 | 41 | 3 | 7 | 1 | 0 | 23 | 0.046 | 56 |  | 7.7 | 0.056 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1959 | 52 | 645 | 66 | 598 | 5591 | 25 | 5 | 16 | 1 | 0 | 44 | 0.067 | 38 |  | 4 | 0.083 | DGA is assessed as acceptable. | Moisture content of oil is high. Other test results are assessed as acceptable.
33000 | 1959 | 52 | 360.8 | 42 | 327 | 6935.7 | 15.1 | 3.3 | 12.5 | 2.9 | 0 | 31 | 0.085 | 26 |  | 0.29 | 1.12 | Dissolved gas analysis is assessed as acceptable. | Breakdown voltage of sample is low. Resistivity of sample is outside acceptance limit.
33000 | 1959 | 52 | 540.5 | 54 | 476.7 | 6813.2 | 46.4 | 4.5 | 10.4 | 2.5 | 0 | 57 | 0.094 | 23 |  | 0.44428 | 0.7018 | Dissolved gas analysis is assessed as acceptable. | Moisture content of sample is high. Breakdown voltage of sample is low. Dielectric Dissipation Factor (DDF) and Resistivity are outside acceptance limits.
33000 | 1959 | 52 | 384.2 | 52 | 356.4 | 5762.9 | 15.6 | 4.2 | 6.2 | 1.8 | 0 | 42 | 0.07 | 21 |  | 0.581 | 0.481 | DGA is assessed as acceptable. | Oil quality is poor.
33000 | 1959 | 52 | 320.9 | 48 | 284.6 | 5442.6 | 17.2 | 7.7 | 10.8 | 0.6 | 0 | 45 | 0.102 | 20 |  | 0.658 | 0.438 | DGA is assessed as acceptable. | Oil quality is poor.
33000 | 1959 | 52 | 248.5 | 48 | 221.7 | 3596.8 | 15.8 | 3.5 | 4.8 | 2.7 | 0 | 34 | 0.08 | 26 |  | 0.767 | 0.384 | DGA is assessed as acceptable. | Oil quality is poor.
33000 | 1959 | 52 | 376.6 | 40 | 337.5 | 5581.7 | 27.1 | 4.5 | 5.5 | 2 | 0 | 36 | 0.088 | 26 |  | 0.737 | 0.368 | DGA is assessed as acceptable. | Breakdown voltage is low. DDF is high and Resistivity is low.
33000 | 1959 | 52 | 450.2 | 56 | 388.2 | 7125.5 | 21.8 | 12.9 | 20.4 | 6.9 | 0 | 52 | 0.104 | 22 |  | 0.813 | 0.324 | DGA is assessed as acceptable. | Oil quality is poor. Corrosive IEC. Corrosive ASTM 4B.
33000 | 1959 | 52 | 329.3 | 39 | 290.4 | 5103.9 | 29.4 | 2.8 | 4.3 | 2.4 | 0 | 37 | 0.092 | 22 |  | 0.782 | 0.343 | DGA is assessed as acceptable. | Breakdown voltage is low. DDF is high and Resistivity is low. Acidity is acceptable. Corrosive IEC. Corrosive ASTM 4B.
33000 | 1959 | 52 | 389.7 | 52 | 336.5 | 5850.3 | 28.1 | 6.2 | 18.9 | 0 | 0 | 50 | 0.09 | 18 |  | 0.934 | 0.292 | DGA is assessed as acceptable. | Acidity is assessed as acceptable. Other oil quality results are assessed as poor.
33000 | 1958 | 53 | 261 | 41.81 | 161 | 4831 | 60 | 3 | 35 | 2 | 0 | 22 | 0.043 | 62 |  | 25 | 0.014 | Test results satisfactory. | Oil quality is assessed as acceptable.
33000 | 1958 | 53 | 230 | 32 | 169 | 3552 | 28 | 2 | 29 | 2 | 0 | 24 | 0.043 | 65 |  | 14.7 | 0.021 | Test results satisfactory. | Oil quality is assessed as acceptable.
33000 | 1958 | 53 | 195 | 48 | 136 | 3753 | 25 | 1 | 33 | 0 | 0 | 33 | 0.058 | 44 |  | 11.3 | 0.028 | Test results satisfactory. | Oil quality is assessed as acceptable.
33000 | 1958 | 53 | 263.3 | 50 | 170.6 | 5888.6 | 0 | 2 | 88.9 | 1.4 | 0.4 | 27 | 0.075 | 24 |  | 6 | 0.045 | The test results are assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1958 | 53 | 300.1 | 43 | 226.7 | 6035.6 | 5 | 2.2 | 65.4 | 0.8 | 0 | 28 | 0.096 | 48 |  | 6 | 0.042 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1958 | 53 | 298 | 41 | 220.3 | 5669.4 | 14.4 | 2.4 | 60.1 | 0.7 | 0.1 | 28 | 0.086 | 43 |  | 7 | 0.043 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1958 | 53 | 265 | 37 | 213.1 | 4848.3 | 4.1 | 2.3 | 45.5 | 0 | 0 | 24 | 0.088 | 46 |  | 6 | 0.039 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1958 | 53 | 247.4 | 36 | 190.9 | 3850.6 | 12.3 | 1.9 | 42.3 | 0 | 0 | 23 | 0.103 | 69 |  | 7 | 0.045 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable. Non-corrosive IEC. Non-corrosive ASTM 3B.
33000 | 1958 | 53 | 217.3 | 28 | 169.2 | 5229.2 | 2.9 | 1.4 | 42.7 | 1.1 | 0 | 20 | 0.097 | 63 |  | 6 | 0.042 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1958 | 53 | 211.3 | 33 | 156.2 | 5478.9 | 3.3 | 2.4 | 49 | 0.4 | 0 | 20 | 0.094 | 74 |  | 6 | 0.043 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1958 | 53 | 218.8 | 50 | 159.6 | 5214.8 | 6.9 | 2.1 | 50.1 | 0.1 | 0 | 23 | 0.097 | 44 |  | 6 | 0.045 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1958 | 53 | 235.8 | 43 | 176.8 | 5141.8 | 9.4 | 1.8 | 47.8 | 0 | 0 | 27 | 0.098 | 57 |  | 6 | 0.041 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1958 | 53 | 370 | 32 | 212 | 3962 | 118 | 2 | 37 | 1 | 0 | 20 | 0.049 | 60 |  | 5.5 | 0.049 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1958 | 53 | 208 | 35 | 176 | 2895 | 0 | 2 | 29 | 1 | 0 | 55 | 0.088 | 23 |  | 9.4 | 0.028 | Sample possibly contaminated with moisture. Otherwise test results satisfactory.
33000 | 1958 | 53 | 275 | 30 | 207 | 2870 | 39 | 2 | 27 | 0 | 0 | 22 | 0.092 | 29 |  | 7.5 | 0.036 | DGA is assessed as acceptable. | Moisture content of oil is high. Other test results are assessed as acceptable.
33000 | 1958 | 53 | 409 | 41.81 | 331 | 4347 | 42 | 3 | 32 | 1 | 0 | 40 | 0.092 | 41 |  | 7.2 | 0.035 | DGA is assessed as acceptable. | Moisture content of oil is high. Other test results are assessed as acceptable.
33000 | 1958 | 53 | 964.8 | 41.81 | 816.5 | 9360 | 77.6 | 7.8 | 60.1 | 2.8 | 0 | 42 | 0.133 | 14 |  | 5 | 0.039 | DGA is assessed as acceptable. | Moisture content of sample is high. Breakdown voltage of sample is low. Other test results are assessed as acceptable.
33000 | 1958 | 53 | 272 | 30 | 120 | 1543 | 135 | 1 | 16 | 0 | 0 | 18 | 0.043 | 45 |  | 5 | 0.058 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1958 | 53 | 251 | 35 | 214 | 3126 | 0 | 2 | 34 | 1 | 0 | 38 | 0.072 | 33 |  | 8.2 | 0.03 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1958 | 53 | 251 | 34 | 178 | 2541 | 43 | 2 | 27 | 0 | 1 | 17 | 0.079 | 39 |  | 8.7 | 0.031 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1958 | 53 | 374 | 38 | 329 | 4305 | 7 | 0 | 37 | 1 | 0 | 26 | 0.096 | 71 |  | 6.5 | 0.042 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1958 | 53 | 875.9 | 41.81 | 749.8 | 8760 | 57 | 6.3 | 60.5 | 1.9 | 0.4 | 37 | 0.143 | 24 |  | 5 | 0.051 | DGA is assessed as acceptable. | Moisture content of sample is high. Breakdown voltage of sample is low. Other test results are assessed as acceptable.
33000 | 1958 | 53 | 929 | 41.81 | 307 | 4932 | 119 | 110 | 329 | 62 | 2 | 21 | 0.262 | 55 |  | 2 | 0.13 | DGA suggests overheating taking place.
33000 | 1958 | 53 | 580 | 23 | 418 | 4418 | 39 | 16 | 82 | 23 | 2 | 36 | 0.253 | 36 |  | 4 | 0.076 | Test results satisfactory at present.
33000 | 1958 | 53 | 432 | 40 | 377 | 4294 | 32 | 6 | 10 | 5 | 2 | 31 | 0.278 | 47 |  | 4.8 | 0.047 | Test results satisfactory.
33000 | 1958 | 53 | 688 | 23 | 612 | 5704 | 56 | 7 | 8 | 5 | 0 | 38 | 0.33 | 48 |  | 4.8 | 0.05 | Acidity content of oil high. Other test results satisfactory.
33000 | 1958 | 53 | 418 | 41.81 | 376 | 3709 | 35 | 3 | 3 | 1 | 0 | 44 | 0.276 | 43 |  | 5.6 | 0.039 | Acidity and moisture levels of oil high. Other test results satisfactory.
33000 | 1958 | 53 | 12 | 41.81 | 10 | 482 | 0 | 1 | 1 | 0 | 0 | 32 | 0.015 | 58 |  | 40.2 | 0.015 | Test results satisfactory after oil change.
33000 | 1958 | 53 | 234 | 39 | 189 | 4275 | 16 | 4 | 24 | 1 | 0 | 26 | 0.044 | 37 |  | 25.1 | 0.012 | Test results are assessed as acceptable.
33000 | 1958 | 53 | 226.6485 | 64 | 177.6091 | 5125.3298 | 3.4804 | 2.5989 | 40.2882 | 2.5086 | 0.1633 | 28 | 0.055 | 31.5 |  | 19 | 0.017 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1958 | 53 | 249.1 | 45 | 201.1 | 6267.9 | 4.5 | 3.2 | 37.9 | 1.8 | 0.6 | 26 | 0.055 | 25 |  | 18 | 0.015 | DGA is assessed as acceptable. | Breakdown voltage is low. Other test results are relatively stable.
33000 | 1958 | 53 | 267.1 | 47 | 219.9 | 5076.9 | 4.7 | 3.1 | 37.5 | 1.9 | 0 | 26 | 0.061 | 27 |  | 11 | 0.024 | The test results are relatively stable. | Breakdown voltage is low. Other oil quality results are assessed as acceptable.
33000 | 1958 | 53 | 240 | 52 | 199.1 | 5295.2 | 0 | 3.1 | 36.2 | 1.4 | 0.2 | 33 | 0.061 | 34 |  | 15 | 0.022 | DGA is assessed as acceptable. | Moisture content of sample is slightly high. Other test results are assessed as relatively stable.
33000 | 1958 | 53 | 289.5 | 41.81 | 249.1 | 6068.9 | 5.8 | 3 | 30.5 | 1.1 | 0 | 27 | 0.062 | 29 |  | 16 | 0.017 | DGA is assessed as acceptable. | Breakdown voltage is slightly low. Other oil quality results are assessed as acceptable.
33000 | 1958 | 53 | 300.6 | 41.81 | 182.7 | 5362 | 39.6 | 5.6 | 28.1 | 1 | 43.6 | 25 | 0.0509 | 30 |  | 15 | 0.018 | DGA is assessed as acceptable at present. | Oil quality is assessed as acceptable.
33000 | 1958 | 53 | 459.3 | 41.81 | 245.7 | 5806.7 | 47.2 | 10 | 38.9 | 1.6 | 115.9 | 35 | 0.058 | 17 |  | 13 | 0.019 | DGA is assessed as acceptable. Acetylene gas possibly communicating from tapchanger. | Moisture content is high. Breakdown voltage is low. Other oil quality results are assessed as acceptable.
33000 | 1958 | 53 | 284 | 41.81 | 236 | 3817 | 0 | 2 | 46 | 0 | 0 | 18 | 0.128 | 72 |  | 45 | 0.062 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1958 | 53 | 446 | 40 | 348 | 3411 | 55 | 4 | 37 | 2 | 0 | 36 | 0.148 | 54 |  | 2.7 | 0.089 | Moisture content of oil high. Other test results satisfactory.
33000 | 1958 | 53 | 475 | 50 | 428 | 3785 | 12 | 2 | 32 | 1 | 0 | 42 | 0.169 | 50 |  | 3.3 | 0.07 | Moisture content of oil high. Other test results satisfactory.
33000 | 1958 | 53 | 490 | 36 | 343 | 4748 | 118 | 11 | 11 | 7 | 0 | 34 | 0.158 | 49 |  | 9 | 0.032 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1958 | 53 | 364 | 39 | 260 | 3541 | 85 | 8 | 6 | 5 | 0 | 23 | 0.147 | 45 |  | 8 | 0.033 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1958 | 53 | 415 | 46 | 355 | 4178 | 50 | 4 | 4 | 2 | 0 | 34 | 0.174 | 39 |  | 6.4 | 0.04 | DGA is assessed as acceptable. | Moisture content of oil slightly high. Other test results satisfactory.
33000 | 1958 | 53 | 395 | 50 | 334 | 4732 | 49 | 5 | 5 | 2 | 0 | 48 | 0.141 | 36 |  | 7.2 | 0.032 | DGA is assessed as acceptable. | Moisture content is high.
33000 | 1958 | 53 | 418 | 40 | 353 | 5111 | 53 | 5 | 5 | 2 | 0 | 47 | 0.159 | 34 |  | 7.8 | 0.032 | DGA is assessed as acceptable. | Moisture content is high.
33000 | 1958 | 53 | 671 | 50 | 563 | 5853 | 91 | 8 | 6 | 3 | 0 | 46 | 0.168 | 23 |  | 8.2 | 0.027 | DGA is assessed as acceptable. | Moisture content is high. Breakdown voltage is low.
33000 | 1958 | 53 | 546 | 53 | 469 | 6128 | 55 | 8 | 9 | 5 | 0 | 43 | 0.17 | 34 |  | 7.3 | 0.035 | DGA is assessed as acceptable. | Moisture content is high.
33000 | 1958 | 53 | 43.2 | 30 | 31.1 | 2175.4 | 3.3 | 1.3 | 4.6 | 2.9 | 0 | 25 | 0.193 | 56 |  | 7 | 0.033 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1958 | 53 | 90.7 | 50 | 52 | 1464.8 | 23.6 | 3.2 | 8.6 | 3 | 0.3 | 22 | 0.184 | 70 |  | 6 | 0.039 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1957 | 54 | 214 | 45 | 173 | 4118 | 0 | 4 | 35 | 2 | 0 | 33 | 0.086 | 28 |  | 7 | 0.033 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1957 | 54 | 273 | 41.81 | 235 | 2242 | 0 | 3 | 35 | 0 | 0 | 35 | 0.102 | 49 |  | 8 | 0.033 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1957 | 54 | 293 | 40 | 244 | 4138 | 14 | 2 | 32 | 1 | 0 | 34 | 0.11 | 30 |  | 7.2 | 0.031 | Other test results are assessed as acceptable. | Moisture content of oil is slightly high.
33000 | 1957 | 54 | 330.8 | 45 | 271.4 | 5298.6 | 13.6 | 2.1 | 42.6 | 1.1 | 0 | 27 | 0.126 | 39 |  | 5 | 0.047 | Other test results are assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1957 | 54 | 249.1 | 50 | 216.2 | 3343.5 | 4.8 | 2.8 | 24.2 | 1.1 | 0 | 33 | 0.108 | 41 |  | 5 | 0.046 | DGA is assessed as acceptable. | Moisture content is high. Other oil quality results are assessed as acceptable.
33000 | 1957 | 54 | 324.9 | 40 | 277.2 | 4059.7 | 13.9 | 3.3 | 29.3 | 1.2 | 0 | 34 | 0.128 | 54 |  | 5 | 0.046 | DGA is assessed as acceptable. | Moisture content is high. Other oil quality results are assessed as acceptable.
33000 | 1957 | 54 | 246.3 | 41.81 | 206.2 | 3486.1 | 6.4 | 3 | 26.9 | 1.1 | 2.7 | 27 | 0.139 | 40 |  | 6 | 0.046 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1957 | 54 | 282.5 | 41.81 | 247.2 | 4100.1 | 10.7 | 2.8 | 21.2 | 0.4 | 0.2 | 37 | 0.132 | 26 |  | 6 | 0.043 | DGA is assessed as acceptable. | Breakdown voltage is low. Other oil quality results are assessed as acceptable.
33000 | 1957 | 54 | 276.6 | 26 | 243.2 | 3652 | 6.2 | 4.5 | 21.9 | 0.8 | 0 | 29 | 0.131 | 43 |  | 5 | 0.045 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1957 | 54 | 166.5 | 41.81 | 138.8 | 2522 | 8 | 2.2 | 16.9 | 0.6 | 0 | 35 | 0.148 | 29 |  | 6 | 0.039 | DGA is assessed as acceptable. | Breakdown voltage is low. Other oil quality results are assessed as acceptable.
33000 | 1957 | 54 | 209 | 41.81 | 178 | 3084 | 0 | 3 | 26 | 2 | 0 | 22 | 0.088 | 39 |  | 5 | 0.052 | Test results satisfactory.
33000 | 1957 | 54 | 320 | 41.81 | 283 | 3281 | 0 | 5 | 28 | 2 | 2 | 20 | 0.091 | 53 |  | 6.5 | 0.041 | DGA suggests that arcing has taken place but low level of gas dissolved suggests very low energy.
33000 | 1957 | 54 | 345 | 41.81 | 283 | 3037 | 14 | 5 | 40 | 3 | 0 | 13 | 0.068 | 66 |  | 10 | 0.039 | DGA is assessed as acceptable.
33000 | 1957 | 54 | 298 | 41.81 | 238 | 2751 | 20 | 4 | 33 | 3 | 0 | 17 | 0.051 | 55 |  | 17.8 | 0.017 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1957 | 54 | 556 | 41.81 | 473 | 4032 | 29 | 7 | 44 | 3 | 0 | 21 | 0.077 | 64 |  | 11.2 | 0.023 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1957 | 54 | 455 | 41.81 | 387 | 3912 | 12 | 6 | 46 | 4 | 0 | 20 | 0.078 | 35 |  | 15.4 | 0.021 | Dielectric strength of oil slightly low. Other test results satisfactory.
33000 | 1957 | 54 | 220 | 41.81 | 159 | 1923 | 33 | 3 | 21 | 2 | 2 | 18 | 0.065 | 65 |  | 13.8 | 0.017 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1957 | 54 | 520 | 24 | 454 | 4283 | 0 | 8 | 51 | 6 | 1 | 15 | 0.058 | 44 |  | 20 | 0.02 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1957 | 54 | 460 | 35 | 391 | 3265 | 11 | 6 | 44 | 6 | 2 | 17 | 0.062 | 47 |  | 15.3 | 0.02 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1957 | 54 | 428 | 30 | 372 | 2673 | 17 | 6 | 30 | 3 | 0 | 18 | 0.171 | 55 |  | 14.5 | 0.022 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1957 | 54 | 551 | 33 | 472 | 3033 | 42 | 6 | 28 | 3 | 0 | 17 | 0.068 | 59 |  | 16.4 | 0.025 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1957 | 54 | 673 | 41.81 | 589 | 4420 | 35 | 8 | 36 | 4 | 1 | 28 | 0.07 | 47 |  | 12.2 | 0.02 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1957 | 54 | 796 | 41.81 | 704 | 8070 | 23 | 10 | 53 | 6 | 0 | 24 | 0.099 | 47 |  | 11 | 0.027 | Test results are assessed as acceptable for the age of the transformer. | Oil quality is assessed as acceptable.
33000 | 1957 | 54 | 971.2 | 41.81 | 632.2 | 7253.3 | 127.3 | 20.9 | 71 | 8.9 | 110.9 | 20 | 0.128 | 65 |  | 7 | 0.036 | Acetylene level is inconsistent with history of this transformer. Other dissolved gas levels are assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1957 | 54 | 673.6 | 41.81 | 457.3 | 7216.8 | 49.3 | 16.4 | 60 | 7.7 | 82.9 | 19 | 0.117 | 54 |  | 9 | 0.031 | Dissolved gas levels are relatively stable. | Oil quality is assessed as acceptable.
33000 | 1957 | 54 | 475.2 | 41.81 | 390.8 | 4136.6 | 12.7 | 7.5 | 38.6 | 5.6 | 20 | 16 | 0.111 | 67 |  | 8 | 0.031 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1957 | 54 | 396.3 | 24 | 340.9 | 4023.3 | 11.2 | 5.6 | 30.9 | 4.2 | 3.5 | 15 | 0.114 | 62 |  | 8 | 0.038 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1957 | 54 | 475 | 22 | 396 | 4162.3 | 22 | 6.8 | 32.7 | 5.1 | 12.4 | 15 | 0.124 | 67 |  | 8 | 0.036 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable. Corrosive IEC. Non-corrosive ASTM 2C.
33000 | 1957 | 54 | 451.5 | 20 | 388.1 | 4117.1 | 15.2 | 6.8 | 30.5 | 6.2 | 4.7 | 17 | 0.14 | 75 |  | 8 | 0.036 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1957 | 54 | 431 | 30 | 375 | 4348.4 | 14.4 | 6.1 | 29.3 | 4.9 | 1.3 | 15 | 0.136 | 68 |  | 6 | 0.039 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1957 | 54 | 530 | 41.81 | 481 | 7071 | 15 | 3 | 30 | 1 | 0 | 21 | 0.15 | 60 |  | 4.5 | 0.0596 | Test results satisfactory.
33000 | 1957 | 54 | 516 | 41.81 | 477 | 6411 | 7 | 3 | 28 | 1 | 0 | 19 | 0.147 | 67 |  | 3.5 | 0.0659 | Test results satisfactory.
33000 | 1957 | 54 | 17 | 41.81 | 9 | 1336 | 0 | 1 | 7 | 0 | 0 | 14 | 0.148 | 70 |  | 3.1 | 0.073 | Reduced DGA level as transformer out of service at Northgate.
33000 | 1957 | 54 | 24 | 41.81 | 20 | 679 | 0 | 1 | 3 | 0 | 0 | 36 | 0.161 | 67 |  | 3.4 | 0.081 | Moisture content high for transformer in storage. Careful resampling required to check moisture content.
33000 | 1957 | 54 | 15 | 41.81 | 8 | 593 | 0 | 2 | 2 | 3 | 0 | 19 | 0.146 | 50 |  | 3 | 0.078 | Test results are assessed as acceptable.
33000 | 1957 | 54 | 240 | 52 | 174 | 3062 | 34 | 3 | 28 | 1 | 0 | 9 | 0.018 | 65 |  | 9 | 0.065 | DGA is assessed as acceptable | Oil quality is assessed as acceptable.
33000 | 1957 | 54 | 288 | 45 | 238 | 4156 | 14 | 4 | 30 | 2 | 0 | 56 | 0.043 | 20 |  | 18.2 | 0.027 | DGA is assessed as acceptable. | Water content of sample high. Suspect contamination of sample. Breakdown voltage is low.
33000 | 1957 | 54 | 256 | 50 | 191 | 3451 | 39 | 2 | 23 | 1 | 0 | 22 | 0.052 | 57 |  | 14.1 | 0.028 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1957 | 54 | 1610 | 41.81 | 512 | 7909 | 1029 | 7 | 60 | 2 | 0 | 24 | 0.049 | 58 |  | 13.3 | 0.02 | Carbon oxide gas levels increasing.
33000 | 1957 | 54 | 687.2 | 50 | 405.3 | 3977.7 | 213.8 | 5.4 | 59.6 | 3.1 | 0 | 25 | 0.061 | 29 |  | 8 | 0.035 | DGA is assessed as acceptable | Breakdown voltage of sample is low. Other test results are assessed as acceptable.
33000 | 1957 | 54 | 557.6 | 35 | 466.9 | 7457.1 | 28.4 | 4.6 | 54.7 | 3 | 0 | 24 | 0.066 | 47 |  | 9 | 0.028 | The test results are consistent with age of transformer.
33000 | 1957 | 54 | 541.1 | 35 | 466.6 | 7466.8 | 11.2 | 5.3 | 54.5 | 3.5 | 0 | 24 | 0.065 | 56 |  | 9 | 0.027 | The test results are consistent with main tank sample and are assessed as acceptable.
33000 | 1957 | 54 | 302.8 | 36 | 241.4 | 4469.5 | 24.7 | 3.1 | 31.6 | 2 | 0 | 15 | 0.054 | 34 |  | 8 | 0.035 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1957 | 54 | 285.9 | 31 | 231.7 | 3743.9 | 27.2 | 2.7 | 23.3 | 1 | 0 | 19 | 0.06 | 39 |  | 7 | 0.03258 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1957 | 54 | 215.6 | 25 | 185.9 | 2937.9 | 7.8 | 2.1 | 18.9 | 0.9 | 0 | 17 | 0.074 | 72 |  | 7 | 0.031 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1957 | 54 | 275.9 | 30 | 238.8 | 3298.7 | 14.6 | 2.1 | 20 | 0.4 | 0 | 19 | 0.075 | 82 |  | 7 | 0.045 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable. Corrosive IEC. Non-corrosive ASTM 3B.
33000 | 1957 | 54 | 377.8 | 38 | 253.2 | 3672.4 | 102.2 | 2.1 | 19.7 | 0.6 | 0 | 21 | 0.075 | 80 |  | 6 | 0.039 | Hydrogen level is increased. Other dissolved gas levels are assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1957 | 54 | 482 | 32 | 225.1 | 5670.1 | 223.3 | 9.1 | 24.1 | 0.4 | 0 | 36 | 0.078 | 33 |  | 5 | 0.048 | DGA is assessed as acceptable. | Breakdown voltage is low. Other oil quality results are assessed as acceptable.
33000 | 1957 | 54 | 1131 | 32 | 820 | 7033 | 201 | 47 | 23 | 40 | 0 | 56 | 0.168 | 21 |  | 1.5 | 0.164 | Moisture high;low breakdown suggests slight overheating. Recommend resample to confirm results.
33000 | 1957 | 54 | 1131 | 31 | 820 | 7033 | 201 | 47 | 23 | 40 | 0 | 63 | 0.332 | 34 |  | 1.6 | 0.14 | Oil condition generally poor and moisture high. Recommend oil treatment.
33000 | 1957 | 54 | 902 | 48 | 687 | 5605 | 147 | 24 | 16 | 26 | 2 | 50 | 0.325 | 19 |  | 2 | 0.136 | Oil condition poor. Oil treatment or replacement recommended.
33000 | 1957 | 54 | 443 | 40 | 328 | 2952 | 78 | 12 | 10 | 15 | 0 | 75 | 0.32 | 22 |  | 2.3 | 0.103 | Oil condition poor. Oil treatment or replacement recommended.
33000 | 1957 | 54 | 479 | 52 | 392 | 6101 | 48 | 13 | 12 | 14 | 0 | 38 | 0.37 | 53 |  | 1.9 | 0.125 | Oil acidity high; oil condition poor. DGA satisfactory.
33000 | 1957 | 54 | 394 | 58 | 343 | 5739 | 25 | 8 | 10 | 7 | 1 | 39 | 0.309 | 41 |  | 2 | 0.13 | Oil sampled before oil change.
33000 | 1957 | 54 | 226 | 54 | 140 | 2218 | 68 | 2 | 15 | 1 | 0 | 44 | 0.041 | 51 |  | 20.9 | 0.021 | Moisture content remains high after oil change. Other test results are satisfactory.
33000 | 1957 | 54 | 193 | 48 | 155 | 3303 | 14 | 3 | 20 | 1 | 0 | 30 | 0.048 | 56 |  | 20.8 | 0.022 | Moisture content of oil slightly high. Other test results satisfactory.
33000 | 1957 | 54 | 332 | 41.81 | 273 | 7833 | 16 | 4 | 38 | 1 | 0 | 39 | 0.056 | 26 |  | 17.2 | 0.019 | Moisture content of oil is high. Dielectric strength slightly low. Carbon oxide gas levels increasing. RECOMMEND RESAMPLE IN 6 MONTHS TO MONITOR TRENDS.
33000 | 1957 | 54 | 542.7 | 56 | 449.6 | 8502.6 | 33 | 7.4 | 50.8 | 1.9 | 0 | 47 | 0.071 | 19 |  | 11 | 0.025 | Dissolved gas analysis is assessed as acceptable. Moisture content of oil is high. Breakdown voltage of oil is low. 2-furfural level is high suggesting accelerated rate of insulation degradation. RECOMMEND RESAMPLE IN 1 YEAR TO MONITOR CONDITION.
33000 | 1957 | 54 | 1200 | 53 | 1065 | 6857 | 78 | 36 | 15 | 6 | 0 | 50 | 0.326 | 59 |  | 4.5 | 0.0801 | DGA is assessed as acceptable | Acidity level and moisture level notable otherwise test results satisfactory.
33000 | 1957 | 54 | 883 | 42 | 780 | 5172 | 60 | 25 | 13 | 5 | 0 | 30 | 0.326 | 68 |  | 4 | 0.0793 | DGA is assessed as acceptable
33000 | 1957 | 54 | 510 | 25 | 448 | 3237 | 32 | 17 | 8 | 5 | 0 | 24 | 0.333 | 41 |  | 2 | 0.104 | DGA is assessed as acceptable
33000 | 1957 | 54 | 526 | 50 | 464 | 4097 | 49 | 4 | 7 | 2 | 0 | 48 | 0.335 | 34 |  | 2.5 | 0.089 | DGA is assessed as acceptable | Moisture content of oil high; acidity level high. Other test results satisfactory.
33000 | 1957 | 54 | 701 | 50 | 629 | 4864 | 57 | 5 | 8 | 2 | 0 | 49 | 0.345 | 43 |  | 2.4 | 0.089 | DGA is assessed as acceptable | Acidity and moisture levels of oil high. Other test results satisfactory.
33000 | 1957 | 54 | 42 | 64 | 40 | 575 | 0 | 1 | 1 | 0 | 0 | 28 | 0.023 | 33 |  | 30.1 | 0.017 | DGA is assessed as acceptable
33000 | 1957 | 54 | 441 | 47 | 383 | 6379 | 24 | 6 | 27 | 1 | 0 | 33 | 0.041 | 37 |  | 16 | 0.018 | DGA is assessed as acceptable | Moisture content of oil is above defect level. Other test results are assessed as acceptable.
33000 | 1957 | 54 | 431.4 | 58 | 366.6 | 8946.4 | 13.1 | 6.8 | 42.6 | 2.3 | 0 | 37 | 0.063 | 21 |  | 13 | 0.024 | DGA is assessed as acceptable | Moisture content of sample is high. Breakdown voltage of sample is low. Other test results are assessed as acceptable.
33000 | 1957 | 54 | 423.2 | 44 | 366.6 | 6707.1 | 14.9 | 6.8 | 33.1 | 1.8 | 0 | 35 | 0.066 | 15 |  | 9 | 0.03 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1957 | 54 | 781 | 34 | 563 | 6107 | 171 | 21 | 14 | 12 | 0 | 39 | 0.198 | 66 |  | 7 | 0.057 | H2 Level slightly high. Otherwise D.G.A. satisfactory. | Oil quality is assessed as acceptable.
33000 | 1957 | 54 | 539 | 41.81 | 387 | 4731 | 121 | 14 | 8 | 8 | 1 | 17 | 0.184 | 48 |  | 10 | 0.029 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1957 | 54 | 774 | 41.81 | 590 | 6299 | 161 | 11 | 7 | 5 | 0 | 48 | 0.216 | 61 |  | 6.7 | 0.041 | DGA is assessed as acceptable. | Moisture content of oil slightly high. Other test results satisfactory.
33000 | 1957 | 54 | 590 | 41.81 | 483 | 5609 | 85 | 10 | 6 | 5 | 1 | 49 | 0.216 | 50 |  | 7.4 | 0.036 | Previous comments still apply.
33000 | 1957 | 54 | 531 | 41.81 | 445 | 2666 | 69 | 9 | 4 | 3 | 1 | 48 | 0.212 | 57 |  | 7.5 | 0.036 | DGA is assessed as acceptable. | Moisture content of oil high. Other test results satisfactory.
33000 | 1957 | 54 | 526 | 41.81 | 434 | 4957 | 72 | 9 | 8 | 3 | 0 | 49 | 0.197 | 29 |  | 7.5 | 0.03 | DGA is assessed as acceptable. | Moisture content high; dielectric strength low; other test results satisfactory.
33000 | 1957 | 54 | 648 | 41.81 | 529 | 5980 | 91 | 13 | 9 | 6 | 0 | 38 | 0.197 | 51 |  | 7.5 | 0.033 | DGA is assessed as acceptable. | Moisture content of oil is high. Other test results are assessed as acceptable.
33000 | 1957 | 54 | 1067.9 | 50 | 813 | 8387.8 | 201.7 | 26.9 | 14.7 | 11.6 | 0 | 56 | 0.257 | 33 |  | 8 | 0.032 | DGA is assessed as acceptable. | Oil and insulation are deteriorated.
33000 | 1957 | 54 | 524.4 | 20 | 403.2 | 7468.2 | 85.8 | 12.8 | 10.6 | 9.9 | 2.1 | 37 | 0.262 | 34 |  | 5 | 0.047 | DGA is assessed as acceptable. | Acidity level is high. Moisture content is high. Other oil quality results are assessed as acceptable.
33000 | 1957 | 54 | 185 | 25 | 148 | 2084 | 16 | 5 | 15 | 1 | 0 | 7 | 0.014 | 64 |  | 30 | 0.046 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1957 | 54 | 410 | 35 | 379 | 3969 | 4 | 3 | 21 | 3 | 0 | 10 | 0.039 | 54 |  | 28.1 | 0.019 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1957 | 54 | 386 | 36 | 311 | 5198 | 37 | 6 | 30 | 2 | 0 | 18 | 0.034 | 69 |  | 25.4 | 0.018 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1957 | 54 | 302 | 43 | 256 | 5128 | 4 | 5 | 35 | 2 | 0 | 15 | 0.026 | 66 |  | 23.5 | 0.019 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1957 | 54 | 457.9 | 25 | 359.6 | 6874.2 | 16 | 11.4 | 64.8 | 5.8 | 0.3 | 24 | 0.037 | 37 |  | 16 | 0.027 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1957 | 54 | 346 | 38 | 282 | 5946 | 8 | 8 | 44 | 4 | 0 | 15 | 0.032 | 72 |  | 14 | 0.025 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1957 | 54 | 373.3 | 47 | 308.1 | 5953.2 | 9.5 | 8.3 | 43.2 | 4.2 | 0 | 20 | 0.035 | 33 |  | 16 | 0.025 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1957 | 54 | 390 | 40 | 321 | 1662 | 6 | 9 | 50 | 4 | 0 | 15 | 0.045 | 46 |  | 13 | 0.028 | DGA is consistant with previous main tank sample and is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1957 | 54 | 429.7 | 49 | 367.9 | 6219.9 | 7.3 | 5.8 | 46.4 | 2.3 | 0 | 23 | 0.039 | 45 |  | 10 | 0.035 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1957 | 54 | 396.4 | 46 | 335.7 | 5731.5 | 8.3 | 5.6 | 43.4 | 3.4 | 0 | 24 | 0.051 | 43 |  | 12 | 0.027 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1957 | 54 | 759 | 41.81 | 681 | 7648 | 31 | 19 | 19 | 9 | 0 | 47 | 0.297 | 49 |  | 4.5 | 0.064 | Test results satisfactory though acidity and moisture level notable. Additional sample 26/2/88 confirm high moisture.
33000 | 1957 | 54 | 700 | 41.81 | 630 | 7793 | 23 | 18 | 20 | 9 | 0 | 30 | 0.284 | 62 |  | 5 | 0.059 | DGA satisfactory.
33000 | 1957 | 54 | 507 | 41.81 | 474 | 6539 | 0 | 13 | 13 | 7 | 0 | 27 | 0.416 | 58 |  | 5.5 | 0.048 | Sharp increase in acidity level noted. RECOMMEND RESAMPLE IN 6 MONTHS.
33000 | 1957 | 54 | 370 | 41.81 | 335 | 5194 | 14 | 8 | 8 | 5 | 0 | 33 | 0.294 | 26 |  | 4.4 | 0.056 | DGA satisfactory.
33000 | 1957 | 54 | 595 | 41.81 | 561 | 7710 | 0 | 13 | 13 | 8 | 0 | 35 | 0.352 | 47 |  | 4.1 | 0.062 | DGA satisfactory.
33000 | 1957 | 54 | 422 | 41.81 | 386 | 5843 | 8 | 11 | 11 | 6 | 0 | 38 | 0.326 | 49 |  | 4.5 | 0.058 | Moisture content and acidity levels are high. DGA satisfactory. Transformer has history of high acidity levels.
33000 | 1957 | 54 | 795 | 41.81 | 730 | 8362 | 30 | 15 | 13 | 7 | 0 | 50 | 0.391 | 41 |  | 5.2 | 0.045 | Moisture and acidity levels are high. 2-furfural is above 1ppm. Other test results are assessed as acceptable.
33000 | 1957 | 54 | 558.5 | 42 | 489.9 | 12714.9 | 16.4 | 11.1 | 22.2 | 18.8 | 0.1 | 26 | 0.389 | 65 |  | 3 | 0.078 | Acidity level of sample is high. Carbon dioxide level is high. 2-furfural level is high suggesting accelerated rate of insulation degradation. RECOMMEND RESAMPLE IN 1 YEAR TO MONITOR CONDITION.
33000 | 1956 | 55 | 669 | 34 | 533 | 5727 | 91 | 10 | 17 | 8 | 10 | 36 | 0.392 | 65 |  | 6 | 0.049 | Acidity content of oil high. Other test results satisfactory.
33000 | 1956 | 55 | 514 | 40 | 424 | 4901 | 57 | 9 | 8 | 4 | 12 | 36 | 0.33 | 39 |  | 6.2 | 0.035 | Acidity content of oil high. Other test results satisfactory.
33000 | 1956 | 55 | 672 | 41.81 | 528 | 7414 | 49 | 13 | 24 | 6 | 52 | 34 | 0.382 | 62 |  | 4.6 | 0.046 | Acidity level quite high. Moisture level high; other results satisfactory. Acetylene gas possibly from tapchanger.
33000 | 1956 | 55 | 148 | 41.81 | 113 | 1562 | 11 | 3 | 9 | 1 | 11 | 24 | 0.043 | 42 |  | 18.9 | 0.016 | Test results satisfactory. Has this TX had an oil change ?
33000 | 1956 | 55 | 259 | 41.81 | 192 | 6231 | 20 | 5 | 24 | 3 | 15 | 24 | 0.059 | 68 |  | 26.3 | 0.012 | Test results are assessed as acceptable.
33000 | 1956 | 55 | 292.5 | 41.81 | 234.7 | 9338.3 | 14.3 | 5.9 | 23.1 | 3.2 | 11.3 | 30 | 0.068 | 36 |  | 17 | 0.017 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1956 | 55 | 216.9 | 41.81 | 186.2 | 5584.7 | 6.7 | 4.1 | 15 | 2.2 | 2.7 | 28 | 0.087 | 28 |  | 14 | 0.017 | DGA is assessed as acceptable. | Breakdown voltage is low. Other oil quality results are assessed as acceptable.
33000 | 1956 | 55 | 303.2 | 41.81 | 255.8 | 6802 | 5.9 | 6 | 20.2 | 2.1 | 13.2 | 31 | 0.078 | 55 |  | 17 | 0.016 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable. Non-corrosive IEC. Non-corrosive ASTM 3A.
33000 | 1956 | 55 | 156.4 | 41.81 | 133.4 | 4050.5 | 3 | 3.2 | 11.6 | 1.7 | 3.5 | 23 | 0.087 | 53 |  | 15 | 0.018 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1956 | 55 | 391 | 30 | 309 | 3864 | 25 | 3 | 42 | 1 | 11 | 28 | 0.186 | 45 |  | 8 | 0.035 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1956 | 55 | 284 | 40 | 243 | 2884 | 0 | 3 | 30 | 1 | 7 | 29 | 0.173 | 49 |  | 5.9 | 0.041 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1956 | 55 | 672 | 41.81 | 384 | 5821 | 140 | 6 | 69 | 3 | 70 | 27 | 0.185 | 62 |  | 6.1 | 0.044 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1956 | 55 | 410 | 41.81 | 315 | 4789 | 28 | 4 | 43 | 3 | 17 | 27 | 0.193 | 69 |  | 5.5 | 0.045 | 2-Furfural level is above 1PPM. Other test results are assessed as acceptable.
33000 | 1956 | 55 | 422.9 | 41.81 | 340.6 | 7046.4 | 11.6 | 4.5 | 46.2 | 2.7 | 17.3 | 29 | 0.235 | 39 |  | 4 | 0.057 | DGA is assessed as acceptable. | Acidity level is high. Other oil quality results are assessed as acceptable.
33000 | 1956 | 55 | 417 | 41.81 | 365.5 | 5399.3 | 9.4 | 4 | 32.4 | 1.9 | 3.8 | 23 | 0.214 | 32 |  | 4 | 0.0487 | DGA is assessed as acceptable. | Acidity level is high but stable. Breakdown voltage is slightly low. Other oil quality results are assessed as acceptable.
33000 | 1956 | 55 | 467.6 | 28 | 365.3 | 5056.3 | 61.3 | 4.1 | 28.2 | 1.9 | 6.8 | 34 | 0.247 | 35 |  | 4 | 0.055 | DGA is assessed as acceptable. | Acidity level is high. Breakdown voltage is low. DDF and Resistivity are assessed as acceptable.
33000 | 1956 | 55 | 393.4 | 29 | 324.8 | 5185.2 | 25.3 | 3.6 | 29.2 | 2.9 | 7.6 | 38 | 0.29 | 29 |  | 4 | 0.055 | DGA is assessed as acceptable. | Breakdown voltage is low. Acidity level is high. DDF and Resistivity are assessed as acceptable. Corrosive IEC. Non-corrosive ASTM 3B.
33000 | 1956 | 55 | 245 | 34 | 221 | 1421 | 0 | 1 | 22 | 1 | 0 | 15 | 0.022 | 52 |  | 150 | 0.029 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1956 | 55 | 275 | 46 | 245 | 2028 | 0 | 2 | 28 | 0 | 0 | 17 | 0.04 | 54 |  | 13.5 | 0.03 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1956 | 55 | 418 | 39 | 336 | 2094 | 55 | 2 | 25 | 0 | 0 | 21 | 0.036 | 70 |  | 16 | 0.027 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1956 | 55 | 652 | 42 | 580 | 3512 | 31 | 5 | 35 | 1 | 0 | 17 | 0.07 | 60 |  | 11.1 | 0.023 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1956 | 55 | 859 | 72 | 788 | 4780 | 26 | 6 | 37 | 2 | 0 | 18 | 0.064 | 41 |  | 10 | 0.03 | DGA is assessed as acceptable | Oil quality is assessed as acceptable.
33000 | 1956 | 55 | 599.3 | 36 | 538.4 | 5537.1 | 19.3 | 3.7 | 36.1 | 1.6 | 0.2 | 16 | 0.069 | 46 |  | 9 | 0.028 | DGA is assessed as acceptable | Oil quality is assessed as acceptable.
33000 | 1956 | 55 | 806 | 34 | 740.4 | 6557.3 | 28.2 | 4.5 | 31.9 | 0.9 | 0.1 | 28 | 0.069 | 74 |  | 8 | 0.032 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1956 | 55 | 134 | 22 | 122 | 1185 | 0 | 0 | 12 | 0 | 0 | 18 | 0.216 | 63 |  | 6 | 0.036 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1956 | 55 | 396 | 42 | 342 | 4584 | 14 | 4 | 34 | 2 | 0 | 17 | 0.207 | 61 |  | 5.3 | 0.045 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1956 | 55 | 596 | 40 | 546 | 7244 | 0 | 4 | 45 | 1 | 0 | 28 | 0.207 | 50 |  | 4.8 | 0.046 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1956 | 55 | 627 | 50 | 534 | 7988 | 37 | 4 | 50 | 1 | 1 | 21 | 0.21 | 67 |  | 5.5 | 0.049 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1956 | 55 | 627 | 52 | 557 | 7194 | 20 | 4 | 44 | 1 | 1 | 31 | 0.216 | 72 |  | 4.9 | 0.05 | DGA is assessed as acceptable. Acetylene gas possibly from tapchanger. | Moisture content of oil is slightly high. Other test results are assessed as acceptable.
33000 | 1956 | 55 | 756.1 | 49 | 636.7 | 8673.8 | 25.1 | 8.2 | 78.8 | 7.2 | 0.1 | 28 | 0.225 | 38 |  | 4 | 0.061 | DGA is assessed as acceptable. | Acidity level of oil is high. Other test results are assessed as acceptable.
33000 | 1956 | 55 | 772.2 | 40 | 657.4 | 10275.4 | 30.7 | 6.9 | 71.7 | 5.4 | 0.1 | 21 | 0.27 | 46 |  | 3 | 0.068 | 2-furfural, acidity and carbon dioxide levels are trending upwards, suggesting accelerated rate of insulation degradation. | Oil quality is assessed as acceptable.
33000 | 1956 | 55 | 550.7 | 29 | 518.1 | 9221.4 | 23.5 | 7.8 | 0 | 1.3 | 0 | 27 | 0.237 | 67 |  | 3.7 | 0.067 | DGA is assessed as acceptable. | Acidity level is high but stable. Other oil quality results are assessed as acceptable.
33000 | 1956 | 55 | 519 | 44 | 451 | 6679 | 12 | 4 | 51 | 1 | 0 | 18 | 0.057 | 64 |  | 13 | 0.026 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1956 | 55 | 453 | 30 | 410 | 5224 | 0 | 3 | 39 | 1 | 0 | 16 | 0.053 | 46 |  | 9 | 0.03 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1956 | 55 | 267 | 35 | 213 | 3533 | 10 | 4 | 32 | 1 | 7 | 21 | 0.052 | 29 |  | 16.1 | 0.021 | DGA is assessed as acceptable.
33000 | 1956 | 55 | 611 | 43 | 553 | 7422 | 0 | 5 | 52 | 1 | 0 | 16 | 0.051 | 30 |  | 16.3 | 0.02 | DGA is assessed as acceptable.
33000 | 1956 | 55 | 427 | 40 | 377 | 6832 | 0 | 4 | 45 | 1 | 0 | 21 | 0.044 | 49 |  | 13.3 | 0.025 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1956 | 55 | 485 | 50 | 432 | 7032 | 0 | 5 | 47 | 1 | 0 | 16 | 0.049 | 50 |  | 13.4 | 0.025 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1956 | 55 | 538 | 41.81 | 468 | 7402 | 8 | 6 | 54 | 2 | 0 | 27 | 0.057 | 53 |  | 12.1 | 0.025 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1956 | 55 | 606.5 | 50 | 496.3 | 7842.8 | 10.8 | 6.4 | 89.3 | 3.5 | 0.2 | 13 | 0.08 | 41 |  | 6 | 0.064 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1956 | 55 | 613.4 | 31 | 536.4 | 7773.6 | 11.3 | 5.1 | 58.8 | 1.8 | 0 | 14 | 0.068 | 59 |  | 6.6 | 0.045 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1956 | 55 | 810 | 27 | 678 | 9272 | 74 | 6 | 50 | 2 | 0 | 26 | 0.136 | 50 |  | 6 | 0.041 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1956 | 55 | 853 | 41.81 | 740 | 9332 | 56 | 6 | 49 | 2 | 0 | 20 | 0.133 | 64 |  | 6.7 | 0.036 | No increase in gas levels in main tank. Oil sample taken after suspect TX fault. To be returned to Ngate for examination.
33000 | 1956 | 55 | 867 | 37 | 769 | 10884 | 40 | 22 | 24 | 12 | 0 | 53 | 0.315 | 50 |  | 6 | 0.048 | Moisture and acidity levels notable; otherwise satisfactory.Moisture tests 26/2/88 confirm high moisture level.
33000 | 1956 | 55 | 379 | 21 | 335 | 5709 | 14 | 12 | 11 | 6 | 1 | 26 | 0.312 | 46.7 |  | 6 | 0.044 | DGA satisfactory.
33000 | 1956 | 55 | 532 | 44 | 494 | 7986 | 0 | 13 | 16 | 9 | 0 | 31 | 0.305 | 51 |  | 4 | 0.0595 | DGA satisfactory.
33000 | 1956 | 55 | 448 | 44 | 414 | 7456 | 0 | 12 | 13 | 8 | 1 | 34 | 0.329 | 39 |  | 5.3 | 0.048 | Acidity content of oil high. Other test results satisfactory.
33000 | 1956 | 55 | 610 | 46 | 511 | 5937 | 48 | 13 | 12 | 7 | 19 | 35 | 0.385 | 61 |  | 5.1 | 0.046 | Acidity content of oil high. Other test results satisfactory.
33000 | 1956 | 55 | 625 | 61 | 575 | 7115 | 15 | 15 | 10 | 9 | 1 | 46 | 0.371 | 43 |  | 5.7 | 0.046 | Acidity and moisture levels of oil high. Other test results satisfactory.
33000 | 1956 | 55 | 335 | 41.81 | 288 | 4282 | 23 | 7 | 12 | 5 | 0 | 25 | 0.38 | 69 |  | 4.1 | 0.052 | Acidity level high; other test results satisfactory.
33000 | 1956 | 55 | 247 | 25 | 211 | 3063 | 18 | 5 | 9 | 4 | 0 | 24 | 0.351 | 64 |  | 3.9 | 0.07 | Acidity level of oil is high. Other test results are assessed as acceptable.
33000 | 1956 | 55 | 205.2 | 22 | 167.5 | 3093.2 | 22.8 | 2.7 | 7.3 | 4.1 | 0.8 | 19 | 0.333 | 75 |  | 4 | 0.066 | Acidity level of sample is high. 2-furfural level is high suggesting accelerated rate of insulation degradation. RECOMMEND RESAMPLE IN 1 MONTH TO MONITOR CONDITION.
33000 | 1956 | 55 | 773 | 41.81 | 689 | 8434 | 35 | 19 | 19 | 9 | 2 | 54 | 0.319 | 40 |  | 5 | 0.055 | Moisture and acidity content notable; otherwise results satisfactory. Samples 26/2/88 confirm high moisture.
33000 | 1956 | 55 | 532 | 41.81 | 472 | 7050 | 21 | 15 | 16 | 7 | 1 | 26 | 0.307 | 42 |  | 5 | 0.0469 | DGA satisfactory.
33000 | 1956 | 55 | 470 | 41.81 | 442 | 5648 | 0 | 11 | 10 | 6 | 1 | 28 | 0.304 | 51 |  | 7 | 0.0413 | DGA satisfactory.
33000 | 1956 | 55 | 486 | 41.81 | 445 | 7824 | 0 | 15 | 16 | 9 | 1 | 31 | 0.321 | 34 |  | 4.6 | 0.054 | DGA satisfactory.
33000 | 1956 | 55 | 710 | 41.81 | 650 | 8713 | 11 | 18 | 16 | 13 | 2 | 47 | 0.323 | 56 |  | 4.8 | 0.053 | DGA satisfactory.
33000 | 1956 | 55 | 439 | 41.81 | 396 | 4911 | 9 | 11 | 18 | 5 | 0 | 49 | 0.315 | 53 |  | 4.1 | 0.06 | Moisture content very high; acidity level high. DGA satisfactory.
33000 | 1956 | 55 | 791 | 41.81 | 717 | 8333 | 28 | 17 | 23 | 6 | 0 | 54 | 0.365 | 25 |  | 3.3 | 0.076 | Moisture and acidity levels are high. 2-furfural level is above 1ppm. Other test results are assessed as acceptable.
33000 | 1956 | 55 | 435.3 | 37 | 379.4 | 8235.2 | 7.9 | 9.9 | 25 | 13 | 0.1 | 28 | 0.347 | 59 |  | 3 | 0.083 | Acidity level of sample is high. 2-furfural level is high suggesting accelerated rate of insulation degradation. RECOMMEND RESAMPLE IN 1 YEAR TO MONITOR CONDITION.
33000 | 1955 | 56 | 1907 | 19 | 1335 | 16799 | 507 | 45 | 9 | 11 | 0 | 55 | 0.312 | 23 |  | 7 | 0.032 | CO2 level very high. | Acidity and moisture level quite high.
33000 | 1955 | 56 | 410 | 41.81 | 376 | 5339 | 27 | 5 | 1 | 1 | 0 | 30 | 0.343 | 56 |  | 4 | 0.056 | DGA is assessed as acceptable. | Acidity content of oil quite high. Moisture content slightly high. Other test results satisfactory.
33000 | 1955 | 56 | 12 | 41.81 | 11 | 448 | 0 | 1 | 0 | 0 | 0 | 21 | 0.022 | 55 |  | 41.2 | 0.014 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1955 | 56 | 286 | 41.81 | 262 | 5409 | 12 | 4 | 7 | 1 | 0 | 33 | 0.044 | 35 |  | 25.5 | 0.013 | DGA is assessed as acceptable. | Moisture content of oil is slightly high. Other test results are assessed as acceptable.
33000 | 1955 | 56 | 385.2 | 41.81 | 350.8 | 6010.9 | 13.5 | 6 | 12.5 | 2.4 | 0 | 36 | 0.053 | 19 |  | 14 | 0.021 | DGA is assessed as acceptable. | Breakdown voltage of sample is low. Moisture content of sample is high. Other test results are assessed as acceptable.
33000 | 1955 | 56 | 374.6 | 41.81 | 345.3 | 8019.1 | 12.1 | 5 | 10.5 | 1.7 | 0 | 29 | 0.058 | 18 |  | 15 | 0.018 | DGA is assessed as acceptable. | Breakdown voltage is low. Other oil quality results are assessed as acceptable.
33000 | 1955 | 56 | 378.4 | 41.81 | 341.7 | 7670.4 | 18 | 5.4 | 11 | 2 | 0.3 | 34 | 0.053 | 37 |  | 10 | 0.024 | DGA is assessed as acceptable. | Moisture content is slightly high. Other oil quality results are assessed as acceptable.
33000 | 1955 | 56 | 290.5 | 41.81 | 267.9 | 6376.9 | 10.2 | 4.5 | 6.6 | 1.3 | 0 | 38 | 0.059 | 22 |  | 14 | 0.017 | DGA is assessed as acceptable. | Moisture content is high. Breakdown voltage is low. Other oil quality results are assessed as acceptable.
33000 | 1955 | 56 | 297.1 | 41.81 | 237.7 | 6353.6 | 45.6 | 4.3 | 7.4 | 2.1 | 0 | 28 | 0.056 | 28 |  | 12 | 0.024 | DGA is assessed as acceptable. | Breakdown voltage is low. Other oil quality results are assessed as acceptable. Corrosive IEC. Non-corrosive ASTM 3B.
33000 | 1955 | 56 | 312.9 | 28 | 286.7 | 6557.6 | 10.9 | 4.5 | 9.3 | 1.5 | 0 | 32 | 0.053 | 38 |  | 9 | 0.03 | DGA is assessed as acceptable. | Breakdown voltage is low. Other oil quality results are assessed as acceptable.
33000 | 1955 | 56 | 254.6 | 27 | 233.2 | 5496.8 | 9.4 | 4.8 | 6.3 | 0.9 | 0 | 29 | 0.051 | 27 |  | 15 | 0.016 | DGA is assessed as acceptable. | Breakdown voltage is low. Other oil quality results are assessed as acceptable.
33000 | 1955 | 56 | 216 | 41.81 | 187 | 3760 | 0 | 3 | 20 | 1 | 5 | 20 | 0.174 | 64 |  | 3.5 | 0.063 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1955 | 56 | 466 | 41.81 | 380 | 5887 | 28 | 5 | 35 | 2 | 16 | 33 | 0.172 | 50 |  | 4 | 0.055 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1955 | 56 | 673 | 41.81 | 504 | 6879 | 36 | 10 | 50 | 4 | 69 | 33 | 0.192 | 50 |  | 3.6 | 0.063 | Moisture content of oil slightly high. Other test results satisfactory.
33000 | 1955 | 56 | 696 | 41.81 | 479 | 7480 | 43 | 9 | 63 | 4 | 98 | 27 | 0.21 | 50 |  | 4.2 | 0.062 | Test results satisfactory. Acetylene gas possibly from tapchanger.
33000 | 1955 | 56 | 225 | 41.81 | 179 | 2366 | 10 | 4 | 19 | 3 | 10 | 33 | 0.202 | 62 |  | 3.6 | 0.063 | Moisture and acidity levels are slightly high. Other test results are assessed as acceptable.
33000 | 1955 | 56 | 446 | 41.81 | 366 | 7370 | 0 | 5 | 55 | 3 | 17 | 24 | 0.14 | 53 |  | 6 | 0.0417 | Dissolved gas analysis is assessed as acceptable. Oil quality is assessed as acceptable.
33000 | 1955 | 56 | 586 | 41.81 | 443 | 7920 | 11 | 8 | 70 | 4 | 50 | 35 | 0.165 | 35 |  | 5.1 | 0.046 | Moisture content of oil slightly high. Other test results satisfactory.
33000 | 1955 | 56 | 762 | 41.81 | 600 | 8845 | 24 | 11 | 67 | 4 | 56 | 37 | 0.18 | 64 |  | 4.8 | 0.048 | Moisture content of oil slightly high. Other test results satisfactory.
33000 | 1955 | 56 | 841 | 41.81 | 618 | 10517 | 48 | 14 | 70 | 4 | 87 | 28 | 0.208 | 43 |  | 5.4 | 0.051 | Test results satisfactory. Acetylene gas possibly from tapchanger.
33000 | 1955 | 56 | 366 | 19 | 303 | 5363 | 6 | 4 | 33 | 5 | 15 | 32 | 0.238 | 67 |  | 4.6 | 0.051 | 2-furfural level is above 1ppm. Acidity level of oil is high. Other test results are assessed as acceptable.
33000 | 1955 | 56 | 23.1 | 29 | 15.4 | 893 | 0 | 1.2 | 5.9 | 0 | 0.6 | 20 | 0.01 | 47 |  | 159 | 0.01 | The test results are assessed as acceptable for a tapchanger.
33000 | 1955 | 56 | 327.3 | 29 | 272.9 | 2070.8 | 31.7 | 3.8 | 15.9 | 1.7 | 1.3 | 32 | 0.271 | 34 |  | 3 | 0.076 | Acidity level of sample is high. Other test results are assessed as acceptable.
33000 | 1955 | 56 | 205.7 | 41.81 | 183.5 | 5052.3 | 6.1 | 4.9 | 5.1 | 2.4 | 3.7 | 23 | 0.022 | 75 |  | 16.5 | 0.0185 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1955 | 56 | 162.2 | 41.81 | 133.7 | 4744.7 | 10 | 4.3 | 5.1 | 2.9 | 6.2 | 20 | 0.0136 | 61 |  | 15 | 0.018 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1955 | 56 | 229.3 | 41.81 | 196.8 | 6129.2 | 7.7 | 7.2 | 8 | 3.9 | 5.7 | 21 | 0.029 | 38 |  | 17 | 0.015 | DGA is assessed as acceptable. | Breakdown voltage is slightly low. Other oil quality results are assessed as acceptable.
33000 | 1955 | 56 | 358.4 | 25 | 215.3 | 5993 | 11.4 | 13.4 | 92.7 | 18.1 | 7.5 | 22 | 0.033 | 66 |  | 12 | 0.03 | Ethylene level is high. Other dissolved gas levels are assessed as acceptable. | Oil quality is assessed as acceptable. Corrosive IEC. Corrosive ASTM 4A.
33000 | 1955 | 56 | 235.1 | 23 | 127.1 | 5385.3 | 4.9 | 8.3 | 70.7 | 16.9 | 7.2 | 20 | 0.025 | 34 |  | 17 | 0.015 | Dissolved gas levels are relatively stable. | Breakdown voltage is low. Other oil quality results are assessed as acceptable.
33000 | 1955 | 56 | 179.5 | 24 | 111 | 4478 | 6.5 | 5 | 38.2 | 14 | 4.8 | 17 | 0.029 | 81 |  | 17 | 0.014 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1955 | 56 | 798 | 41.81 | 678 | 4373 | 96 | 9 | 8 | 4 | 3 | 47 | 0.374 | 35 |  | 6 | 0.0398 | Acidity level should be noted. Otherwise test results satisfactory.
33000 | 1955 | 56 | 701 | 41.81 | 582 | 8116 | 73 | 12 | 16 | 7 | 11 | 63 | 0.482 | 28 |  | 6.2 | 0.035 | Acidity level of oil is quite high. 2-furfural level is above 1ppm. Moisture content of oil is high. Other test results are assessed as acceptable.
33000 | 1955 | 56 | 875 | 41.81 | 729 | 6779 | 80 | 13 | 18 | 9 | 26 | 26 | 0.307 | 44 |  | 6.3 | 0.037 | Acidity content of oil high. Other test results satisfactory.
33000 | 1955 | 56 | 1001 | 41.81 | 842 | 7182 | 112 | 13 | 13 | 8 | 13 | 63 | 0.356 | 32 |  | 7.1 | 0.033 | Moisture and acidity levels high. Other test results satisfactory. Acetylene gas possibly from tapchanger.
33000 | 1955 | 56 | 67 | 41.81 | 62 | 851 | 0 | 2 | 2 | 0 | 1 | 32 | 0.034 | 34 |  | 42.8 | 0.013 | Test results satisfactory.
33000 | 1955 | 56 | 599 | 41.81 | 482 | 12331 | 36 | 11 | 45 | 7 | 18 | 38 | 0.1 | 41 |  | 11.1 | 0.014 | Moisture content of oil high. Other test results are assessed as acceptable at present. However; due to carbon dioxide level; RECOMMEND RESAMPLE IN 6 MONTHS TO MONITOR TREND.
33000 | 1955 | 56 | 675 | 41.81 | 533 | 15013 | 40 | 14 | 53 | 9 | 26 | 39 | 0.101 | 59 |  | 19.7 | 0.012 | Moisture content of oil is high. 2-Furfural level is above 1PPM. Carbon Oxide gas levels increasing. RECOMMEND RESAMPLE IN 1 YEAR TO MONITOR TREND.
33000 | 1955 | 56 | 635 | 41.81 | 508 | 14775 | 25 | 12 | 54 | 8 | 28 | 37 | 0.114 | 47 |  | 22.2 | 0.013 | Moisture content of oil is high. 2-Furfural level is above 1PPM and increasing. Carbon Oxide gas levels remained stable. RECOMMEND RESAMPLE IN 1 YEAR TO MONITOR TREND.
33000 | 1955 | 56 | 78 | 41.81 | 20 | 1548 | 34 | 1 | 23 | 0 | 0 | 15 | 0.056 | 64 |  | 11.5 | 0.023 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1955 | 56 | 274 | 41.81 | 237 | 2968 | 0 | 3 | 32 | 1 | 1 | 21 | 0.049 | 64 |  | 16.4 | 0.018 | Test results satisfactory.
33000 | 1955 | 56 | 281 | 41.81 | 248 | 2840 | 5 | 2 | 25 | 1 | 0 | 25 | 0.049 | 75 |  | 12 | 0.023 | Test results are assessed as acceptable.
33000 | 1955 | 56 | 442 | 41.81 | 341 | 5598 | 84 | 8 | 5 | 4 | 0 | 42 | 0.264 | 58 |  | 9 | 0.0371 | DGA is assessed as acceptable | Moisture content is high.
33000 | 1955 | 56 | 420 | 41.81 | 324 | 5162 | 77 | 8 | 5 | 5 | 1 | 32 | 0.26 | 46 |  | 8.5 | 0.0332 | DGA is assessed as acceptable
33000 | 1955 | 56 | 453 | 41.81 | 358 | 4692 | 78 | 7 | 6 | 3 | 1 | 30 | 0.233 | 42 |  | 8 | 0.0301 | DGA is assessed as acceptable
33000 | 1955 | 56 | 453 | 41.81 | 374 | 4660 | 65 | 6 | 5 | 3 | 0 | 50 | 0.268 | 51 |  | 6.8 | 0.033 | DGA is assessed as acceptable | Moisture content is high. Acidity level is high.
33000 | 1955 | 56 | 31 | 41.81 | 28 | 527 | 0 | 1 | 1 | 1 | 0 | 39 | 0.031 | 39 |  | 38.6 | 0.012 | DGA is assessed as acceptable | Moisture content of oil samples remain slightly high after oil change.
33000 | 1955 | 56 | 506 | 41.81 | 427 | 8427 | 50 | 6 | 22 | 1 | 0 | 40 | 0.046 | 47 |  | 29 | 0.011 | Moisture content of oil is above defect level. 2-furfural level is above 1ppm. Carbon dioxide level is high. Other test results are assessed as acceptable. RECOMMEND RESAMPLE IN 1 YEAR TO MONITOR TREND.
33000 | 1955 | 56 | 475 | 52 | 401 | 8492 | 47 | 6 | 20 | 1 | 0 | 37 | 0.057 | 22 |  | 22.9 | 0.017 | Moisture content of oil is high. Dielectric strength is low. 2-Furfural level is above 1ppm and increasing. Other test results are assessed as acceptable. RECOMMEND RESAMPLE IN 1 YEAR TO MONITOR TRENDS.
33000 | 1955 | 56 | 511 | 71 | 434 | 9675 | 45 | 6 | 26 | 0 | 0 | 51 | 0.051 | 31 |  | 22.6 | 0.011 | 2-fufural level is high and trending upwards. Moisture content of oil is high. Other test results are assessed as acceptable. RECOMMEND RESAMPLE IN 1 YEAR TO MONITOR TREND.
33000 | 1955 | 56 | 452 | 28 | 371 | 8397 | 44 | 8 | 26 | 2 | 1 | 25 | 0.063 | 27 |  | 10 | 0.026 | Main tank dissolved gas analysis results are consistent with previous main tank results. 2-furfural level is high and trending upwards suggesting accelerated rate of insulation degradation. Breakdown voltage of sample is low. RECOMMEND RESAMPLE IN 1 YE
33000 | 1955 | 56 | 212 | 33 | 193 | 5874 | 12 | 3 | 3 | 1 | 0 | 241 | 0.084 | 30 |  | 7 | 0.034 | Free water in sample possibly sample contamination. RECOMMEND RESAMPLE FOR MOISTURE. Other results satisfactory.
33000 | 1955 | 56 | 398 | 40 | 388 | 5346 | 0 | 5 | 4 | 1 | 0 | 30 | 0.127 | 23 |  | 7.7 | 0.031 | Test results satisfactory.
33000 | 1955 | 56 | 374 | 35 | 351 | 3938 | 15 | 3 | 3 | 2 | 0 | 27 | 0.092 | 72 |  | 7.7 | 0.033 | Test results satisfactory.
33000 | 1955 | 56 | 362 | 40 | 336 | 3815 | 18 | 4 | 3 | 1 | 0 | 28 | 0.117 | 43 |  | 7.4 | 0.032 | Test results satisfactory.
33000 | 1955 | 56 | 331 | 48 | 313 | 4224 | 9 | 4 | 4 | 1 | 0 | 34 | 0.136 | 68 |  | 7.4 | 0.036 | Moisture and acidity levels of oil high. Other test results satisfactory.
33000 | 1955 | 56 | 588 | 44 | 522 | 5536 | 40 | 12 | 10 | 4 | 0 | 56 | 0.16 | 57 |  | 8 | 0.026 | 2-Furfural level is high and increasing moisture content of oil is high. Other test results are assessed as acceptable. RECOMMEND RESAMPLE IN 1 YEAR TO MONITOR 2-FURFURAL.
33000 | 1954 | 57 | 205 | 47 | 162 | 3882 | 18 | 5 | 18 | 2 | 0 | 34 | 0.238 | 64 |  | 50 | 0.056 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1954 | 57 | 242 | 40 | 212 | 4675 | 0 | 6 | 20 | 4 | 0 | 34 | 0.266 | 39 |  | 3.9 | 0.058 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1954 | 57 | 209 | 35 | 184 | 4120 | 0 | 6 | 14 | 3 | 2 | 29 | 0.252 | 65 |  | 4.2 | 0.054 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1954 | 57 | 253 | 41.81 | 219 | 3429 | 19 | 5 | 8 | 2 | 0 | 39 | 0.237 | 45 |  | 4.3 | 0.053 | DGA is assessed as acceptable. | Moisture content of oil slightly high. Other test results satisfactory.
33000 | 1954 | 57 | 3767 | 41.81 | 349 | 8092 | 216 | 928 | 1871 | 349 | 54 | 44 | 0.248 | 43 |  | 5 | 0.05 | DGA shows significant oil overheating; possibly connection / contact. RECOMMEND INVESTIGATE.
33000 | 1954 | 57 | 90 | 41.81 | 66 | 2416 | 0 | 3 | 18 | 3 | 0 | 21 | 0.064 | 49 |  | 6.5 | 0.035 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1954 | 57 | 330 | 48 | 283 | 3735 | 17 | 5 | 22 | 3 | 0 | 21 | 0.038 | 72 |  | 23.7 | 0.015 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1954 | 57 | 339.6 | 30 | 295.7 | 4296 | 11.6 | 5.9 | 19.1 | 5.1 | 2.2 | 15 | 0.035 | 75 |  | 16 | 0.02 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1954 | 57 | 251.8 | 45 | 223.3 | 3552.2 | 6.6 | 4.3 | 14 | 3.6 | 0 | 22 | 0.032 | 34 |  | 14 | 0.02 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1954 | 57 | 283 | 40 | 255.3 | 3828.4 | 9.2 | 4.9 | 12.2 | 1.4 | 0 | 17 | 0.047 | 50 |  | 16 | 0.016 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1954 | 57 | 433.8 | 40 | 337.8 | 4553 | 52.9 | 5.9 | 32.9 | 4.3 | 0 | 23 | 0.042 | 49 |  | 8 | 0.03 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable. Corrosive IEC. Non-corrosive ASTM 3B.
33000 | 1954 | 57 | 367.3 | 47 | 330.9 | 4258.6 | 13.8 | 4.8 | 12.5 | 5.3 | 0 | 21 | 0.04 | 64 |  | 12 | 0.021 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1954 | 57 | 206 | 16 | 179 | 4152 | 7 | 3 | 14 | 3 | 0 | 12 | 0.041 | 66 |  | 15 | 0.015 | DGA is assessed as acceptable. | Resistivity is fair. Other oil quality results are assessed as acceptable.
33000 | 1954 | 57 | 218 | 12 | 182 | 3348 | 8 | 4 | 20 | 3 | 1 | 18 | 0.078 | 62 |  | 9 | 0.035 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1954 | 57 | 226 | 41.81 | 182 | 3185 | 25 | 3 | 12 | 3 | 1 | 17 | 0.071 | 57 |  | 9.4 | 0.025 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1954 | 57 | 356 | 41.81 | 313 | 4125 | 10 | 5 | 20 | 5 | 3 | 24 | 0.086 | 53 |  | 8.6 | 0.028 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1954 | 57 | 299 | 41.81 | 258 | 3674 | 18 | 5 | 15 | 3 | 0 | 21 | 0.092 | 49 |  | 8.8 | 0.03 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1954 | 57 | 237 | 41.81 | 209 | 2986 | 3 | 4 | 16 | 3 | 2 | 19 | 0.086 | 72 |  | 8.6 | 0.027 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1954 | 57 | 154 | 41.81 | 75 | 2026 | 26 | 8 | 18 | 2 | 25 | 22 | 0.09 | 46 |  | 8 | 0.024 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1954 | 57 | 774 | 41.81 | 609 | 6309 | 115 | 16 | 15 | 11 | 8 | 41 | 0.518 | 43 |  | 6 | 0.036 | Acidity too high. Oil replacement or inspection for sludge should be considered.
33000 | 1954 | 57 | 1047 | 41.81 | 831 | 8679 | 152 | 27 | 16 | 14 | 7 | 48 | 0.551 | 47 |  | 4.7 | 0.047 | Moisture and acidity levels of oil too high. Other test results satisfactory. RECOMMEND OIL CHANGE.
33000 | 1954 | 57 | 1238 | 41.81 | 956 | 8973 | 205 | 41 | 18 | 16 | 2 | 65 | 0.66 | 27 |  | 6.7 | 0.031 | 2-Furfural level is above 1PPM. Moisture and acidity levels very high. RECOMMEND OIL CHANGE/OIL TREATMENT.
33000 | 1954 | 57 | 742.8 | 41.81 | 515.2 | 8146.3 | 169.8 | 18.5 | 16.2 | 20.4 | 2.7 | 34 | 0.753 | 33 |  | 4 | 0.048 | 2-furfural level is high and trenging upwards suggesting accelerated rate of insulation degradation. Acidity level of sample is very high. Other test results are assessed as acceptable. RECOMMEND RESAMPLE IN 6 MONTHS TO MONITOR TREND. RECOMMEND OIL CH
33000 | 1954 | 57 | 1275 | 41.81 | 978.2 | 8448.4 | 241.7 | 21.9 | 14.3 | 16.3 | 2.6 | 59 | 0.701 | 33 |  | 5.3 | 0.045 | DGA is assessed as acceptable. | Oil quality is poor. Acidity level is very high.
33000 | 1954 | 57 | 633.3 | 41.81 | 506 | 5441.3 | 95.9 | 10.2 | 8.1 | 11 | 2.1 | 49 | 0.7535 | 58 |  | 3 | 0.058 | DGA is assessed as acceptable. | Moisture content is high. Acidity level is very high. Other oil quality results are assessed as acceptable.
33000 | 1954 | 57 | 856.1 | 41.81 | 674.6 | 6834 | 151.3 | 12 | 8.4 | 8.9 | 0.9 | 42 | 1.04 | 40 |  | 5 | 0.046 | DGA is assessed as acceptable. | Moisture content is high. Acidity level is high and outside acceptance limits. Other oil quality results are assessed as acceptable at present.
33000 | 1954 | 57 | 963.5 | 41.81 | 777.7 | 7397.4 | 148.8 | 18.7 | 8.1 | 10.1 | 0.1 | 46 | 0.708 | 23 |  | 6 | 0.038 | DGA is assessed as acceptable. | Acidity level is high. Breakdown voltage is low. DDF and Resistivity are assessed as acceptable. Corrosive IEC. Non-corrosive ASTM 3A.
33000 | 1954 | 57 | 777.8 | 20 | 627.7 | 7709.6 | 121.3 | 12.1 | 7.5 | 9.2 | 0 | 40 | 0.802 | 41 |  | 6 | 0.034 | DGA is assessed as acceptable. | Acidity level is high. Other oil quality results are assessed as acceptable.
33000 | 1954 | 57 | 253 | 54 | 226 | 922 | 0 | 5 | 19 | 2 | 1 | 18 | 0.026 | 47 |  | 43.8 | 0.01 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1954 | 57 | 198 | 30 | 170 | 2592 | 0 | 4 | 20 | 4 | 0 | 18 | 0.027 | 47 |  | 27.6 | 0.012 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1954 | 57 | 284 | 60 | 249 | 3094 | 6 | 4 | 21 | 3 | 1 | 21 | 0.036 | 61 |  | 20.7 | 0.013 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1954 | 57 | 375.9 | 75 | 323.3 | 3452.3 | 8.1 | 5.9 | 33.3 | 5.3 | 0 | 15 | 0.049 | 42 |  | 11 | 0.026 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1954 | 57 | 313.3 | 40 | 266.2 | 4071.3 | 7.4 | 5 | 30.3 | 4.3 | 0.1 | 15 | 0.051 | 37 |  | 11 | 0.024 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1954 | 57 | 206.2 | 41.81 | 175.2 | 2209.5 | 6.5 | 3.2 | 18.1 | 2.4 | 0.8 | 14 | 0.066 | 75 |  | 8 | 0.031 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1954 | 57 | 203.3 | 23 | 172.5 | 1915 | 10.1 | 2.5 | 15.5 | 2.7 | 0 | 14 | 0.06 | 75 |  | 11 | 0.025 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable. Corrosive IEC. Non-corrosive ASTM 3B.
33000 | 1954 | 57 | 214.7 | 41.81 | 187.5 | 2235.3 | 4.6 | 3.7 | 16.3 | 2.6 | 0 | 16 | 0.066 | 57 |  | 11 | 0.023 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1954 | 57 | 197.9 | 20 | 178.9 | 2005.2 | 0 | 2.9 | 13.9 | 2.2 | 0 | 14 | 0.064 | 70 |  | 10 | 0.026 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1954 | 57 | 380 | 41.81 | 338 | 4814 | 18 | 9 | 5 | 8 | 2 | 29 | 0.36 | 45 |  | 6.9 | 0.036 | DGA is assessed as acceptable. | Acidity content of oil high. Other test results satisfactory.
33000 | 1954 | 57 | 496 | 41.81 | 441 | 5311 | 29 | 12 | 7 | 7 | 0 | 42 | 0.409 | 54 |  | 7.1 | 0.03 | DGA is assessed as acceptable. | Moisture and acidity levels are high. Other test results are assessed as acceptable.
33000 | 1954 | 57 | 663.3 | 55 | 578.8 | 5636.6 | 44.8 | 15.4 | 10.8 | 13.5 | 0 | 44 | 0.423 | 23 |  | 5 | 0.043 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1954 | 57 | 677.5 | 41.81 | 600.4 | 8113.8 | 47.7 | 11.6 | 7.8 | 10 | 0 | 50 | 0.473 | 29 |  | 5 | 0.047 | DGA is assessed as acceptable. | Oil quality is poor.
33000 | 1954 | 57 | 573.3 | 41.81 | 503.7 | 4828.8 | 32.6 | 14.2 | 10.5 | 12.3 | 0 | 44 | 0.442 | 28 |  | 5 | 0.042 | DGA is assessed as acceptable. | Oil quality is poor.
33000 | 1954 | 57 | 495.5 | 41.81 | 438.2 | 5913.8 | 32.3 | 11 | 5.5 | 8.5 | 0 | 48 | 0.456 | 22 |  | 6 | 0.036 | DGA is assessed as acceptable. | Oil quality is poor.
33000 | 1954 | 57 | 413.3 | 42 | 368.6 | 3121.6 | 28.9 | 7.6 | 3.7 | 4.5 | 0 | 46 | 0.442 | 26 |  | 4 | 0.067 | DGA is assessed as acceptable. | Oil quality is poor. Corrosive IEC. Non-corrosive ASTM 3A.
33000 | 1954 | 57 | 343.1 | 22 | 311.3 | 2446.3 | 18.6 | 7.4 | 2.1 | 3.7 | 0 | 45 | 0.437 | 45 |  | 6 | 0.035 | DGA is assessed as acceptable. | Acidity level is high. Other oil quality results are assessed as acceptable.
33000 | 1954 | 57 | 559.9 | 28 | 493.3 | 3561.2 | 39.6 | 17.8 | 4 | 5.2 | 0 | 45 | 0.554 | 36 |  | 5 | 0.045 | DGA is assessed as acceptable. | Acidity level is high. Breakdown voltage is low. DDF and Resistivity are assessed as acceptable.
33000 | 1954 | 57 | 433.4 | 27 | 377.2 | 4307.9 | 29.3 | 13.2 | 5.1 | 8.6 | 0 | 38 | 0.499 | 26 |  | 6 | 0.034 | DGA is assessed as acceptable. | Acidity level is high. Breakdown voltage is low. DDF and Resistivity are assessed as acceptable.
33000 | 1954 | 57 | 831 | 25 | 427 | 3955 | 40 | 78 | 246 | 28 | 12 | 18 | 0.145 | 60 |  | 6 | 0.046 | Gas analysis suggests overheating joint /circulating currents.Resample 12 mths. Loose connections on A & C phases. (07/09/89 J.Daley)
33000 | 1954 | 57 | 918 | 30 | 417 | 3318 | 38 | 84 | 317 | 41 | 21 | 17 | 0.115 | 49 |  | 3.7 | 0.061 | Gas levels have remained stable. RECOMMEND RESAMPLE IN 12 MONTHS.
33000 | 1954 | 57 | 1301 | 29 | 433 | 3559 | 89 | 190 | 487 | 63 | 39 | 29 | 0.163 | 67 |  | 3.3 | 0.069 | A slow upward trend; suggesting overheating joint or circulating currents. RESAMPLE IN 12 MONTHS.
33000 | 1954 | 57 | 1495 | 25 | 571 | 4547 | 32 | 118 | 627 | 100 | 47 | 36 | 0.187 | 74 |  | 3.7 | 0.071 | Ethylene gas level is high. Suggests hot spot in oil. RECOMMEND RESAMPLE IN 12 MONTHS.
33000 | 1954 | 57 | 867 | 41.81 | 595 | 5166 | 65 | 27 | 102 | 21 | 57 | 39 | 0.178 | 58 |  | 3.2 | 0.058 | Ethylene gas level reduced. Has transformer been repaired? Has oil been filted/degassed? Test results satisfactory; however RECOMMEND RESAMPLE IN 1 YEAR TO MONITOR TREND.
33000 | 1954 | 57 | 892 | 41.81 | 518 | 4869 | 18 | 54 | 212 | 33 | 57 | 30 | 0.198 | 74 |  | 3.1 | 0.063 | Ethylene level increasing. Suggesting possible hot spot in oil. Other test results are assessed as acceptable. RECOMMEND RESAMPLE IN 6 MONTHS TO MONITOR ETHYLENE.
33000 | 1954 | 57 | 646 | 41.81 | 454 | 3691 | 15 | 19 | 107 | 15 | 36 | 31 | 0.207 | 73 |  | 3 | 0.066 | Gas levels have decreased. Other test results are assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1954 | 57 | 696.3 | 41.81 | 558.4 | 6310.1 | 24.1 | 17 | 60.4 | 14.8 | 21.6 | 39 | 0.248 | 31 |  | 3 | 0.091 | Dissolved hydrocarbon gas levels are reduced. | Moisture content of sample is high. Other test results are assessed as acceptable.
33000 | 1954 | 57 | 705.2 | 41.81 | 560 | 7083.9 | 21.6 | 20.6 | 58.5 | 14.2 | 30.3 | 38 | 0.26 | 35 |  | 2 | 0.078 | DGA is assessed as acceptable. | Acidity level is high. Moisture content is high. Other oil quality results are assessed as acceptable.
33000 | 1954 | 57 | 549.7 | 41.81 | 474.5 | 4779 | 15.6 | 13.8 | 33.7 | 6.3 | 5.8 | 29 | 0.288 | 42 |  | 2 | 0.083 | DGA is assessed as acceptable. | Acidity level is high. Other oil quality results are assessed as acceptable.
33000 | 1954 | 57 | 20275 | 41.81 | 4324 | 7329 | 3324 | 1967 | 4309 | 357 | 5994 | 50 | 0.368 | 24 |  | 3 | 0.078 | DGA suggests arcing has occurred. | Moisture content is high. Acidity level is high. Breakdown voltage is low.
33000 | 1954 | 57 | 9720.4 | 22 | 1497.2 | 5209.7 | 215.2 | 960.3 | 3000.4 | 308.3 | 3739 | 20 | 0.246 | 72 |  | 3 | 0.077 | DGA suggests arcing has occurred. Dissolved gas levels possibly communicating from tapchanger. | Oil quality is assessed as acceptable.
33000 | 1954 | 57 | 1409 | 36 | 890 | 3285 | 53 | 163 | 91 | 211 | 1 | 14 | 0.078 | 42 |  | 6 | 0.04 | D.G.A. Suggests slight overheating. Suggest resample in 12 months.
33000 | 1954 | 57 | 627 | 29 | 553 | 6999 | 0 | 4 | 68 | 1 | 1 | 16 | 0.111 | 49 |  | 6.5 | 0.04 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1954 | 57 | 809 | 40 | 715 | 7488 | 19 | 4 | 70 | 1 | 0 | 25 | 0.086 | 40 |  | 5.1 | 0.046 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1954 | 57 | 656 | 40 | 597 | 5637 | 0 | 3 | 51 | 1 | 4 | 29 | 0.076 | 60 |  | 6.5 | 0.041 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1954 | 57 | 904 | 40 | 767 | 6720 | 19 | 6 | 68 | 1 | 43 | 34 | 0.048 | 65 |  | 7.2 | 0.046 | Moisture content of oil slightly high. Other test results satisfactory.
33000 | 1954 | 57 | 812 | 45 | 700 | 6841 | 26 | 5 | 61 | 1 | 19 | 28 | 0.093 | 53 |  | 5 | 0.04 | DGA satisfactory. Results similar to 28/5/96. Sampled after Buchholz surge trip. No gas in Buchholz.
33000 | 1954 | 57 | 662 | 41.81 | 588 | 5796 | 18 | 4 | 48 | 1 | 3 | 32 | 0.099 | 69 |  | 6 | 0.04 | Moisture content of oil slightly high. Other test results are assessed as acceptable.
33000 | 1954 | 57 | 844.4 | 47 | 729.8 | 4914.2 | 28.4 | 5.8 | 78.2 | 1.8 | 0.4 | 31 | 0.135 | 48 |  | 4 | 0.071 | Moisture content of sample is slightly high, otherwise the test results are assessed as acceptable.
33000 | 1954 | 57 | 1418 | 42 | 828 | 7760 | 171 | 58 | 193 | 14 | 154 | 46 | 0.128 | 31 |  | 4 | 0.074 | Moisture content of sample is high. Dissolved gas analysis suggests high energy arcing with insulation damage. RECOMMEND INVESTIGATE.
33000 | 1954 | 57 | 416 | 34 | 346 | 6668 | 0 | 6 | 57 | 7 | 0 | 18 | 0.065 | 62 |  | 7 | 0.049 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1954 | 57 | 230 | 50 | 210 | 3536 | 0 | 3 | 16 | 1 | 0 | 21 | 0.014 | 34 |  | 76.9 | 0.0086 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1954 | 57 | 273 | 40 | 241 | 5354 | 0 | 3 | 28 | 1 | 0 | 19 | 0.014 | 57 |  | 55.6 | 0.01 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1954 | 57 | 384 | 50 | 344 | 6034 | 5 | 4 | 30 | 1 | 0 | 19 | 0.029 | 67 |  | 30.4 | 0.017 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1954 | 57 | 288 | 41.81 | 245 | 5227 | 1 | 4 | 30 | 1 | 7 | 20 | 0.023 | 60 |  | 49.8 | 0.008 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1954 | 57 | 557.9 | 51 | 467.1 | 6354.5 | 8.1 | 5.6 | 74.7 | 2.4 | 0 | 25 | 0.034 | 42 |  | 20 | 0.022 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1954 | 57 | 547.5 | 45 | 473.4 | 9616.3 | 8.2 | 4.7 | 59.5 | 1.7 | 0 | 23 | 0.041 | 36 |  | 18 | 0.02 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1954 | 57 | 519.8 | 41.81 | 446.1 | 9255.9 | 9.6 | 4.6 | 53.7 | 0.3 | 5.5 | 27 | 0.047 | 39 |  | 18 | 0.02 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1953 | 58 | 1776 | 41.81 | 389 | 6494 | 293 | 143 | 393 | 46 | 512 | 24 | 0.414 | 57 |  | 9 | 0.0285 | Oil sample taken while at Northgate before untanking for inspection.
33000 | 1953 | 58 | 269 | 41.81 | 196 | 2873 | 39 | 13 | 17 | 4 | 0 | 36 | 0.037 | 32 |  | 60 | 0.01 | Test results satisfactory. Oil changed?
33000 | 1953 | 58 | 42 | 41.81 | 31 | 918 | 0 | 1 | 9 | 1 | 0 | 18 | 0.024 | 59 |  | 25.3 | 0.015 | Test results satisfactory.
33000 | 1953 | 58 | 38 | 41.81 | 15 | 1089 | 0 | 1 | 16 | 6 | 0 | 16 | 0.043 | 58 |  | 23.4 | 0.012 | Test results are assessed as acceptable.
33000 | 1953 | 58 | 17 | 25 | 11 | 382 | 6 | 0 | 0 | 0 | 0 | 10 | 0.005 | 49 |  | 22.2 | 0.021 | Test results are assessed as acceptable.
33000 | 1953 | 58 | 533 | 41.81 | 394 | 6995 | 52 | 25 | 58 | 4 | 0 | 35 | 0.306 | 46 |  | 6 | 0.0649 | Test results satisfactory.
33000 | 1953 | 58 | 51 | 41.81 | 8 | 2292 | 0 | 1 | 32 | 10 | 0 | 19 | 0.289 | 59 |  | 4.3 | 0.04 | Noted.
33000 | 1953 | 58 | 158 | 41.81 | 126 | 2145 | 0 | 2 | 29 | 1 | 0 | 17 | 0.149 | 54 |  | 4.5 | 0.0561 | Test results satisfactory.
33000 | 1953 | 58 | 88 | 41.81 | 83 | 793 | 0 | 1 | 4 | 0 | 0 | 23 | 0.158 | 59 |  | 3.5 | 0.074 | Test results satisfactory.
33000 | 1953 | 58 | 284 | 41.81 | 252 | 3568 | 0 | 13 | 12 | 6 | 1 | 16 | 0.07 | 58 |  | 10 | 0.0318 | Test results satisfactory.
33000 | 1953 | 58 | 190 | 41.81 | 172 | 3078 | 0 | 7 | 8 | 3 | 0 | 12 | 0.088 | 47 |  | 13.6 | 0.0183 | Test results satisfactory.
33000 | 1953 | 58 | 957 | 40 | 891 | 8598 | 26 | 22 | 8 | 10 | 0 | 44 | 0.262 | 36 |  | 10.5 | 0.023 | DGA is assessed as acceptable. | Moisture content is high. Acidity level is high.
33000 | 1953 | 58 | 1132 | 70 | 1055 | 9449 | 36 | 23 | 9 | 9 | 0 | 45 | 0.263 | 42 |  | 11.5 | 0.022 | Moisture and acidity quite high. Carbon oxide gases quite high. Transformer shows signs of insulation ageing.
33000 | 1953 | 58 | 1056 | 55 | 978 | 10679 | 35 | 23 | 10 | 9 | 1 | 52 | 0.268 | 29 |  | 10.3 | 0.024 | 2-furfural shows insulation degradation. Moisture content of oil is high. Carbon oxide levels are high.
33000 | 1953 | 58 | 997 | 35 | 905 | 8808 | 34 | 25 | 11 | 10 | 12 | 35 | 0.283 | 33 |  | 8.9 | 0.029 | Acidity level is high. Moisture content of oil is high. 2-furfural level is high but stable. Gas levels have remained fairly stable. RECOMMEND RESAMPLE IN 1 YEAR TO MONITOR TREND.
33000 | 1953 | 58 | 784 | 50 | 719 | 7945 | 23 | 21 | 8 | 11 | 2 | 45 | 0.266 | 26 |  | 8.2 | 0.027 | 2-furfural level is high. Acidity level of oil is high; Moisture content of oil is high. Dielectric strength is slightly low. RECOMMEND RESAMPLE IN 1 YEAR TO MONITOR.
33000 | 1953 | 58 | 0 | 41.81 | [8 empty] | 0.24 | 58 |  | 7 | 0.031 | Test results satisfactory.
33000 | 1953 | 58 | 861 | 38 | 793 | 7408 | 18 | 20 | 23 | 6 | 1 | 36 | 0.062 | 49 |  | 33.9 | 0.01 | Test results satisfactory.
33000 | 1953 | 58 | 919 | 53 | 839 | 9320 | 33 | 20 | 20 | 7 | 0 | 32 | 0.062 | 43 |  | 22.8 | 0.015 | Oil quality satisfactory. Level of carbon oxide gases quite high. Suggests aged deterioration of insulation.
33000 | 1953 | 58 | 815 | 54 | 761 | 8970 | 14 | 18 | 17 | 5 | 0 | 40 | 0.074 | 49 |  | 18.3 | 0.017 | 2-furfural levels show further degradation. Moisture content of oil is high. Other test results are assessed as acceptable.
33000 | 1953 | 58 | 494 | 41.81 | 457 | 5720 | 0 | 18 | 9 | 8 | 2 | 20 | 0.116 | 59 |  | 5 | 0.0685 | Test results satisfactory.
33000 | 1953 | 58 | 172 | 41.81 | 152 | 4614 | 0 | 9 | 5 | 6 | 0 | 19 | 0.162 | 44 |  | 6.7 | 0.0351 | Test results satisfactory.
33000 | 1953 | 58 | 790 | 44 | 748 | 9034 | 0 | 20 | 10 | 9 | 3 | 34 | 0.176 | 49 |  | 4.5 | 0.052 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1953 | 58 | 875 | 35 | 649 | 18776 | 52 | 16 | 94 | 10 | 54 | 51 | 0.244 | 24 |  | 7 | 0.036 | CO2 and moisture quite high. DGA suggests slight overheating.
33000 | 1953 | 58 | 537 | 41.81 | 427 | 13526 | 32 | 10 | 61 | 5 | 2 | 42 | 0.259 | 52 |  | 4.9 | 0.051 | CO2 level quite high. Suggests advanced stage of insulation ageing.
33000 | 1953 | 58 | 511 | 41.81 | 393 | 12678 | 43 | 9 | 59 | 5 | 2 | 48 | 0.266 | 34 |  | 4.9 | 0.047 | Consistent with previous result.
33000 | 1953 | 58 | 674 | 32 | 575 | 11443 | 0 | 10 | 77 | 7 | 5 | 53 | 0.233 | 29 |  | 8 | 0.033 | Moisture content of oil slightly high. Other test results satisfactory.
33000 | 1953 | 58 | 321 | 41.81 | 306 | 2788 | 0 | 3 | 11 | 1 | 0 | 38 | 0.2 | 57 |  | 5.7 | 0.051 | Gas levels reduced significantly. Has transformer oil been treated?
33000 | 1951 | 60 | 260 | 41.81 | 228 | 3025 | 15 | 6 | 6 | 5 | 0 | 19 | 0.273 | 29 |  | 7.2 | 0.0323 | DGA satisfactory. | Oil quality is assessed as acceptable.
33000 | 1951 | 60 | 388 | 41.81 | 333 | 5684 | 35 | 7 | 6 | 6 | 1 | 45 | 0.346 | 45 |  | 5 | 0.045 | DGA is assessed as acceptable. | Acidity and moisture levels are high. Other test results are assessed as acceptable.
33000 | 1951 | 60 | 509 | 41.81 | 420 | 6600 | 50 | 11 | 16 | 12 | 0 | 56 | 0.358 | 20 |  | 6 | 0.037 | DGA is assessed as acceptable. | 2-furfural, moisture and acidity levels are high suggesting accelerated rate of insulation degradation. Breakdown voltage is low. Other test results are assessed as acceptable.
33000 | 1951 | 60 | 888.8 | 41.81 | 583.2 | 9404.3 | 268.5 | 11.3 | 14.6 | 8.6 | 2.6 | 49 | 0.37 | 26 |  | 4 | 0.046 | DGA is assessed as acceptable. | Breakdown voltage of sample is low. Moisture content of sample is high. Acidity level of sample is high.
33000 | 1951 | 60 | 535.8 | 41.81 | 374.1 | 5260.2 | 138 | 8.9 | 7.1 | 7.6 | 0.1 | 47 | 0.375 | 23 |  | 6 | 0.036 | DGA is assessed as acceptable. | Oil quality is poor. Acidity level is high. Sample is cloudy in appearance.
33000 | 1951 | 60 | 431.5 | 41.81 | 371.6 | 5871.5 | 33.5 | 9.5 | 7.5 | 9.4 | 0 | 49 | 0.375 | 37 |  | 4 | 0.048 | DGA is assessed as acceptable. | Moisture content is high. Acidity level is high. Other oil quality results are assessed as acceptable.
33000 | 1951 | 60 | 339.8 | 41.81 | 264.1 | 4774.2 | 15.6 | 15.3 | 32.1 | 12.7 | 0 | 33 | 0.36 | 39 |  | 7 | 0.035 | DGA is assessed as acceptable. | Moisture content is high. Acidity level is high. Other oil quality results are assessed as acceptable.
33000 | 1951 | 60 | 444.8 | 24 | 319.7 | 4530.7 | 79.3 | 12.4 | 23.2 | 10.2 | 0 | 40 | 0.387 | 29 |  | 6 | 0.036 | DGA is assessed as acceptable. | Acidity level is high. Breakdown voltage is low. DDF and Resistivity are assessed as acceptable. Corrosive IEC. Non-corrosive ASTM 3B.
33000 | 1951 | 60 | 888.1 | 30 | 281.2 | 4347.4 | 22.7 | 69.8 | 410.2 | 102.3 | 1.9 | 38 | 0.417 | 29 |  | 6 | 0.035 | DGA suggests high temperature oil overheating (300-700°C) has occurred. | Oil quality is poor.
33000 | 1951 | 60 | 779.9 | 41.81 | 249.3 | 4115.6 | 19.7 | 57.5 | 361.1 | 90.6 | 1.7 | 41 | 0.408 | 43 |  | 5 | 0.04 | Dissolved gas levels are reduced slightly. DGA suggests high temperature oil overheating (300-700°C) has occurred. | Acidity level is high. Other oil quality results are assessed as acceptable.
33000 | 1951 | 60 | 616.6 | 30 | 233 | 3868.9 | 16.6 | 32.1 | 260.2 | 73.7 | 1 | 39 | 0.379 | 44 |  | 6 | 0.036 | DGA suggests high temperature oil overheating (300-700°C) has occurred. | Acidity level is high. Other oil quality results are assessed as acceptable.
33000 | 1951 | 60 | 470.9 | 31 | 271.9 | 4341.9 | 20.9 | 17.2 | 116.1 | 44.8 | 0 | 33 | 0.43 | 30 |  | 6 | 0.032 | Dissolved gas levels are reduced. DGA suggests high temperature oil overheating has occurred. | Acidity level is high. Breakdown voltage is low. Other oil quality results are assessed as acceptable.
33000 | 1951 | 60 | 223 | 41.81 | 189 | 3095 | 26 | 4 | 0 | 4 | 0 | 42 | 0.251 | 30 |  | 8 | 0.028 | DGA is assessed as acceptable. | Moisture content high. Acidity should be monitored.
33000 | 1951 | 60 | 258 | 41.81 | 219 | 2265 | 29 | 5 | 3 | 2 | 0 | 39 | 0.331 | 30 |  | 7.9 | 0.028 | DGA is assessed as acceptable. | Moisture content of oil is high. Other test results are assessed as acceptable.
33000 | 1951 | 60 | 224.2 | 41.81 | 194.7 | 2355.6 | 17.4 | 4.3 | 4.1 | 3.7 | 0 | 28 | 0.363 | 50 |  | 5 | 0.041 | Dissolved gas analysis is assessed as acceptable. | Acidity level of sample is high but relatively stable. Other oil quality results are assessed as acceptable.
33000 | 1951 | 60 | 254.8 | 41.81 | 224.5 | 3207.5 | 15 | 6.5 | 4.9 | 3.9 | 0 | 37 | 0.328 | 42 |  | 4 | 0.048 | DGA is assessed as acceptable. | Moisture content is slightly high. Acidity level is high. Other oil quality results are assessed as acceptable.
33000 | 1951 | 60 | 176.1 | 41.81 | 152 | 2328.3 | 14.2 | 4.1 | 2.9 | 2.9 | 0 | 36 | 0.358 | 42 |  | 8 | 0.032 | DGA is assessed as acceptable. | Acidity level is high. Moisture content is high. Other oil quality results are assessed as acceptable.
33000 | 1951 | 60 | 241.8 | 41.81 | 199.8 | 3275.4 | 28.5 | 5.2 | 4.3 | 4 | 0 | 34 | 0.345 | 55 |  | 6 | 0.034 | DGA is assessed as acceptable. | Moisture content is high. Acidity level is high. Other oil quality results are assessed as acceptable.
33000 | 1951 | 60 | 185.4 | 41.81 | 160.4 | 2816.7 | 14.2 | 4.3 | 3.2 | 3.3 | 0 | 27 | 0.365 | 50 |  | 5 | 0.04 | DGA is assessed as acceptable. | Acidity level is high but relatively stable. Other oil quality results are assessed as acceptable.
33000 | 1951 | 60 | 139.7 | 41.81 | 121.3 | 2393.5 | 8.4 | 3.6 | 3.2 | 3.2 | 0 | 33 | 0.375 | 58 |  | 6 | 0.032 | DGA is assessed as acceptable. | Acidity level is high. Other oil quality results are assessed as acceptable.
33000 | 1951 | 60 | 244.8 | 41.81 | 213.2 | 3442.7 | 19.6 | 5.1 | 3.5 | 3.4 | 0 | 32 | 0.347 | 34 |  | 6 | 0.034 | DGA is assessed as acceptable. | Acidity level is high. Breakdown voltage is low. DDF and Resistivity are assessed as acceptable. Corrosive IEC. Non-corrosive ASTM 3B.
33000 | 1951 | 60 | 205.8 | 23 | 176.5 | 2958.5 | 15.3 | 5.7 | 3.7 | 4.6 | 0 | 29 | 0.344 | 42 |  | 6 | 0.034 | DGA is assessed as acceptable. | Acidity level is high but stable. Other oil quality results are assessed as acceptable.
33000 | 1951 | 60 | 171.4 | 28 | 152.7 | 2713.6 | 9.4 | 4.3 | 2.8 | 2.2 | 0 | 38 | 0.328 | 55 |  | 7 | 0.03 | DGA is assessed as acceptable. | Acidity level is high. Other oil quality results are assessed as acceptable.
33000 | 1951 | 60 | 829 | 39 | 698 | 7875 | 99 | 14 | 12 | 6 | 0 | 44 | 0.466 | 42 |  | 7 | 0.051 | Acidity level high. Oil change should be considered for future.D.G.A. satisfactory.
33000 | 1951 | 60 | 378 | 25 | 321 | 4258 | 42 | 6 | 6 | 3 | 0 | 33 | 0.415 | 61 |  | 7 | 0.033 | D.G.A. Satisfactory. Acidity level high. Future oil change should be considered.
33000 | 1951 | 60 | 523 | 41.81 | 450 | 4631 | 57 | 6 | 7 | 3 | 0 | 59 | 0.485 | 49 |  | 4.5 | 0.053 | Previous comments still apply.
33000 | 1951 | 60 | 375 | 41.81 | 312 | 4076 | 50 | 5 | 6 | 2 | 0 | 47 | 0.43 | 56 |  | 4.5 | 0.054 | Oil sample prior to oil change.
33000 | 1951 | 60 | 293 | 41.81 | 224 | 2361 | 49 | 3 | 16 | 1 | 0 | 47 | 0.092 | 46 |  | 17.5 | 0.02 | Moisture content of oil high. Other test results satisfactory.
33000 | 1951 | 60 | 405 | 41.81 | 311 | 2408 | 58 | 5 | 29 | 1 | 1 | 44 | 0.081 | 39 |  | 20.7 | 0.018 | Moisture content of oil high. Other test results satisfactory.
33000 | 1951 | 60 | 424 | 41.81 | 322 | 5013 | 47 | 6 | 47 | 2 | 0 | 50 | 0.079 | 30 |  | 12.3 | 0.022 | Moisture content of oil is high. Other test results are assessed as acceptable.
33000 | 1951 | 60 | 340.5 | 44 | 223.5 | 5520 | 28.6 | 4 | 81.1 | 3.3 | 0 | 29 | 0.099 | 23 |  | 6 | 0.041 | 2-furfural level is high suggesting accelerated rate of insulation degradation. Breakdown voltage of sample is low. RECOMMEND RESAMPLE IN 1 YEAR TO MONITOR CONDITION.
33000 | 1949 | 62 | 184 | 41.81 | 160 | 3109 | 0 | 3 | 19 | 2 | 0 | 22 | 0.098 | 48 |  | 7 | 0.036 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1949 | 62 | 252 | 32 | 222 | 4396 | 0 | 4 | 22 | 3 | 1 | 21 | 0.122 | 46 |  | 6.3 | 0.037 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1949 | 62 | 429 | 41.81 | 331 | 11416 | 42 | 8 | 43 | 5 | 0 | 36 | 0.124 | 46 |  | 5.1 | 0.047 | Moisture content of oil slightly high; possibly sample contamination. Other test results are assessed as acceptable at present. However; RECOMMEND RESAMPLE IN 6 MONTHS TO MONITOR CARBON DIOXIDE GAS LEVEL.
33000 | 1949 | 62 | 537 | 30 | 451 | 13939 | 37 | 5 | 42 | 2 | 0 | 42 | 0.186 | 43 |  | 5 | 0.048 | Moisture content of oil is high. 2-Furfural level is above 1PPM. Carbon Oxide gas levels increasing. RECOMMNED RESAMPLE IN 1 YEAR TO MONITOR TREND.
33000 | 1949 | 62 | 557 | 41.81 | 455 | 14389 | 32 | 11 | 51 | 8 | 0 | 38 | 0.179 | 38 |  | 4.7 | 0.042 | Moisture content of oil is high. 2-Furfural level is above 1PPM and increasing. Carbon Oxide gas levels are fairly stable. RECOMMEND RESAMPLE IN 1 YEAR TO MONITOR TREND.
33000 | 1949 | 62 | 228 | 41.81 | 198 | 3244 | 6 | 3 | 20 | 1 | 0 | 71 | 0.094 | 42 |  | 7.2 | 0.031 | Moisture content of oil is very high. Other test results are assessed as acceptable. RECOMMEND RESAMPLE TO CHECK MOISTURE CONTENT OF OIL.
33000 | 1949 | 62 | 197 | 41.81 | 171 | 3328 | 3 | 1 | 22 | 0 | 0 | 34 | 0.104 | 25 |  | 6.4 | 0.035 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1949 | 62 | 344.2 | 41.81 | 261.6 | 4586.1 | 38.5 | 5 | 35.8 | 3.3 | 0 | 23 | 0.135 | 38 |  | 6 | 0.038 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1949 | 62 | 386.4 | 41.81 | 285.9 | 5308.4 | 59.8 | 4.9 | 32.7 | 3.1 | 0 | 21 | 0.132 | 45 |  | 6.1 | 0.041 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1949 | 62 | 216.5 | 41.81 | 175.1 | 4368.9 | 12.6 | 3.7 | 22.7 | 2.4 | 0 | 30 | 0.1531 | 70 |  | 5 | 0.04 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1949 | 62 | 264.4 | 41.81 | 205 | 3848.4 | 30 | 3.6 | 24.1 | 1.7 | 0 | 22 | 0.174 | 42 |  | 5 | 0.04 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1949 | 62 | 342.2 | 23 | 300.6 | 4902.3 | 8.2 | 4.1 | 28.1 | 1.2 | 0 | 51 | 0.185 | 28 |  | 5 | 0.047 | DGA is assessed as acceptable. | Breakdown voltage is low. Other oil quality results are assessed as acceptable. Corrosive IEC. Non-corrosive ASTM 3B.
33000 | 1949 | 62 | 234.4 | 18 | 205.3 | 3745.2 | 1.3 | 3 | 21.9 | 2.9 | 0 | 36 | 0.175 | 38 |  | 6 | 0.037 | DGA is assessed as acceptable. | Breakdown voltage is low. Other oil quality results are assessed as acceptable. Corrosive IEC. Non-corrosive ASTM 3A.
33000 | 1949 | 62 | 188.4 | 24 | 163 | 3869.1 | 4.3 | 2.3 | 17.2 | 1.6 | 0 | 60 | 0.196 | 16 |  | 5 | 0.041 | DGA is assessed as acceptable. | Breakdown voltage is low. Other oil quality results are assessed as acceptable.
33000 | 1949 | 62 | 164 | 41.81 | 145 | 2240 | 0 | 1 | 17 | 1 | 0 | 31 | 0.112 | 49 |  | 3.3 | 0.078 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1949 | 62 | 235 | 41.81 | 207 | 3282 | 0 | 3 | 24 | 1 | 0 | 23 | 0.132 | 57 |  | 4.8 | 0.058 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1949 | 62 | 243 | 41.81 | 219 | 3017 | 0 | 3 | 20 | 1 | 0 | 29 | 0.135 | 50 |  | 3.2 | 0.071 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1949 | 62 | 258.3 | 41.81 | 220.4 | 3622.9 | 5.6 | 2.7 | 27 | 2.6 | 0 | 23 | 0.156 | 41 |  | 4 | 0.059 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1949 | 62 | 249.4 | 41.81 | 217.7 | 3226.3 | 5.6 | 3.1 | 21.1 | 1.9 | 0 | 22 | 0.143 | 51 |  | 4.1 | 0.059 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1949 | 62 | 204.2 | 41.81 | 177.6 | 3139.5 | 4.3 | 2.4 | 17.7 | 2.2 | 0 | 15 | 0.208 | 75 |  | 4 | 0.05 | DGA is assessed as acceptable. | Acidity level is high. Other oil quality results are assessed as acceptable.
33000 | 1949 | 62 | 225.9 | 41.81 | 197.8 | 3194.5 | 5.6 | 2.9 | 17.9 | 1.7 | 0 | 19 | 0.183 | 58 |  | 4 | 0.059 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable. Corrosive IEC. Non-corrosive ASTM 3A.
33000 | 1949 | 62 | 198.7 | 20 | 177.6 | 3294.7 | 2.1 | 1.7 | 16 | 1.3 | 0 | 17 | 0.213 | 80 |  | 4 | 0.05 | DGA is assessed as acceptable. | Acidity level is high. Other oil quality results are assessed as acceptable.
33000 | 1949 | 62 | 238.1 | 26 | 209.5 | 3224.9 | 6.7 | 4.9 | 14.9 | 2.1 | 0 | 24 | 0.199 | 58 |  | 4 | 0.049 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1949 | 62 | 178 | 41.81 | 172 | 3087 | 0 | 2 | 2 | 1 | 1 | 41 | 0.396 | 49 |  | 4.6 | 0.043 | DGA satisfactory but acidity level quite high.
33000 | 1949 | 62 | 250 | 41.81 | 206 | 3721 | 36 | 3 | 3 | 2 | 0 | 39 | 0.365 | 69 |  | 6.6 | 0.032 | Moisture and acidity levels of oil quite high. Other test results satisfactory. OIL CHANGE IS RECOMMENDED.
33000 | 1949 | 62 | 29 | 41.81 | 27 | 356 | 0 | 1 | 1 | 0 | 0 | 17 | 0.022 | 57 |  | 56.5 | 0.008 | Test results satisfactory. TX has had oil change.
33000 | 1949 | 62 | 97 | 41.81 | 82 | 2630 | 3 | 2 | 9 | 1 | 0 | 25 | 0.046 | 52 |  | 33.3 | 0.009 | Test results are assessed as acceptable.
33000 | 1949 | 62 | 109.7 | 41.81 | 95.2 | 3002.7 | 0 | 2.1 | 10.5 | 1.9 | 0 | 21 | 0.048 | 38 |  | 17 | 0.016 | The test results are assessed as acceptable.
33000 | 1949 | 62 | 119.1 | 41.81 | 104.6 | 2541.3 | 3.1 | 2.3 | 7.9 | 1.2 | 0 | 21 | 0.049 | 44 |  | 19.3 | 0.015 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1949 | 62 | 116.6 | 41.81 | 85.2 | 2692.8 | 21 | 2.2 | 6.9 | 1.3 | 0 | 16 | 0.074 | 60 |  | 17 | 0.01453 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1949 | 62 | 151.6 | 41.81 | 133 | 2593.7 | 2.6 | 8.2 | 6.7 | 1.1 | 0 | 17 | 0.058 | 73 |  | 16 | 0.017 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable. Corrosive IEC. Non-corrosive ASTM 3B.
33000 | 1949 | 62 | 89.3 | 20 | 79.6 | 2704.1 | 0 | 1.4 | 6.9 | 1.4 | 0 | 16 | 0.064 | 73 |  | 16 | 0.016 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1949 | 62 | 110.5 | 26 | 92 | 2579 | 5.1 | 5.5 | 6.8 | 1.1 | 0 | 22 | 0.059 | 37 |  | 13 | 0.018 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1949 | 62 | 575 | 41.81 | 497 | 5492 | 50 | 7 | 9 | 4 | 8 | 35 | 0.382 | 69 |  | 7.8 | 0.027 | Acidity level of oil is high. Moisture content of oil is slightly high. 2-furfural level is above 1ppm. Other test results are assessed as acceptable.
33000 | 1949 | 62 | 644.1 | 41.81 | 560.3 | 7560.1 | 45 | 10.6 | 10.8 | 6.8 | 10.6 | 36 | 0.424 | 39 |  | 7 | 0.032 | Moisture content of sample is high. Acidity level of sample is high. Carbon dioxide level is high. 2-furfural level is high suggesting accelerated rate of insulation degradation. RECOMMEND RESAMPLE IN 1 YEAR TO MONITOR CONDITION.
33000 | 1949 | 62 | 658.9 | 41.81 | 586.1 | 7290.6 | 43.3 | 9 | 9.3 | 6.1 | 5.1 | 32 | 0.413 | 52 |  | 6.5 | 0.038 | DGA is assessed as acceptable. | Moisture content is high. Acidity level is very high.
33000 | 1949 | 62 | 282.6 | 41.81 | 235.6 | 3267.1 | 35.8 | 3.7 | 3.5 | 1.6 | 2.4 | 26 | 0.462 | 61 |  | 6 | 0.038 | DGA is assessed as acceptable. | Acidity level is high. Other oil quality results are assessed as acceptable.
33000 | 1949 | 62 | 288.8 | 41.81 | 258.8 | 2649.8 | 15.2 | 9.9 | 2.3 | 2.4 | 0.2 | 21 | 0.45 | 28 |  | 7 | 0.034 | DGA is assessed as acceptable. | Acidity level is high. Breakdown voltage is low. Other oil quality results are assessed as acceptable. Corrosive IEC. Non-corrosive ASTM 3B.
33000 | 1949 | 62 | 168.4 | 41.81 | 164.7 | 2212.6 | 0 | 1.1 | 2 | 0.4 | 0.2 | 26 | 0.433 | 59 |  | 6 | 0.036 | DGA is assessed as acceptable. | Acidity level is high. Other oil quality results are assessed as acceptable. Non-corrosive IEC. Non-corrosive ASTM 3A.
33000 | 1949 | 62 | 185.6 | 28 | 168.5 | 2467.1 | 11.2 | 3.1 | 1.9 | 0.9 | 0 | 20 | 0.431 | 34 |  | 6 | 0.035 | DGA is assessed as acceptable. | Acidity level is high. Breakdown voltage is low. DDF and Resistivity are assessed as acceptable.
33000 | 1949 | 62 | 205.2 | 20 | 189.3 | 2741.2 | 9.8 | 2.8 | 1.6 | 1.7 | 0 | 23 | 0.458 | 65 |  | 7 | 0.032 | DGA is assessed as acceptable. | Acidity level is high. Other oil quality results are assessed as acceptable.
33000 | 1949 | 62 | 228.1 | 23 | 203.3 | 2610.4 | 13.9 | 5.7 | 2 | 3.2 | 0 | 26 | 0.478 | 43 |  | 6 | 0.033 | DGA is assessed as acceptable. | Acidity level is high. Other oil quality results are assessed as acceptable.
33000 | 1949 | 62 | 176 | 41.81 | 148 | 1242 | 0 | 2 | 26 | 0 | 0 | 9 | 0.037 | 69 |  | 40 | 0.012 | Test results satisfactory.
33000 | 1949 | 62 | 232 | 41.81 | 194 | 1489 | 0 | 3 | 24 | 2 | 9 | 24 | 0.068 | 55 |  | 11.4 | 0.021 | Test results satisfactory.
33000 | 1949 | 62 | 104 | 41.81 | 78 | 845 | 16 | 2 | 7 | 1 | 0 | 18 | 0.089 | 62 |  | 9.6 | 0.022 | Test results are assessed as acceptable.
33000 | 1949 | 62 | 8.5 | 25 | 8.2 | 152.1 | 0 | 0.3 | 0 | 0 | 0 | 6 | 0.01 | 38 |  | 53 | 0.011 | The test results are assessed as acceptable.
33000 | 1949 | 62 | 15.8 | 41.81 | 11.7 | 343.4 | 0 | 1.4 | 1.8 | 0.3 | 0.6 | 3 | 0.01 | 75 |  | 39 | 0.014 | The test results are assessed as acceptable.
33000 | 1949 | 62 | 33.9 | 41.81 | 4.6 | 271.6 | 2.8 | 2.7 | 3.1 | 1 | 19.7 | 14 | 0.01 | 45 |  | 39 | 0.019 | The test results are assessed as acceptable.
33000 | 1949 | 62 | 72 | 41.81 | 54.3 | 969.7 | 1.6 | 2.3 | 3.2 | 1.6 | 9 | 9 | 0.01 | 75 |  | 26 | 0.014 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1949 | 62 | 107.4 | 41.81 | 83.3 | 1339.8 | 5.2 | 3 | 3.3 | 2 | 10.6 | 6 | 0.01 | 75 |  | 24 | 0.01293 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1949 | 62 | 65.3 | 41.81 | 49.6 | 1044.5 | 4.8 | 2.3 | 2 | 1.7 | 4.9 | 5 | 0.01 | 75 |  | 24 | 0.013 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable. Corrosive IEC. Corrosive ASTM 4A.
33000 | 1949 | 62 | 53.3 | 20 | 45.8 | 1043.3 | 0 | 2.2 | 1.7 | 1.2 | 2.4 | 6 | 0.007 | 89 |  | 20 | 0.014 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1949 | 62 | 224 | 41.81 | 199 | 3437 | 0 | 6 | 15 | 4 | 0 | 24 | 0.033 | 46 |  | 21.8 | 0.023 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1949 | 62 | 270 | 41.81 | 240 | 3356 | 6 | 6 | 15 | 3 | 0 | 22 | 0.037 | 54 |  | 20.4 | 0.013 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1949 | 62 | 392.4 | 41.81 | 334.2 | 4458.2 | 10.2 | 8.1 | 31.5 | 8.4 | 0 | 19 | 0.052 | 49 |  | 12 | 0.022 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1949 | 62 | 356.6 | 41.81 | 311 | 5313.7 | 8.6 | 7.1 | 24.3 | 5.6 | 0 | 28 | 0.053 | 36 |  | 12 | 0.022 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1949 | 62 | 304.7 | 41.81 | 264.5 | 4638.8 | 7.5 | 8.1 | 21.3 | 3.3 | 0 | 25 | 0.062 | 40 |  | 11 | 0.023 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1949 | 62 | 298.8 | 41.81 | 258.6 | 3656.7 | 7.8 | 8.2 | 19.1 | 5.1 | 0 | 24 | 0.064 | 39 |  | 8 | 0.04 | DGA is assessed as acceptable. | Breakdown voltage is low. Other oil quality results are assessed as acceptable. Corrosive IEC. Non-corrosive ASTM 3B.
33000 | 1949 | 62 | 230.4 | 22 | 198.8 | 3039.8 | 3.2 | 8.6 | 15.2 | 4.6 | 0 | 28 | 0.06 | 66 |  | 13 | 0.019 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1949 | 62 | 350.7 | 27 | 303.1 | 4604.7 | 9.3 | 9.2 | 22.3 | 6.8 | 0 | 64 | 0.066 | 52 |  | 8 | 0.028 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1949 | 62 | 269.1 | 27 | 225 | 4378.9 | 7.9 | 9.7 | 20.3 | 6.2 | 0 | 22 | 0.074 | 37 |  | 12 | 0.021 | DGA is assessed as acceptable. | Breakdown voltage is low. Other oil quality results are assessed as acceptable.
33000 | 1948 | 63 | 198 | 41.81 | 49 | 2720 | 137 | 4 | 5 | 2 | 1 | 29 | 0.365 | 45 |  | 7 | 0.028 | DGA satisfactory. Acidity level slightly high.
33000 | 1948 | 63 | 315 | 41.81 | 279 | 4600 | 19 | 7 | 6 | 3 | 1 | 35 | 0.425 | 38 |  | 8 | 0.037 | D.G.A. Satisfactory. Acidity level getting high.
33000 | 1948 | 63 | 481 | 41.81 | 426 | 7850 | 36 | 10 | 5 | 4 | 0 | 36 | 0.459 | 51 |  | 6.9 | 0.036 | Moisture and acidity levels of oil high. Other test results satisfactory.
33000 | 1948 | 63 | 8 | 41.81 | 6 | 388 | 0 | 1 | 1 | 0 | 0 | 15 | 0.017 | 60 |  | 38.4 | 0.014 | Test results satisfactory. OIL CHANGED.
33000 | 1948 | 63 | 332 | 41.81 | 274 | 8197 | 27 | 8 | 20 | 3 | 0 | 44 | 0.088 | 25 |  | 20.8 | 0.013 | Moisture content of oil is high. 2-Furfural level is above 1PPM. Other test results are assessed as acceptable. RECOMMEND RESAMPLE IN 1 YEAR TO MONITOR TREND IN CARBON OXIDE GASES AND 2-FURFURAL LEVEL.
33000 | 1948 | 63 | 120.5 | 41.81 | 95.8 | 4065.4 | 3.6 | 3.6 | 13.8 | 3.7 | 0 | 17 | 0.129 | 39 |  | 11 | 0.026 | 2-furfural level is high and trending upwards suggesting accelerated rate of insulation degradation. Other test results are assessed as acceptable. RECOMMEND RESAMPLE IN 6 MONTHS TO MONITOR CONDITION. Note sample received approximately one month after
33000 | 1948 | 63 | 211.7 | 41.81 | 188.6 | 4272.9 | 4.5 | 4.2 | 11.8 | 2.3 | 0.3 | 34 | 0.108 | 33 |  | 12.2 | 0.024 | DGA is assessed as acceptable. | Moisture content is high. Other oil quality results are assessed as acceptable.
33000 | 1948 | 63 | 109.8 | 41.81 | 92.9 | 2423.3 | 5.3 | 2.3 | 7.1 | 2.2 | 0 | 25 | 0.114 | 37 |  | 9 | 0.026 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1948 | 63 | 142.9 | 41.81 | 123.7 | 2902 | 5.8 | 3 | 8.4 | 1 | 1 | 24 | 0.176 | 43 |  | 10 | 0.023 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1948 | 63 | 185.9 | 41.81 | 164.2 | 2898.7 | 4.3 | 7.4 | 8.4 | 1.6 | 0 | 22 | 0.139 | 69 |  | 10 | 0.028 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable. Corrosive IEC. Corrosive ASTM 4A.
33000 | 1948 | 63 | 160.5 | 20 | 146.5 | 3004.8 | 0 | 3.9 | 8.4 | 1.7 | 0 | 22 | 0.148 | 48 |  | 9 | 0.029 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1948 | 63 | 18.1 | 26 | 9 | 824.4 | 6.2 | 0.9 | 1.3 | 0.7 | 0 | 23 | 0.012 | 24 |  | 42 | 0.01 | DGA is assessed as acceptable. | Breakdown voltage is low. Other oil quality results are assessed as acceptable.
33000 | 1948 | 63 | 398 | 41.81 | 333 | 7237 | 40 | 11 | 8 | 6 | 0 | 51 | 0.33 | 46 |  | 8.5 | 0.026 | DGA is assessed as acceptable. | Slightly high moisture level associated with acidity level. Other tests satisfactory.
33000 | 1948 | 63 | 390 | 45 | 339 | 7822 | 31 | 9 | 7 | 4 | 0 | 52 | 0.38 | 48 |  | 10.5 | 0.019 | DGA is assessed as acceptable. | Moisture and acidity levels are high. Other test results are satisfactory.
33000 | 1948 | 63 | 360 | 40 | 305 | 8271 | 37 | 8 | 6 | 4 | 0 | 64 | 0.398 | 34 |  | 8.7 | 0.027 | DGA is assessed as acceptable. | Acidity level is high. Moisture content is high.
33000 | 1947 | 64 | 220 | 25 | 208 | 4064 | 0 | 5 | 4 | 3 | 0 | 41 | 0.384 | 52 |  | 6.7 | 0.033 | Acidity quite high. Future oil change should be considered.
33000 | 1947 | 64 | 11 | 41.81 | 8 | 309 | 0 | 1 | 1 | 0 | 1 | 20 | 0.012 | 40 |  | 46.6 | 0.014 | Test results satisfactory. New or reconditioned oil
33000 | 1947 | 64 | 316 | 41.81 | 273 | 5952 | 16 | 7 | 16 | 4 | 0 | 35 | 0.069 | 41 |  | 24.9 | 0.014 | Moisture content of oil is slightly high. 2-Furfural level is 1ppm. Other test results are assessed as acceptable.
33000 | 1947 | 64 | 354.5 | 41.81 | 293.1 | 8534.6 | 18.4 | 9.8 | 26.5 | 6.7 | 0 | 33 | 0.112 | 27 |  | 15 | 0.017 | 2-furfural and carbon dioxide gas levels are high suggesting accelerated rate of insulation degradation. Moisture content of sample is high. Breakdown voltage of sample is low. Other test results are assessed as acceptable. RECOMMEND RESAMPLE IN 1 YEA
33000 | 1947 | 64 | 321.1 | 41.81 | 273.2 | 7626.9 | 12.7 | 8.3 | 22 | 4.9 | 0 | 33 | 0.112 | 38 |  | 13 | 0.02 | DGA is assessed as acceptable. | Moisture content is slightly high. Other oil quality results are assessed as acceptable.
33000 | 1947 | 64 | 198.4 | 41.81 | 168.4 | 3798.3 | 10.8 | 4.3 | 12.8 | 1.7 | 0.4 | 28 | 0.132 | 43 |  | 10 | 0.025 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1947 | 64 | 189.5 | 41.81 | 157 | 3669.7 | 15.5 | 2.3 | 11.9 | 2.8 | 0 | 22 | 0.136 | 23 |  | 12 | 0.025 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable. Corrosive IEC. Non-corrosive ASTM 2C.
33000 | 1947 | 64 | 208.5 | 22 | 187.9 | 4010.1 | 0 | 5.5 | 11.5 | 3.6 | 0 | 26 | 0.149 | 51 |  | 10 | 0.023 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1947 | 64 | 219 | 23 | 190.1 | 3934.5 | 6.2 | 6.5 | 13.5 | 2.7 | 0 | 28 | 0.153 | 35 |  | 9 | 0.026 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1947 | 64 | 467 | 41.81 | 402 | 3172 | 53 | 6 | 3 | 3 | 0 | 36 | 0.351 | 55 |  | 4.6 | 0.04 | DGA is assessed as acceptable. | Acidity level is high. Moisture content of oil is slightly high. Other test results are assessed as acceptable.
33000 | 1947 | 64 | 384 | 40 | 340 | 3900 | 27 | 8 | 4 | 5 | 0 | 49 | 0.333 | 23 |  | 5 | 0.045 | DGA is assessed as acceptable. | Moisture and acidity levels are high. Other test results are assessed as acceptable.
33000 | 1947 | 64 | 607.8 | 41.81 | 548.2 | 7003 | 37.6 | 9.4 | 6.4 | 6.2 | 0 | 59 | 0.363 | 14 |  | 4 | 0.052 | Dissolved gas analysis is assessed as acceptable. | Breakdown voltage of sample is low. Moisture content of sample is high. Acidity level of sample is high.
33000 | 1947 | 64 | 484.3 | 41.81 | 427.6 | 5894.6 | 34 | 10 | 6.5 | 6.2 | 0 | 48 | 0.31 | 19 |  | 4 | 0.054 | DGA is assessed as acceptable. | Oil quality is poor. Sample is cloudy in appearance.
33000 | 1947 | 64 | 545 | 41.81 | 459.1 | 6440 | 63.4 | 8.9 | 6.3 | 7.1 | 0.2 | 43 | 0.336 | 36 |  | 5 | 0.043 | DGA is assessed as acceptable. | Acidity level is high. Moisture content is high. Other oil quality results are assessed as acceptable.
33000 | 1947 | 64 | 463.7 | 41.81 | 377.4 | 5539.7 | 66.4 | 7.8 | 5.8 | 6.3 | 0 | 39 | 0.326 | 34 |  | 5 | 0.039 | DGA is assessed as acceptable. | Oil quality is poor.
33000 | 1947 | 64 | 547.7 | 24 | 456.8 | 6026.2 | 70.7 | 9.4 | 4.7 | 6.1 | 0 | 38 | 0.359 | 28 |  | 4 | 0.056 | DGA is assessed as acceptable. | Acidity level is high. Breakdown voltage is low. DDF and Resistivity are assessed as acceptable. Corrosive IEC. Non-corrosive ASTM 3B.
33000 | 1947 | 64 | 474.8 | 34 | 398.4 | 5903.3 | 57.8 | 7.3 | 4.8 | 6.5 | 0 | 39 | 0.373 | 26 |  | 5 | 0.045 | DGA is assessed as acceptable. | Acidity level is high. Breakdown voltage is low. DDF and Resistivity are assessed as acceptable.
33000 | 1947 | 64 | 439.1 | 30 | 369.6 | 5717.2 | 49 | 8.1 | 5.9 | 6.5 | 0 | 37 | 0.393 | 32 |  | 5 | 0.043 | DGA is assessed as acceptable. | Oil quality is poor.
33000 | 1947 | 64 | 360.9 | 30 | 308.3 | 4833.4 | 35.4 | 7.4 | 4 | 5.8 | 0 | 42 | 0.359 | 27 |  | 6 | 0.036 | DGA is assessed as acceptable. | Oil quality is poor.
33000 | 1947 | 64 | 706 | 41.81 | 354 | 5566 | 20 | 58 | 220 | 53 | 1 | 32 | 0.165 | 41 |  | 5.1 | 0.048 | Dissolved gas analysis suggests hot spot in oil. | Moisture content of oil slightly high. Other test results are assessed as acceptable.
33000 | 1947 | 64 | 714 | 41.81 | 360 | 7400 | 26 | 65 | 196 | 67 | 0 | 39 | 0.175 | 39 |  | 6 | 0.036 | Dissolved gas analysis is relatively stable. | Moisture content of oil is high. Other test results are assessed as acceptable.
33000 | 1947 | 64 | 2984.2 | 41.81 | 367.4 | 7236.6 | 100.4 | 510.8 | 1675.2 | 317 | 13.4 | 34 | 0.161 | 36 |  | 5 | 0.045 | DGA suggests high temperature oil overheating has occurred. | Moisture content is slightly high. Other oil quality results are assessed as acceptable.
33000 | 1947 | 64 | 3050.8 | 41.81 | 309.1 | 8098.4 | 55 | 420.8 | 1904.3 | 346.4 | 15.2 | 26 | 0.182 | 62 |  | 5 | 0.042 | Dissolved hydrocarbon gas levels are increasing. DGA suggests high temperature oil overheating has occurred. | Oil quality is assessed as acceptable.
33000 | 1947 | 64 | 2770 | 35 | 335.2 | 7733.8 | 30.5 | 294.1 | 1755 | 355.2 | 0 | 30 | 0.19 | 33 |  | 6 | 0.036 | DGA suggests high temperature oil overheating has occurred. | Breakdown voltage is slightly low. Moisture content is slightly high. Other oil quality results are assessed as acceptable at present.
33000 | 1947 | 64 | 662.8 | 26 | 357.4 | 6940.4 | 14.9 | 19.4 | 191.8 | 78.5 | 0.8 | 28 | 0.18 | 66 |  | 5 | 0.044 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable. Corrosive IEC. Non-corrosive ASTM 3B.
33000 | 1947 | 64 | 994.9 | 26 | 325 | 7958.6 | 21.6 | 91.2 | 431 | 126.1 | 0 | 32 | 0.169 | 26 |  | 6 | 0.04 | DGA suggests high temperature oil overheating (300-700°C) has occurred. | Breakdown voltage is low. Other oil quality results are assessed as acceptable.
33000 | 1947 | 64 | 564.8 | 27 | 314.4 | 6943.5 | 12.6 | 29.3 | 143.8 | 64.2 | 0.5 | 44 | 0.156 | 25 |  | 3 | 0.073 | DGA suggests high temperature oil overheating (300-700°C) has occurred. | Breakdown voltage is low. Other oil quality results are assessed as acceptable.
33000 | 1947 | 64 | 4804 | 41.81 | 1380 | 4499 | 1364 | 709 | 490 | 133 | 728 | 28 | 0.041 | 28 |  | 180 | 0.0079 | Noted.
33000 | 1947 | 64 | 67 | 41.81 | 13 | 246 | 9 | 8 | 18 | 2 | 17 | 27 | 0.027 | 41 |  | 70 | 0.0157 | Noted.
33000 | 1947 | 64 | 219 | 41.81 | 183 | 2817 | 0 | 3 | 31 | 2 | 0 | 14 | 0.038 | 51 |  | 30 | 0.0191 | Test results satisfactory.
33000 | 1947 | 64 | 25 | 41.81 | 2 | 561 | 0 | 0 | 1 | 1 | 21 |  | 0.07 | 23 |  | 13 | 0.02 | D.G.A. Indicates circulating currents causing overheating.
33000 | 1947 | 64 | 1979 | 41.81 | 1269 | 8512 | 279 | 138 | 20 | 199 | 74 |  | 0.1206 | 20 |  | 13 | 0.022 | D.G.A. Indicates circulating currents causing over heating.
33000 | 1947 | 64 | 276 | 41.81 | 237 | 3485 | 0 | 4 | 33 | 2 | 0 | 19 | 0.041 | 67 |  | 15 | 0.0268 | Test results satisfactory.
33000 | 1947 | 64 | 289 | 41.81 | 237 | 4355 | 0 | 4 | 44 | 3 | 1 | 17 | 0.06 | 43 |  | 27.6 | 0.014 | Test results satisfactory.
33000 | 1947 | 64 | 379 | 44 | 311 | 7146 | 3 | 5 | 56 | 4 | 0 | 27 | 0.07 | 70 |  | 13.8 | 0.02 | Test results are assessed as acceptable.
33000 | 1947 | 64 | 362 | 22 | 289 | 7671 | 8 | 5 | 56 | 4 | 0 | 19 | 0.06 | 55 |  | 15.7 | 0.02 | Test results are assessed as acceptable. EX MALENY.
33000 | 1947 | 64 | 394.5 | 33 | 311.7 | 6101.8 | 6.4 | 5.9 | 65 | 5.5 | 0 | 30 | 0.116 | 34 |  | 8 | 0.0322 | Moisture content of sample is high. Other test results are assessed as acceptable. RECOMMEND RESAMPLE IN 1 YEAR TO MONITOR TREND.
33000 | 1946 | 65 | 984 | 41.81 | 765 | 6391 | 149 | 26 | 18 | 25 | 1 | 38 | 0.334 | 70.8 |  | 1.5 | 0.209 | Loss tangent of oil poor. Acidity quite high. D.G.A. Satisfactory.
33000 | 1946 | 65 | 879 | 41.81 | 696 | 5926 | 112 | 23 | 19 | 28 | 1 | 45 | 0.3 | 56.8 |  | 1.5 | 0.192 | DGA satisfactory.
33000 | 1946 | 65 | 870 | 41.81 | 702 | 5729 | 122 | 17 | 15 | 13 | 1 | 57 | 0.33 | 32 |  | 2 | 0.165 | DGA stable. Acidity quite high.
33000 | 1946 | 65 | 727 | 41.81 | 592 | 5544 | 91 | 18 | 13 | 13 | 0 | 36 | 0.311 | 26 |  | 1.2 | 0.235 | Poor oil quality. DGA satisfactory.
33000 | 1946 | 65 | 782 | 41.81 | 546 | 6121 | 170 | 12 | 14 | 5 | 35 | 41 | 0.305 | 47 |  | 0.41 | 0.828 | Oil quality very poor. Oil change should be considered. RECOMMEND RESAMPLE IN 1 YEAR.
33000 | 1946 | 65 | 705 | 41.81 | 582 | 6959 | 96 | 10 | 11 | 4 | 2 | 66 | 0.349 | 38 |  | 0.387 | 0.878 | Oil quality very poor. Oil change recommended. DGA satisfactory at present RECOMMEND RESAMPLE IN 1 YEAR.
33000 | 1946 | 65 | 656 | 41.81 | 554 | 8754 | 74 | 10 | 12 | 5 | 1 | 68 | 0.394 | 43 |  | 0.25 | 1.001 | Oil quality very poor. Oil change recommended. RECOMMEND RESAMPLE IN 1 YEAR.
33000 | 1946 | 65 | 664 | 41.81 | 538 | 7827 | 102 | 9 | 10 | 4 | 1 | 76 | 0.342 | 34 |  | 0.256 | 0.954 | Oil quality poor. Oil change is recommended. RECOMMEND RESAMPLE IN 1 YEAR TO MONITOR.
33000 | 1946 | 65 | 1098.8 | 46 | 799.9 | 10407 | 225.9 | 35.5 | 22.8 | 14.6 | 0.1 | 64 | 0.402 | 18 |  | 0.172 | 1.683 | The test results suggest advanced rate of insulation degradation. FUTURE OIL CHANGE IS RECOMMENDED.
33000 | 1946 | 65 | 1206.6 | 55 | 813 | 11471.9 | 276.8 | 62.5 | 26.3 | 27.8 | 0.2 | 96 | 0.447 | 18 |  | 0.13861 | 2.0317 | The test results are consistent with main tank sample. Oil quality is outside acceptance limits. Carbon dioxide level is high.
33000 | 1946 | 65 | 1610 | 55 | 931.9 | 12419 | 559.2 | 64.4 | 27.9 | 26.6 | 0 | 88 | 0.431 | 12 |  | 0.12293 | 2.3804 | 2-furfural and carbon dioxide levels are high suggesting advanced state of insulation degradation. Oil quality is outside acceptance limits. RECOMMEND OIL CHANGE / TREATMENT. RECOMMEND RESAMPLE IN 1 YEAR TO MONITOR CONDITION.
33000 | 1945 | 66 | 3359 | 41.81 | 1081 | 5567 | 467 | 347 | 767 | 87 | 610 | 28 | 0.149 | 61 |  | 3.4 | 0.11 | High level of hydrocarbon gases suggest internal fault. High carbon monoxide suggests possible insulation overheat.
33000 | 1945 | 66 | 280 | 42 | 233 | 3508 | 7 | 5 | 32 | 3 | 0 | 35 | 0.17 | 46 |  | 5 | 0.048 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1945 | 66 | 445 | 41.81 | 372 | 5995 | 30 | 5 | 36 | 2 | 0 | 54 | 0.245 | 14 |  | 5.8 | 0.037 | DGA is assessed as acceptable. | Oil quality is poor.
33000 | 1945 | 66 | 162 | 41.81 | 56 | 1147 | 0 | 12 | 21 | 2 | 71 | 22 | 0.024 | 44 |  | 46.6 | 0.009 | Acetylene level high. Possibly from tapchanger? Otherwise test results satisfactory.
33000 | 1945 | 66 | 122 | 41.81 | 103 | 1995 | 0 | 3 | 12 | 2 | 2 | 34 | 0.037 | 64 |  | 38.4 | 0.01 | Moisture content of oil slightly high. Other test results satisfactory.
33000 | 1945 | 66 | 136 | 41.81 | 120 | 2104 | 0 | 3 | 11 | 2 | 0 | 21 | 0.035 | 75 |  | 48.6 | 0.007 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1945 | 66 | 170 | 41.81 | 142.6 | 2781.6 | 3.3 | 2.9 | 17.7 | 3.5 | 0 | 23 | 0.044 | 37 |  | 27 | 0.01 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1945 | 66 | 186 | 41.81 | 174 | 3556 | 0 | 4 | 4 | 3 | 1 | 39 | 0.308 | 57 |  | 9 | 0.024 | Acidity should be noted. Test results satisfactory.
33000 | 1945 | 66 | 197 | 41.81 | 156 | 4811 | 26 | 4 | 6 | 4 | 1 | 33 | 0.333 | 49 |  | 4.7 | 0.041 | Acidity level of oil high. Moisture content slightly high. Other test results satisfactory.
33000 | 1945 | 66 | 184 | 41.81 | 160 | 3471 | 8 | 4 | 7 | 5 | 0 | 37 | 0.362 | 37 |  | 8.7 | 0.026 | Acidity level is high. Moisture content of oil is high. 2-furfural level is above 1ppm. Other test results are assessed as acceptable.
33000 | 1945 | 66 | 281 | 41.81 | 199 | 2652 | 49 | 14 | 11 | 8 | 0 | 32 | 0.353 | 62 |  | 9.2 | 0.025 | DGA is assessed as acceptable. | Acidity level of oil is high. Other test results are assessed as acceptable.
33000 | 1945 | 66 | 378.4 | 41.81 | 263.7 | 3981.4 | 73.1 | 14.4 | 12.5 | 14.7 | 0 | 34 | 0.364 | 35 |  | 8 | 0.026 | Dissolved gas analysis is assessed as acceptable. | Moisture content of sample is high. Acidity level of sample is high.
33000 | 1945 | 66 | 318.2 | 41.81 | 244.8 | 4075.8 | 30.9 | 20.2 | 10.8 | 11.5 | 0 | 33 | 0.373 | 37 |  | 8 | 0.026 | DGA is assessed as acceptable. | Acidity level is high. Other oil quality results are assessed as acceptable.
33000 | 1945 | 66 | 444.5 | 41.81 | 350 | 4989.2 | 41.3 | 21.8 | 16.2 | 15 | 0.2 | 34 | 0.344 | 38 |  | 8 | 0.03 | DGA is assessed as acceptable. | Acidity level is high. Other oil quality results are assessed as acceptable.
33000 | 1945 | 66 | 385.6 | 41.81 | 304.8 | 4664.7 | 43.5 | 11.9 | 13.4 | 12 | 0 | 32 | 0.418 | 34 |  | 8 | 0.03 | DGA is assessed as acceptable. | Acidity level is high. Breakdown voltage is slightly low. Other oil quality results are assessed as acceptable.
33000 | 1945 | 66 | 418.3 | 23 | 329.2 | 4550 | 64.3 | 10.4 | 6.6 | 7.8 | 0 | 34 | 0.437 | 64 |  | 6 | 0.054 | DGA is assessed as acceptable. | Acidity level is high. Other oil quality results are assessed as acceptable. Non-corrosive IEC. Non-corrosive ASTM 3B.
33000 | 1945 | 66 | 317.5 | 20 | 261.7 | 3870.8 | 37.8 | 6.1 | 5.1 | 6.8 | 0 | 28 | 0.427 | 52 |  | 8 | 0.027 | DGA is assessed as acceptable. | Acidity level is high. Other oil quality results are assessed as acceptable.
33000 | 1945 | 66 | 304.9 | 22 | 252.3 | 3423.6 | 27.8 | 9.5 | 6.7 | 8.3 | 0.3 | 27 | 0.438 | 42 |  | 6 | 0.037 | DGA is assessed as acceptable. | Acidity level is high. Other oil quality results are assessed as acceptable.
33000 | 1945 | 66 | 255 | 41.81 | 167 | 2203 | 16 | 18 | 43 | 11 | 0 | 24 | 0.226 | 73 |  | 9.4 | 0.024 | DGA is assessed as acceptable. | Acidity level is high. Other test results are assessed as acceptable.
33000 | 1945 | 66 | 317 | 41.81 | 205 | 3396 | 20 | 20 | 50 | 15 | 7 | 24 | 0.247 | 52 |  | 7.3 | 0.03 | DGA is assessed as acceptable. | Acidity level is high. Other test results are assessed as acceptable.
33000 | 1945 | 66 | 357.8 | 41.81 | 265.4 | 3785.1 | 19.3 | 13.2 | 34.6 | 14.7 | 10.6 | 28 | 0.242 | 39 |  | 7 | 0.029 | DGA is assessed as acceptable. | Acidity level of sample is high. Other test results are assessed as acceptable.
33000 | 1945 | 66 | 384.5 | 41.81 | 212 | 3476.5 | 14.3 | 25.9 | 97.8 | 28.3 | 6.2 | 26 | 0.251 | 49 |  | 7 | 0.03 | Ethylene level is increasing. | Acidity level is high. Other oil quality results are assessed as acceptable.
33000 | 1945 | 66 | 328.6 | 41.81 | 241.9 | 3200 | 23.3 | 8.9 | 34.6 | 16.6 | 3.3 | 28 | 0.226 | 47 |  | 6 | 0.044 | DGA is assessed as acceptable. | Acidity level is high. Other oil quality results are assessed as acceptable.
33000 | 1945 | 66 | 203.4 | 41.81 | 156.4 | 2509.2 | 10.2 | 8 | 18.3 | 7.6 | 2.9 | 24 | 0.255 | 53 |  | 8 | 0.029 | DGA is assessed as acceptable. | Acidity level is high. Other oil quality results are assessed as acceptable.
33000 | 1945 | 66 | 302.6 | 23 | 235.6 | 3121.3 | 17 | 10.1 | 19.2 | 5.7 | 15 | 28 | 0.301 | 75 |  | 6 | 0.034 | DGA is assessed as acceptable. | Acidity level is high. Other oil quality results are assessed as acceptable. Non-corrosive IEC. Non-corrosive ASTM 3B.
33000 | 1945 | 66 | 191.5 | 20 | 157.6 | 2581.4 | 10.8 | 3.5 | 7.6 | 5.3 | 6.7 | 28 | 0.277 | 56 |  | 7 | 0.029 | DGA is assessed as acceptable. | Acidity level is high. Other oil quality results are assessed as acceptable.
33000 | 1945 | 66 | 210.7 | 22 | 174.3 | 2464.6 | 13.8 | 5.5 | 5.5 | 4.3 | 7.3 | 25 | 0.277 | 78 |  | 7 | 0.027 | DGA is assessed as acceptable. | Acidity level is high. Other oil quality results are assessed as acceptable.
33000 | 1945 | 66 | 310 | 41.81 | 258 | 3056 | 22 | 12 | 12 | 6 | 0 | 40 | 0.39 | 54 |  | 6.5 | 0.035 | DGA is assessed as acceptable. | Moisture and acidity levels are high. Other test results are assessed as acceptable.
33000 | 1945 | 66 | 415 | 41.81 | 340.4 | 4862.6 | 31.5 | 15.3 | 14.8 | 12.8 | 0.2 | 35 | 0.418 | 27 |  | 5 | 0.04 | Dissolved gas analysis is assessed as acceptable. | Breakdown voltage of sample is low. Moisture content of sample is high. Acidity level of sample is high.
33000 | 1945 | 66 | 347.4 | 41.81 | 246.8 | 4057.6 | 22 | 29.6 | 26.7 | 13.5 | 8.8 | 32 | 0.429 | 38 |  | 5.3 | 0.044 | DGA is assessed as acceptable. | Acidity level is high. Other oil quality results are assessed as acceptable.
33000 | 1945 | 66 | 400.7 | 41.81 | 306.7 | 3954.6 | 39.2 | 17.2 | 22.4 | 14.9 | 0.3 | 34 | 0.406 | 65 |  | 6 | 0.039 | DGA is assessed as acceptable. | Acidity level is high. Other oil quality results are assessed as acceptable.
33000 | 1945 | 66 | 271 | 41.81 | 213.1 | 3049.6 | 20 | 12.6 | 15.4 | 9.9 | 0 | 26 | 0.416 | 63 |  | 6 | 0.041 | DGA is assessed as acceptable. | Acidity level is high but stable. Other oil quality results are assessed as acceptable.
33000 | 1945 | 66 | 314.6 | 23 | 275.3 | 3816.4 | 19.2 | 8.8 | 4.8 | 6.5 | 0 | 32 | 0.502 | 52 |  | 5 | 0.045 | DGA is assessed as acceptable. | Acidity level is high. Other oil quality results are assessed as acceptable. Non-corrosive IEC. Non-corrosive ASTM 3B.
33000 | 1945 | 66 | 269.9 | 20 | 226.4 | 3346.1 | 17.6 | 7.3 | 10.6 | 8 | 0 | 24 | 0.454 | 49 |  | 5 | 0.04 | DGA is assessed as acceptable. | Acidity level is high. Other oil quality results are assessed as acceptable.
33000 | 1945 | 66 | 249.4 | 22 | 209.6 | 3036.5 | 17.3 | 8.7 | 6.6 | 6.8 | 0.4 | 26 | 0.479 | 51 |  | 5 | 0.039 | DGA is assessed as acceptable. | Acidity level is high. Other oil quality results are assessed as acceptable.
33000 | 1945 | 66 | 50 | 41.81 | 40 | 970 | 0 | 1 | 8 | 1 | 0 | 18 | 0.059 | 74 |  | 8.9 | 0.034 | DGA is assessed as acceptable.
33000 | 1945 | 66 | 275 | 41.81 | 240 | 3612 | 10 | 4 | 19 | 2 | 0 | 27 | 0.061 | 36 |  | 7.6 | 0.028 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1944 | 67 | 537 | 41.81 | 421 | 7126 | 86 | 9 | 14 | 7 | 0 | 54 | 0.671 | 61 |  | 8 | 0.034 | Acidity very high. Oil change should be considered.
33000 | 1944 | 67 | 486 | 41.81 | 410 | 8284 | 51 | 8 | 11 | 6 | 0 | 58 | 0.756 | 55 |  | 3.2 | 0.067 | Moisture and acidity levels extremely high. RECOMMEND OIL CHANGE.
33000 | 1944 | 67 | 210 | 41.81 | 154 | 2267 | 0 | 4 | 50 | 2 | 0 | 22 | 0.122 | 66.6 |  | 4.5 | 0.0549 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1944 | 67 | 274 | 41.81 | 216 | 3210 | 0 | 4 | 51 | 3 | 0 | 17 | 0.166 | 68 |  | 4.8 | 0.054 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1944 | 67 | 271 | 41.81 | 190 | 2859 | 4 | 3 | 29 | 45 | 0 | 26 | 0.183 | 69 |  | 4.5 | 0.055 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1944 | 67 | 180 | 41.81 | 136 | 1703 | 10 | 2 | 30 | 2 | 0 | 19 | 0.21 | 63 |  | 4 | 0.059 | The test results are assessed as acceptable. EX FLINDERS.
33000 | 1944 | 67 | 181.9 | 33 | 140.6 | 2132.5 | 5.1 | 2.2 | 31.4 | 2.2 | 0.4 | 23 | 0.205 | 54 |  | 3 | 0.06 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1944 | 67 | 155.9 | 41.81 | 116.6 | 1902 | 7 | 1.9 | 27.9 | 2.1 | 0.4 | 19 | 0.22 | 75 |  | 4 | 0.06 | Acidity level of sample is high but stable. Other test results are assessed as acceptable. RECOMMEND RESAMPLE IN 2 YEARS TO MONITOR TREND.
33000 | 1944 | 67 | 177.1 | 41.81 | 144.3 | 1857.1 | 5.6 | 2.3 | 23.1 | 1.7 | 0.1 | 18 | 0.212 | 75 |  | 3.8 | 0.065 | The test results are assessed as relatively stable and assessed as acceptable for transformer age. RECOMMEND RESAMPLE IN 2 YEARS TO MONITOR CONDITION.
33000 | 1944 | 67 | 199.4 | 41.81 | 170.6 | 1884 | 4.3 | 2 | 21.1 | 1.4 | 0 | 20 | 0.197 | 75 |  | 4 | 0.057 | DGA is assessed as acceptable. | Acidity level is high but stable . Other oil quality results are assessed as acceptable.
33000 | 1944 | 67 | 194.4 | 41.81 | 144.4 | 2018 | 26.1 | 2.1 | 20.5 | 1.3 | 0 | 17 | 0.325 | 75 |  | 4 | 0.0567 | DGA is assessed as acceptable. | Acidity level is high. Other oil quality results are assessed as acceptable.
33000 | 1944 | 67 | 225.9 | 41.81 | 190.2 | 2070.4 | 4.7 | 8.1 | 21.4 | 1.5 | 0 | 18 | 0.256 | 75 |  | 4 | 0.064 | DGA is assessed as acceptable. | Acidity level is high but stable. Other oil quality results are assessed as acceptable. Corrosive IEC. Corrosive ASTM 2C.
33000 | 1944 | 67 | 12 | 22 | 9.2 | 870.4 | 0 | 0.9 | 0.6 | 1.3 | 0 | 22 | 0.002 | 28 |  | 135 | 0.004 | Dissolved gas levels are reduced. DGA is assessed as acceptable. | Breakdown voltage is low. Other oil quality results are assessed as acceptable.
33000 | 1944 | 67 | 10.8 | 27 | 7 | 894 | 1.3 | 1.1 | 0.5 | 0.9 | 0 | 24 | 0.001 | 30 |  | 626 | 0.001 | DGA is assessed as acceptable. | Breakdown voltage is low. Other oil quality results are assessed as acceptable.
33000 | 1944 | 67 | 932 | 41.81 | 793 | 8785 | 105 | 18 | 8 | 8 | 0 | 45 | 0.491 | 35 |  | 11.1 | 0.02 | Acidity and moisture levels are high. 2-furfural level is above 1ppm. Other test results are assessed as acceptable.
33000 | 1944 | 67 | 1044.4 | 41.81 | 839.7 | 10907.6 | 153.6 | 25 | 12.3 | 13.8 | 0 | 38 | 0.523 | 32 |  | 11 | 0.02 | Moisture content of sample is high. Acidity level of sample is high. Carbon dioxide level is high. 2-furfural level is high suggesting accelerated rate of insulation degradation. RECOMMEND RESAMPLE IN 1 YEAR TO MONITOR CONDITION.
33000 | 1944 | 67 | 1093.6 | 41.81 | 867 | 10457.3 | 184.3 | 20.6 | 10.6 | 11.1 | 0 | 45 | 0.515 | 29 |  | 8.7 | 0.029 | DGA is assessed as acceptable. | Oil quality is very poor.
33000 | 1944 | 67 | 216.6 | 41.81 | 160.1 | 5455.1 | 34.8 | 8.9 | 6.2 | 6.6 | 0 | 34 | 0.55 | 48 |  | 8 | 0.029 | DGA is assessed as acceptable. | Oil quality is poor.
33000 | 1944 | 67 | 543 | 41.81 | 456.8 | 5060.8 | 50.1 | 21.3 | 5.6 | 9.2 | 0 | 25 | 0.397 | 40 |  | 9 | 0.027 | DGA is assessed as acceptable. | Acidity level is high. Other oil quality results are assessed as acceptable. Corrosive IEC. Corrosive ASTM 4B.
33000 | 1944 | 67 | 538.9 | 41.81 | 470.1 | 5269.6 | 42.2 | 13 | 5 | 8.6 | 0 | 27 | 0.433 | 46 |  | 8 | 0.027 | DGA is assessed as acceptable. | Acidity level is high. Other oil quality results are assessed as acceptable.
33000 | 1944 | 67 | 602.6 | 23 | 522.1 | 4956.5 | 47.2 | 18.5 | 5.6 | 9.2 | 0 | 33 | 0.445 | 36 |  | 8 | 0.025 | DGA is assessed as acceptable. | Acidity level is high. Other oil quality results are assessed as acceptable.
33000 | 1943 | 68 | 314 | 26 | 260 | 3136 | 0 | 3 | 38 | 2 | 11 | 21 | 0.079 | 59 |  | 11.9 | 0.025 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1943 | 68 | 207 | 50 | 174 | 1849 | 6 | 2 | 19 | 1 | 5 | 30 | 0.088 | 31 |  | 8.6 | 0.027 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1943 | 68 | 259 | 40 | 200.7 | 2982.3 | 4.8 | 3.3 | 36.6 | 3 | 10.6 | 20 | 0.123 | 57 |  | 6 | 0.035 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1943 | 68 | 217.6 | 41 | 186.4 | 1811.2 | 7.8 | 2.5 | 15.8 | 2 | 3.1 | 27 | 0.115 | 41 |  | 6 | 0.035 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1943 | 68 | 189.3 | 41.81 | 166.5 | 1649.3 | 6.9 | 2.2 | 11.9 | 0.3 | 1.5 | 23 | 0.114 | 75 |  | 6 | 0.039 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1943 | 68 | 169.2 | 38 | 147.1 | 1649.3 | 5.3 | 2.1 | 13.3 | 1.4 | 0 | 16 | 0.124 | 56 |  | 7 | 0.037 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable. Corrosive IEC. Non-corrosive ASTM 3B.
33000 | 1943 | 68 | 225.5 | 44 | 192.9 | 2499.6 | 8.2 | 2.8 | 19 | 2.6 | 0 | 57 | 0.143 | 46 |  | 7 | 0.035 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1943 | 68 | 755 | 50 | 589 | 13172 | 134 | 14 | 12 | 6 | 0 | 73 | 0.594 | 17 |  | 6 | 0.045 | DGA is assessed as acceptable. | Oil quality is poor.
33000 | 1943 | 68 | 718 | 41.81 | 572 | 15090 | 115 | 9 | 13 | 9 | 0 | 50 | 0.603 | 30 |  | 4.2 | 0.06 | Confirm extremly high acidity level. Oil replacement recommended. Note also very high CO2 level.
33000 | 1943 | 68 | 1344 | 41.81 | 819 | 23349 | 470 | 20 | 19 | 16 | 0 | 59 | 0.525 | 52 |  | 4.7 | 0.053 | Moisture and acidity levels of oil high. High level of CO2. RECOMMEND OIL CHANGE.
33000 | 1941 | 70 | 325 | 41.81 | 269 | 3190 | 31 | 4 | 19 | 2 | 0 | 29 | 0.104 | 62 |  | 11.5 | 0.02 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1941 | 70 | 385.9 | 41.81 | 331.8 | 4128.3 | 15.7 | 5.9 | 27.9 | 4.6 | 0 | 30 | 0.126 | 43 |  | 8 | 0.029 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1941 | 70 | 354.5 | 41.81 | 305.2 | 3688.6 | 17.6 | 4.6 | 23.6 | 3.5 | 0 | 24 | 0.11 | 51 |  | 8.4 | 0.031 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1941 | 70 | 251.8 | 41.81 | 205.5 | 2774.9 | 21.4 | 3.5 | 18 | 3.4 | 0 | 13 | 0.215 | 75 |  | 7 | 0.03163 | DGA is assessed as acceptable. | Acidity level is high. Other oil quality results are assessed as acceptable.
33000 | 1941 | 70 | 195.2 | 41.81 | 172.7 | 1969.2 | 5.8 | 1.4 | 12.6 | 2.7 | 0 | 17 | 0.145 | 43 |  | 8 | 0.033 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable. Corrosive IEC. Corrosive ASTM 4B.
33000 | 1941 | 70 | 186.9 | 20 | 165.8 | 2094.3 | 5.8 | 1.7 | 11.6 | 2 | 0 | 19 | 0.156 | 63 |  | 7 | 0.034 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1941 | 70 | 311 | 42 | 275 | 14183 | 0 | 5 | 28 | 3 | 0 | 57 | 0.225 | 33 |  | 5.5 | 0.045 | CO2 and moisture level quite high. Otherwise test results satisfactory.
33000 | 1941 | 70 | 229 | 41.81 | 203 | 9747 | 0 | 4 | 19 | 3 | 0 | 33 | 0.204 | 58 |  | 5.2 | 0.045 | CO2 level quite high. Suggests advanced insulation ageing.
33000 | 1941 | 70 | 388 | 41.81 | 329 | 3598 | 44 | 7 | 3 | 5 | 0 | 21 | 0.202 | 38 |  | 16 | 0.021 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1940 | 71 | 457 | 41.81 | 412 | 6684 | 0 | 5 | 38 | 2 | 0 | 33 | 0.056 | 58 |  | 20 | 0.016 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1940 | 71 | 541 | 41.81 | 474 | 9436 | 34 | 6 | 25 | 2 | 0 | 30 | 0.081 | 57 |  | 9.5 | 0.025 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1940 | 71 | 373 | 41.81 | 331 | 5822 | 22 | 4 | 14 | 2 | 0 | 34 | 0.083 | 63 |  | 15.8 | 0.017 | Moisture content of oil is above defect level. 2-furfural level is above 1ppm. Other test results are assessed as acceptable.
33000 | 1940 | 71 | 132 | 41.81 | 92 | 2757 | 0 | 1 | 38 | 1 | 0 | 18 | 0.136 | 69 |  | 2 | 0.14 | Test results satisfactory. | Oil quality is assessed as acceptable.
33000 | 1940 | 71 | 238 | 40 | 192 | 3462 | 0 | 2 | 42 | 2 | 0 | 24 | 0.144 | 47 |  | 1.8 | 0.149 | Test results satisfactory. | Oil quality is assessed as acceptable.
33000 | 1940 | 71 | 192 | 41.81 | 154 | 2766 | 0 | 2 | 34 | 2 | 0 | 22 | 0.154 | 58 |  | 2 | 0.138 | Test results satisfactory. | Oil quality is assessed as acceptable.
33000 | 1940 | 71 | 252 | 41.81 | 214 | 3086 | 0 | 3 | 32 | 2 | 1 | 29 | 0.179 | 62 |  | 2.8 | 0.089 | Test results satisfactory. | Oil quality is assessed as acceptable.
33000 | 1940 | 71 | 273 | 41.81 | 231 | 3407 | 0 | 3 | 37 | 2 | 0 | 29 | 0.211 | 61 |  | 3.4 | 0.086 | Test results satisfactory. | Oil quality is assessed as acceptable.
33000 | 1940 | 71 | 272.1 | 41.81 | 235.8 | 3796.4 | 4.1 | 2.5 | 27.9 | 1.8 | 0 | 34 | 0.222 | 47 |  | 3 | 0.076 | DGA is assessed as acceptable. | Moisture content is slightly high. Other oil quality results are assessed as acceptable.
33000 | 1940 | 71 | 308.5 | 31 | 265.3 | 4536 | 8.2 | 2.7 | 30.6 | 1.7 | 0 | 32 | 0.258 | 37 |  | 2 | 0.082 | DGA is assessed as acceptable. | Moisture content is slightly high. Acidity level is high. Other oil quality results are assessed as acceptable.
33000 | 1940 | 71 | 290.5 | 41.81 | 256.1 | 3866.8 | 5.6 | 2.7 | 24.6 | 1.5 | 0 | 28 | 0.263 | 33 |  | 3 | 0.086 | DGA is assessed as acceptable. | Acidity level is high. Breakdown voltage is low. DDF and Resistivity are assessed as acceptable.
33000 | 1940 | 71 | 321 | 30 | 270 | 3418 | 0 | 3 | 46 | 2 | 0 | 18 | 0.152 | 56 |  | 5 | 0.064 | Test results satisfactory. | Oil quality is assessed as acceptable.
33000 | 1940 | 71 | 387 | 41.81 | 276 | 2812 | 73 | 2 | 33 | 1 | 2 | 17 | 0.145 | 56 |  | 5.3 | 0.045 | Test results satisfactory. | Oil quality is assessed as acceptable.
33000 | 1940 | 71 | 392 | 41.81 | 321 | 2777 | 38 | 2 | 30 | 1 | 0 | 27 | 0.161 | 67 |  | 5.6 | 0.043 | Test results satisfactory. | Oil quality is assessed as acceptable.
33000 | 1940 | 71 | 347 | 41.81 | 296 | 2924 | 16 | 3 | 31 | 1 | 0 | 26 | 0.195 | 57 |  | 5.9 | 0.046 | Test results satisfactory. | Acidity level is high but stable. Other oil quality results are assessed as acceptable.
33000 | 1940 | 71 | 425.3 | 41.81 | 377 | 3880.5 | 11.8 | 3.1 | 31.5 | 1.9 | 0 | 27 | 0.196 | 50 |  | 4 | 0.05 | DGA is assessed as acceptable. | Acidity level is high but stable. Other oil quality results are assessed as acceptable.
33000 | 1940 | 71 | 433.7 | 31 | 375.7 | 4433.1 | 18.8 | 3.4 | 34 | 1.8 | 0 | 27 | 0.255 | 42 |  | 4 | 0.058 | DGA is assessed as acceptable. | Acidity level is high. Other oil quality results are assessed as acceptable.
33000 | 1940 | 71 | 445.5 | 41.81 | 393.2 | 4350.7 | 15.2 | 3.5 | 32.3 | 1.3 | 0 | 27 | 0.229 | 38 |  | 4 | 0.06 | DGA is assessed as acceptable. | Acidity level is high. Breakdown voltage is low. DDF and Resistivity are assessed as acceptable.
33000 | 1939 | 72 | 126 | 41.81 | 105 | 789 | 4 | 2 | 6 | 9 | 0 | 14 | 0.066 | 75 |  | 8.3 | 0.03 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1939 | 72 | 115.6 | 23 | 100 | 851.9 | 7.2 | 1.5 | 6.1 | 0.8 | 0 | 13 | 0.065 | 71 |  | 7 | 0.032 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1939 | 72 | 4.9 | 41.81 | 4.6 | 114.4 | 0 | 0.3 | 0 | 0 | 0 | 10 | 0.01 | 69 |  | 51 | 0.014 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1938 | 73 | 611 | 41.81 | 536 | 4058 | 22 | 3 | 49 | 1 | 0 | 30 | 0.13 | 39 |  | 7 | 0.036 | 2-furfural level is above 1ppm. Other test results are assessed as acceptable.
33000 | 1938 | 73 | 100.3 | 31 | 83.8 | 897.2 | 11.7 | 1.8 | 2.1 | 0.5 | 0.4 | 25 | 0.369 | 27 |  | 5 | 0.042 | DGA is assessed as acceptable. | Breakdown voltage is low. Acidity level is high. DDF and Resistivity are assessed as acceptable.
33000 | 1936 | 75 | 280 | 40 | 232 | 2556 | 10 | 4 | 31 | 2 | 1 | 20 | 0.098 | 62 |  | 5.3 | 0.05 | Test results satisfactory. | Oil quality is assessed as acceptable.
33000 | 1936 | 75 | 399 | 41.81 | 314 | 3504 | 43 | 3 | 38 | 1 | 0 | 18 | 0.104 | 73 |  | 5.4 | 0.053 | Test results satisfactory. | Oil quality is assessed as acceptable.
33000 | 1936 | 75 | 314 | 41.81 | 278 | 3466 | 2 | 2 | 31 | 1 | 0 | 29 | 0.103 | 75 |  | 4.4 | 0.058 | Test results are assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1936 | 75 | 297.8 | 50 | 244.5 | 4157.8 | 4.9 | 2.5 | 44.6 | 1.3 | 0 | 23 | 0.147 | 52 |  | 4 | 0.061 | The test results are assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1936 | 75 | 315.8 | 41.81 | 264.4 | 5934.1 | 6.8 | 2.6 | 42 | 0 | 0 | 35 | 0.151 | 23 |  | 4 | 0.067 | DGA is assessed as acceptable. | Moisture content is high. Breakdown voltage is low. Possible sample contamination. Other oil quality results are assessed as acceptable.
33000 | 1936 | 75 | 300 | 41.81 | 256.5 | 4674.9 | 5 | 2.3 | 35.1 | 1.1 | 0 | 23 | 0.189 | 64 |  | 4 | 0.061 | DGA is assessed as acceptable. | Acidity level is high. Other oil quality results are assessed as acceptable.
33000 | 1936 | 75 | 207.5 | 25 | 169.8 | 4186.8 | 2.5 | 2.3 | 31.9 | 1 | 0 | 26 | 0.203 | 37 |  | 3 | 0.07 | DGA is assessed as acceptable. | Acidity level is high. Other oil quality results are assessed as acceptable.
33000 | 1936 | 75 | 379 | 41.81 | 325.9 | 6416.6 | 6.9 | 3 | 42.3 | 0.9 | 0 | 26 | 0.182 | 40 |  | 3 | 0.068 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1936 | 75 | 339.5 | 22 | 284.8 | 5765.2 | 14.7 | 2.5 | 36.9 | 0.6 | 0 | 40 | 0.19 | 27 |  | 3 | 0.064 | DGA is assessed as acceptable. | Breakdown voltage is low. Other oil quality results are assessed as acceptable.
33000 | 1936 | 75 | 408.8 | 55 | 360.6 | 6210.8 | 12.1 | 2.9 | 32.2 | 1 | 0 | 29 | 0.205 | 44 |  | 3 | 0.068 | DGA is assessed as acceptable. | Acidity level is high. Other oil quality results are assessed as acceptable. Non-corrosive IEC. Non-corrosive ASTM 3B.
33000 | 1936 | 75 | 255.5 | 50 | 219.3 | 4543.8 | 5.8 | 2.8 | 26.7 | 0.9 | 0 | 30 | 0.201 | 33 |  | 3 | 0.072 | DGA is assessed as acceptable. | Breakdown voltage is low. Other oil quality results are assessed as acceptable.
33000 | 1936 | 75 | 1019 | 41.81 | 686 | 3822 | 124 | 113 | 15 | 81 | 0 | 65 | 0.245 | 27 |  | 6 | 0.05 | D.G.A. Suggests slight overheating. Breakdown and moisture results poor. Recommend resample.
33000 | 1936 | 75 | 811 | 41.81 | 586 | 3542 | 56 | 80 | 15 | 74 | 0 | 40 | 0.255 | 40 |  | 6 | 0.045 | Gas level stable.
33000 | 1936 | 75 | 1223 | 41.81 | 851 | 4220 | 248 | 70 | 11 | 43 | 0 | 43 | 0.282 | 58 |  | 4.7 | 0.054 | Gas levels stable.Acidity level of oil quite high.Other test results satisfactory.
33000 | 1936 | 75 | 827 | 41.81 | 681 | 4329 | 116 | 14 | 6 | 10 | 0 | 56 | 0.3 | 48 |  | 5 | 0.049 | Moisture content and acidity levels quite high. Other test results satisfactory. OIL CHANGE IS RECOMMENDED.
33000 | 1936 | 75 | 16 | 41.81 | 14 | 299 | 0 | 1 | 0 | 1 | 0 | 14 | 0.02 | 57 |  | 57 | 0.008 | Test results satisfactory. New oil in TX.
33000 | 1936 | 75 | 491 | 41.81 | 415 | 9745 | 51 | 7 | 14 | 4 | 0 | 39 | 0.037 | 27 |  | 20.6 | 0.015 | Moisture content of oil is above defect level. 2-furfural level is above 1ppm. Carbon dioxide level is high. Other test results are assessed as acceptable. RECOMMEND RESAMPLE IN 1 YEAR TO MONITOR TREND.
33000 | 1936 | 75 | 253 | 48 | 220 | 6456 | 14 | 4 | 14 | 1 | 0 | 46 | 0.043 | 20 |  | 18.1 | 0.021 | Moisture content of oil is high; dielectric strength low; possibly sample contamination. 2-Furfural level is above 1ppm. Other test results are assessed as acceptable.
33000 | 1936 | 75 | 175 | 40 | 147 | 6003 | 9 | 4 | 14 | 1 | 0 | 37 | 0.046 | 40 |  | 18.7 | 0.021 | 2-Furfural level is high but stable. Moisture content of oil is high. Other test results are assessed as acceptable.
33000 | 1936 | 75 | 738 | 39 | 650 | 7148 | 50 | 15 | 15 | 8 | 0 | 58 | 0.184 | 18 |  | 7.5 | 0.032 | Moisture content of oil is above defect level. Breakdown of oil is low; 2-fufural level is high suggesting advanced rate of insulation degradation. RECOMMEND RESAMPLE IN 6 MONTHS TO MONITOR TREND.
33000 | 1936 | 75 | 366 | 43 | 295 | 10030 | 28 | 5 | 36 | 2 | 0 | 7 | 0.041 | 46 |  | 17.6 | 0.026 | 2-furfural level is high suggesting advanced insulation degradation. Other test results are assessed as acceptable. RECOMMEND RESAMPLE IN 1 YEAR TO MONITOR TREND.
33000 | 1936 | 75 | 524.7 | 65 | 439.1 | 8561 | 44 | 8 | 29.6 | 2.5 | 1.5 | 40 | 0.064 | 25 |  | 22 | 0.014 | Moisture content of sample is high. Breakdown voltage of sample is low. 2-furfural level is trending upwards suggesting accelerated rate of insulation degradation. RECOMMEND RESAMPLE IN 1 YEAR TO MONITOR CONDITION.
33000 | 1936 | 75 | 304.3 | 50 | 241.9 | 7221.8 | 18.7 | 4.8 | 36.8 | 2.1 | 0 | 36 | 0.042 | 24 |  | 12 | 0.026 | Moisture content of sample is high. Breakdown voltage of sample is low. 2-furfural level is reduced but still high suggesting accelerated rate of insulation degradation. Other test results are assessed as acceptable. RECOMMEND RESAMPLE IN 1 YEAR TO MO
33000 | 1936 | 75 | 289.3 | 40 | 233 | 6519.9 | 20.1 | 3.3 | 31.2 | 1.7 | 0 | 32 | 0.048 | 51 |  | 13 | 0.026 | Moisture content of sample is slightly high. Dissolved gas analysis is assessed as acceptable. RECOMMEND RESAMPLE IN 2 YEARS TO MONITOR TREND.
33000 | 1936 | 75 | 314.3 | 45 | 251.1 | 6824 | 23.2 | 4.3 | 33.8 | 1.9 | 0 | 38 | 0.047 | 15 |  | 14 | 0.023 | DGA is assessed as acceptable. | Moisture content is high. Breakdown voltage is very low.
33000 | 1936 | 75 | 363 | 30 | 296.2 | 7780.7 | 20.8 | 5.2 | 39 | 1.8 | 0 | 32 | 0.038 | 26 |  | 13 | 0.028 | DGA is assessed as acceptable. | Breakdown voltage is low. Other oil quality results are assessed as acceptable.
33000 | 1936 | 75 | 373.3 | 41 | 302 | 7749 | 28 | 5 | 37 | 1.3 | 0 | 38 | 0.04 | 15 |  | 12 | 0.028 | DGA is assessed as acceptable. | Moisture content is high. Breakdown voltage is low. Particles in the oil. Other oil quality results are assessed as acceptable.
33000 | 1936 | 75 | 368 | 46 | 277.5 | 7447.4 | 46.1 | 5 | 37.5 | 1.9 | 0 | 42 | 0.05 | 13 |  | 17 | 0.017 | DGA is assessed as acceptable. | Moisture content is high. Breakdown voltage is low. Other oil quality results are assessed as acceptable.
33000 | 1936 | 75 | 306.4 | 50 | 246.2 | 6426.2 | 16.9 | 5 | 36.5 | 1.8 | 0 | 27 | 0.051 | 16 |  | 16 | 0.019 | DGA is assessed as acceptable. | Breakdown voltage is low but stable. Other oil quality results are assessed as acceptable.
33000 | 1936 | 75 | 373.9 | 48 | 306.6 | 7534.8 | 22.1 | 7.4 | 36.3 | 1.5 | 0 | 34 | 0.04 | 20 |  | 17 | 0.021 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable. Corrosive IEC. Corrosive ASTM 4A.
33000 | 1935 | 76 | 5008 | 41.81 | 227 | 18087 | 139 | 371 | 1547 | 204 | 2520 | 46 | 0.182 | 32 |  | 10.9 | 0.025 | High level of fault gases suggest arcing has taken place; CO2 gas level very high.
33000 | 1931 | 80 | 13 | 41.81 | 12 | 239 | 0 | 0 | 1 | 0 | 0 | 30 | 0.21 | 33 |  | 8 | 0.289 | DGA is assessed as acceptable. | Oil quality is assessed as acceptable.
33000 | 1931 | 80 | 3 | 41.81 | 2 | 530 | 0 | 0 | 1 | 0 | 0 | 31 | 0.61 | 63 |  | 1.5 | 0.164 | Acidity level very high. Should consider oil change. RESAMPLE FIRST TO CONFIRM RESULTS.
33000 | 1931 | 80 | 11 | 41.81 | 10 | 349 | 0 | 0 | 1 | 0 | 0 | 31 | 0.188 | 42 |  | 4.5 | 0.054 | Test results satisfactory.